## Table1
Customer | Study Number | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date without interim redispatch (Parameter) | Deferred Stop Date without interim redispatch | Start Date with interim redispatch | Stop Date with interim redispatch | Minimum Allocated ATC (MW) within reservation period | Season of Minimum Allocated ATC within reservation period | ⁵One or More Study Parameters Exceeded
AEPE | AG1-2017-001 | 84604894 | NPPD | NPPD | 7 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | Note 4 | Note 4 | 0 | 18SP | NO
AEPE | AG1-2017-002 | 84606580 | WAUE | NPPD | 1 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | Note 4 | Note 4 | 0 | 18SP | YES
AEPE | AG1-2017-003 | 84606716 | NPPD | NPPD | 5 | 2018-01-01 | 2022-01-01 | 2018-01-01 | 2022-01-01 | Note 4 | Note 4 | 0 | 18SP | NO
AEPE | AG1-2017-004 | 84727067 | NPPD | NPPD | 7 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | Note 4 | Note 4 | 0 | 18SP | NO
AEPE | AG1-2017-005 | 84729062 | MPS | SPS | 37 | 2019-06-01 | 2026-01-01 | 2019-06-01 | 2026-01-01 | Note 4 | Note 4 | 0 | 21SP | NO
AEPE | AG1-2017-006 | 84740127 | MPS | SPS | 37 | 2019-06-01 | 2026-01-01 | 2022-12-31 | 2029-07-31 | Note 4 | Note 4 | 0 | 21SP | YES
AEPE | AG1-2017-007 | 84740859 | NPPD | NPPD | 36 | 2019-01-01 | 2024-01-01 | 2019-01-01 | 2024-01-01 | Note 4 | Note 4 | 0 | 21SP | NO
AEPE | AG1-2017-008 | 84746514 | NPPD | NPPD | 32 | 2019-01-01 | 2022-01-01 | 2019-01-01 | 2022-01-01 | Note 4 | Note 4 | 0 | 21SP | YES
AEPE | AG1-2017-009 | 84746608 | WAUE | NPPD | 3 | 2019-01-01 | 2024-01-01 | 2019-01-01 | 2024-01-01 | Note 4 | Note 4 | 0 | 21SP | YES
AEPE | AG1-2017-010 | 84755770 | LES | NPPD | 18 | 2019-01-01 | 2022-01-01 | 2019-01-01 | 2022-01-01 | Note 4 | Note 4 | 0 | 21SP | YES
AEPM | AG1-2017-011 | 84903862 | CSWS | CSWS | 400 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 26SP | YES
AEPM | AG1-2017-012 | 84904082 | CSWS | CSWS | 610 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 26SP | YES
AEPM | AG1-2017-013 | 84904145 | OKGE | CSWS | 612 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 26SP | YES
AEPM | AG1-2017-014 | 84904230 | OKGE | CSWS | 450 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 26SP | YES
AEPM | AG1-2017-015 | 84904264 | CSWS | CSWS | 435 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 26SP | YES
AEPM | AG1-2017-016 | 84904431 | OKGE | CSWS | 500 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 26SP | YES
AEPM | AG1-2017-017 | 84904909 | CSWS | CSWS | 147 | 2017-12-01 | 2022-12-01 | 2020-06-01 | 2025-06-01 | 2017-12-01 | 2022-12-01 | 0 | 18SP | YES
BEPM | AG1-2017-018 | 84885588 | WAUE | WAUE | 140 | 2017-12-01 | 2023-10-01 | 2018-10-01 | 2023-10-01 | Note 4 | Note 4 | 0 | 18SP | YES
BEPM | AG1-2017-019 | 84885627 | WAUE | WAUE | 5 | 2018-04-01 | 401769 | 2018-04-01 | 401769 | Note 4 | Note 4 | 0 | 18SP | YES
BEPM | AG1-2017-020 | 84885635 | WAUE | WAUE | 45 | 2017-12-01 | 2023-10-01 | 2017-12-01 | 2023-10-01 | Note 4 | Note 4 | 0 | 18SP | YES
BRPS | AG1-2017-021 | 84912692 | NPPD | NPPD | 19 | 2018-01-01 | 2028-01-01 | 2018-01-01 | 2028-01-01 | 2018-01-01 | 2028-01-01 | 0 | 18SP | NO
FREM | AG1-2017-022 | 84911097 | OPPD | OPPD | 5 | 2018-10-01 | 2028-10-01 | 2018-10-01 | 2028-10-01 | Note 4 | Note 4 | 0 | 21SP | NO
KCPS | AG1-2017-023 | 84873359 | WPEK | KCPL | 50 | 2017-12-01 | 2031-12-01 | 2021-06-01 | 2031-12-01 | Note 4 | Note 4 | 0 | 18SP | YES
KCPS | AG1-2017-024 | 84885455 | WR | KCPL | 1 | 2017-12-01 | 2030-06-01 | 2017-12-01 | 2030-06-01 | Note 4 | Note 4 | 0 | 18SP | NO
KMEA | AG1-2017-025 | 84875443 | MPS | SECI | 30 | 2018-03-01 | 2038-03-01 | 2018-03-01 | 2038-03-01 | 2018-03-01 | 2038-03-01 | 0 | 18SP | NO
KMEA | AG1-2017-026 | 84877536 | MPS | SECI | 5 | 2019-01-01 | 2029-01-01 | 2019-01-01 | 2029-01-01 | 2019-01-01 | 2029-01-01 | 0 | 21SP | NO
KMEA | AG1-2017-027 | 84884608 | SPA | WR | 1 | 2017-12-01 | 2028-06-01 | 2017-12-01 | 2028-06-01 | 2017-12-01 | 2028-06-01 | 0 | 18SP | NO
KMEA | AG1-2017-028 | 84885203 | NPPD | WR | 1 | 2017-12-01 | 2054-10-01 | 2017-12-01 | 2054-10-01 | 2017-12-01 | 2054-10-01 | 0 | 18SP | NO
KMEA | AG1-2017-029 | 84885381 | MPS | KCPL | 5 | 2018-03-01 | 2028-03-01 | 2018-03-01 | 2028-03-01 | 2018-03-01 | 2028-03-01 | 0 | 18SP | NO
KMEA | AG1-2017-030 | 84885945 | MPS | KCPL | 20 | 2019-01-01 | 2029-01-01 | 2019-01-01 | 2029-01-01 | 2019-01-01 | 2029-01-01 | 0 | 21SP | NO
KMEA | AG1-2017-031 | 84906139 | MPS | WR | 1 | 2020-01-01 | 2040-01-01 | 2020-01-01 | 2040-01-01 | 2020-01-01 | 2040-01-01 | 0 | 26SP | NO
KMEA | AG1-2017-032 | 84906152 | MPS | WR | 1 | 2020-01-01 | 2040-01-01 | 2020-01-01 | 2040-01-01 | 2020-01-01 | 2040-01-01 | 0 | 26SP | NO
MEAN | AG1-2017-033 | 84903949 | NPPD | MEC | 10 | 2018-01-01 | 2019-01-01 | 2018-01-01 | 2019-01-01 | 2018-01-01 | 2019-01-01 | 0 | 18SP | NO
MIDW | AG1-2017-034 | 84911381 | SPA | WR | 1 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 0 | 18SP | NO
MIDW | AG1-2017-035 | 84912544 | WR | WR | 1 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 0 | 18SP | NO
MIDW | AG1-2017-036 | 84912549 | SPA | WR | 1 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 0 | 18SP | NO
NPPM | AG1-2017-037 | 84863769 | NPPD | NPPD | 32 | 2018-01-01 | 2025-04-01 | 2020-06-01 | 2027-09-01 | 2018-01-01 | 2025-04-01 | 0 | 18SP | NO
NPPM | AG1-2017-038 | 84863943 | NPPD | NPPD | 36 | 2018-01-01 | 2025-04-01 | 2020-06-01 | 2027-09-01 | 2018-01-01 | 2025-04-01 | 0 | 18SP | NO
OTPW | AG1-2017-039 | 84906479 | OTP | WAUE | 49 | 2018-01-01 | 401769 | 2018-01-01 | 401769 | Note 4 | Note 4 | 0 | 18SP | NO
OTPW | AG1-2017-040 | 84906636 | OTP | WAUE | 49 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | Note 4 | Note 4 | 0 | 18SP | NO
OTPW | AG1-2017-041 | 84906754 | OTP | WAUE | 15 | 2018-01-01 | 401769 | 2018-01-01 | 401769 | Note 4 | Note 4 | 0 | 18SP | NO
OTPW | AG1-2017-042 | 84910586 | OTP | WAUE | 15 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | Note 4 | Note 4 | 0 | 18SP | NO
PEC | AG1-2017-043 | 84885681 | WFEC | WFEC | 50 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | Note 4 | Note 4 | 0 | 18SP | YES
SPSM | AG1-2017-044 | 84730363 | SPS | SPS | 16 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 0 | 21SP | NO
SPSM | AG1-2017-045 | 84734700 | SPS | SPS | 17 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 0 | 21SP | NO
SPSM | AG1-2017-046 | 84734856 | SPS | SPS | 21 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 0 | 21SP | NO
SPSM | AG1-2017-047 | 84734992 | SPS | SPS | 58 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 0 | 21SP | NO
WRGS | AG1-2017-048 | 84877548 | WR | WR | 50 | 2017-12-01 | 2024-01-01 | 2019-10-01 | 2025-11-01 | 2017-12-01 | 2024-01-01 | 0 | 18SP | YES
WRGS | AG1-2017-049 | 84877556 | WR | WR | 26 | 2017-12-01 | 2023-12-01 | 2019-10-01 | 2025-10-01 | 2017-12-01 | 2023-12-01 | 0 | 18SP | YES
4113
Note 1: Start and Stop Dates with interim redispatch are determined based on customers choosing option to pursue redispatch to start service at Requested Start and Stop Dates or earliest date possible.
Note 2: Start dates with and without redispatch are based on the assumed completion dates of previous Aggregate Transmission Service Studies currently being conducted. Actual start dates may differ from the potential start dates upon completion of the previous studies.
Note 3: Request is unable to be deferred due to fixed stop dates.
Note 4: Transmission customer did not select “remain in the study using interim redispatch” option.
Note 5: Request paramaters have been exceeded.

## Table2
Customer | Study Number | Reservation | Engineering and Construction Cost of Upgrades Allocated to Customer for Revenue Requirements | 1Letter of Credit Amount Required (Parameter) | 2Potential Base Plan Engineering and Construction Funding Allowable | Notes | 4Additional Engineering and Construction Cost for 3rd Party Upgrades (Parameter) | 3 5Total Revenue Requirements for Assigned Upgrades Over Term of Reservation WITH Potential Base Plan Funding Allocation | 6,7Total Gross CPOs Over Reservation Period | 9Point-to-Point Base Rate Over Reservation Period | 4Total Cost of Reservation Assignable to Customer Contingent Upon Base Plan Funding | Directly Assigned Upgrade Cost (DAUC) (Parameter) | 9Total Estimated Point-To-Point Base Rate With Applicable Schedules Included.
AEPE | AG1-2017-001 | 84604894 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
AEPE | AG1-2017-002 | 84606580 | 184.28 | 184.28 | 0 |  | 0 | 0 | 237 | 0 | 237 | 184.28
AEPE | AG1-2017-003 | 84606716 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
AEPE | AG1-2017-004 | 84727067 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
AEPE | AG1-2017-005 | 84729062 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
AEPE | AG1-2017-006 | 84740127 | 347199.59 | 0 | 347199.59 | 8 | 0 | 0 | 836384.06 | 0 | Schedule 9 & 11 Charges | 0
AEPE | AG1-2017-007 | 84740859 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
AEPE | AG1-2017-008 | 84746514 | 23600.28 | 23600.28 | 0 |  | 0 | 0 | 68540.4 | 0 | 68540.4 | 23600.28
AEPE | AG1-2017-009 | 84746608 | 2785.63 | 2785.63 | 0 |  | 0 | 0 | 3588 | 0 | 3588 | 2785.63
AEPE | AG1-2017-010 | 84755770 | 10131.22 | 10131.22 | 0 |  | 0 | 0 | 43107.84 | 0 | 43107.84 | 10131.22
AEPM | AG1-2017-011 | 84903862 | 1777778.7 | 1777778.7 | 0 |  | 0 | 2854522 | 1052002.2 | 0 | 3906524.2 | 1777778.7
AEPM | AG1-2017-012 | 84904082 | 7675532 | 7675532 | 0 | 8 | 0 | 4550804 | 7968576 | 0 | 12519380 | 7675532
AEPM | AG1-2017-013 | 84904145 | 6280881.73 | 6269007.66 | 11874.07 |  | 0 | 4393033 | 17609298.6 | 0 | 22002331.6 | 6269007.66
AEPM | AG1-2017-014 | 84904230 | 3416183.64 | 3416183.64 | 0 | 8 | 0 | 3540997 | 7488517.8 | 0 | 11029514.8 | 3416183.64
AEPM | AG1-2017-015 | 84904264 | 5677660.7 | 5677660.7 | 0 | 8 | 0 | 3096347 | 6318005.4 | 0 | 9414352.4 | 5677660.7
AEPM | AG1-2017-016 | 84904431 | 11640871.31 | 11620871.31 | 20000 |  | 0 | 0 | 19964007.9 | 0 | 19929708.0484 | 11620871.31
AEPM | AG1-2017-017 | 84904909 | 44521888 | 18061888 | 26460000 |  | 0 | 22170310.4641 | 1147242 | 0 | 23317552.4641 | 18061888
BEPM | AG1-2017-018 | 84885588 | 617236 | 537236 | 80000 |  | 0 | 401987.9381 | 200419.2 | 0 | 602407.1381 | 537236
BEPM | AG1-2017-019 | 84885627 | 24364.54 | 24364.54 | 0 |  | 0 | 0 | 912556.26 | 0 | 912556.26 | 24364.54
BEPM | AG1-2017-020 | 84885635 | 136079.64 | 136079.64 | 0 |  | 0 | 135928.39 | 19118.4 | 0 | 155046.79 | 136079.64
BRPS | AG1-2017-021 | 84912692 | 1331706.13 | 0 | 1331706.13 |  | 0 | 0 | 1632432 | 0 | Schedule 9 & 11 Charges | 0
FREM | AG1-2017-022 | 84911097 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1631073.6 | 1631073.6 | 0 | 1921455.3557
KCPS | AG1-2017-023 | 84873359 | 1917459.43 | 1917459.43 | 0 |  | 0 | 0 | 3568742.1 | 0 | 3568742.1 | 1917459.43
KCPS | AG1-2017-024 | 84885455 | 3380.61 | 0 | 3380.61 |  | 0 | 0 | 17166 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-025 | 84875443 | 98340.08 | 0 | 98340.08 |  | 0 | 0 | 630470.4 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-026 | 84877536 | 148604.75 | 0 | 148604.75 |  | 0 | 0 | 359114.4 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-027 | 84884608 | 52644.63 | 0 | 52644.63 |  | 0 | 0 | 11900.7 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-028 | 84885203 | 21169.04 | 0 | 21169.04 |  | 0 | 0 | 1237.6 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-029 | 84885381 | 868.7 | 0 | 868.7 |  | 0 | 0 | 6908.4 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-030 | 84885945 | 3118.46 | 0 | 3118.46 |  | 0 | 0 | 26688 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-031 | 84906139 | 91.29 | 0 | 91.29 |  | 0 | 0 | 741.6 | 0 | Schedule 9 & 11 Charges | 0
KMEA | AG1-2017-032 | 84906152 | 91.29 | 0 | 91.29 |  | 0 | 0 | 741.6 | 0 | Schedule 9 & 11 Charges | 0
MEAN | AG1-2017-033 | 84903949 | 0 | 0 | 0 |  | 0 | 0 | 0 | 392493.96 | 392493.96 | 0 | 449129.7111
MIDW | AG1-2017-034 | 84911381 | 2183.53 | 0 | 2183.53 |  | 0 | 0 | 13405.85 | 0 | Schedule 9 & 11 Charges | 0
MIDW | AG1-2017-035 | 84912544 | 2013.32 | 0 | 2013.32 |  | 0 | 0 | 12265.22 | 0 | Schedule 9 & 11 Charges | 0
MIDW | AG1-2017-036 | 84912549 | 1411.51 | 0 | 1411.51 |  | 0 | 0 | 8642.39 | 0 | Schedule 9 & 11 Charges | 0
NPPM | AG1-2017-037 | 84863769 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
NPPM | AG1-2017-038 | 84863943 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
OTPW | AG1-2017-039 | 84906479 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
OTPW | AG1-2017-040 | 84906636 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
OTPW | AG1-2017-041 | 84906754 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
OTPW | AG1-2017-042 | 84910586 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
PEC | AG1-2017-043 | 84885681 | 8865717.61 | 8865539.09 | 178.52 |  | 0 | 8367436.734 | 1331964.4802 | 0 | 9698401.2142 | 8865539.09
SPSM | AG1-2017-044 | 84730363 | 16121.51 | 0 | 16121.51 | 8 | 0 | 0 | 20336.79 | 0 | Schedule 9 & 11 Charges | 0
SPSM | AG1-2017-045 | 84734700 | 9749.82 | 0 | 9749.82 | 8 | 0 | 0 | 13096.09 | 0 | Schedule 9 & 11 Charges | 0
SPSM | AG1-2017-046 | 84734856 | 12127.61 | 0 | 12127.61 | 8 | 0 | 0 | 16283.95 | 0 | Schedule 9 & 11 Charges | 0
SPSM | AG1-2017-047 | 84734992 | 33492.73 | 0 | 33492.73 | 8 | 0 | 0 | 44971.03 | 0 | Schedule 9 & 11 Charges | 0
WRGS | AG1-2017-048 | 84877548 | 9483991.9 | 9480667.38 | 3324.52 |  | 0 | 0 | 6541640.96 | 0 | 14614136.742 | 9480667.38
WRGS | AG1-2017-049 | 84877556 | 3478625.26 | 3475185.83 | 3439.43 |  | 0 | 0 | 1717295.04 | 0 | 5906198.736 | 3475185.83
Grand Total |  |  | 107635286.47 | 78972155.33 | 28591914.14 |  | 0 | 49511366.5262 | 79607645.6602 |  |  | 78972155.33
Note 1: Letter of Credit required for financial security for transmission owner for network upgrades is determined by allocated engineering and construction costs less engineering and construction costs for upgrades when network customer is the transmission owner less the E & C allocation of expedited projects. Letter of Credit is required for upgrades assigned to PTP requests. The amount of the letter of credit will be adjusted down on an annual basis to reflect cost recovery based on revenue allocation. This letter of credit is not required for those facilities that are fully base plan funded. The Letter Of Credit Amount listed is based on meeting OATT Attachment J requirements for base plan funding.
Note 2: If potential base plan funding is applicable, this value is the lesser of the Engineering and Construction costs of assignable upgrades or the value of base plan funding calculated pursuant to Attachment J, Section III B criteria. Allocation of base plan funding is contingent upon verification of customer agreements meeting Attachment J, Section II B criteria. Not applicable if Point-to-Point base rate exceeds revenue requirements.
Note 3: Revenue Requirements (RR) are based upon deferred end dates if applicable. Deferred dates are based upon customer's choice to pursue redispatch. Achievable Base Plan Avoided RR in the case of a Base Plan upgrade being displaced or deferred by an earlier in service date for a Requested Upgrade shall be determined per Attachment J, Section VII.C methodology. Assumption of a 40 year service life is utilized for Base Plan funded projects. A present worth analysis of RR on a common year basis between the Base Plan and Requested Upgrades was performed to determine avoided Base Plan RR due to the displacement or deferral of the Base Plan upgrade by the Requested Upgrade. The incremental increase in present worth of a Requested Upgrade on a common year basis as a Base Plan upgrade is assigned to the transmission requests impacting the upgrade based on the displacement or deferral. If the displacement analysis results in lower RR due to the shorter amortization period of the requested upgrade when compared to a base plan amortization period, then no direct assignment of the upgrade cost is made due to the displacement to an earlier start date.
Note 4: For Point-to-Point requests, total cost is based on the higher of the base rate or assigned upgrade revenue requirements. For Network requests, the total cost is based on the assigned upgrade revenue requirement. Allocation of base plan funding will be determined after verification of designated resource meeting Attachment J, Section II B Criteria. Additionally E & C of 3rd Party upgrades is assignable to Customer. This includes prepayments required for any SWPA upgrades. Revenue requirements for 3rd Party facilities are not calculated. Total cost to customer is based on assumption of Revenue Requirements with confirmation of base plan funding. Customer is responsible for negotiating redispatch costs if applicable. Customer is also responsible to pay credits for previously assigned upgrades that are impacted by their request. Credits can be paid from base plan funding if applicable.
Note 5: RR with base plan funding may increase or decrease even if no base plan funding is applicable to a particular request if another request that shares the upgrade is now full base plan funded resulting in a different amortization period for the upgrade and thus different RR.
Note 6: RR for creditable upgrades.
Note 7: CPOs may be calculated based on estimated upgrade cost and are subject to change.
Note 8: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Note 9: Point-To-Point rates are calculated using the available rate(s). These rate(s) are subject to change.

## Table3
Customer | Study Number
AEPE | AG1-2017-001
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84604894 | NPPD | NPPD | 7 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84604894 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change.
Customer | Study Number
AEPE | AG1-2017-002
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84606580 | WAUE | NPPD | 1 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | 0 | 0 | 184.28 | 237
[9 empty] | 0 | 0 | 184.28 | 237
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84606580 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84606580 | Albion - Petersburg 115kV Ckt 1 Hansford Upgrade | 2012-12-31 | 2012-12-31 |  |  | 184.28 | 237
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 184.28 | 237
Customer | Study Number
AEPE | AG1-2017-003
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84606716 | NPPD | NPPD | 5 | 2018-01-01 | 2022-01-01 | 2018-01-01 | 2022-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84606716 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change.
Customer | Study Number
AEPE | AG1-2017-004
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84727067 | NPPD | NPPD | 7 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84727067 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change.
Customer | Study Number
AEPE | AG1-2017-005
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84729062 | MPS | SPS | 37 | 2019-06-01 | 2026-01-01 | 2019-06-01 | 2026-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84729062 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change.
Customer | Study Number
AEPE | AG1-2017-006
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84740127 | MPS | SPS | 37 | 2019-06-01 | 2026-01-01 | 2022-12-31 | 2029-07-31 | 347199.59 | 0 | 347199.59 | 836384.06
[9 empty] | 347199.59 | 0 | 347199.59 | 836384.06
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84740127 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84740127 | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | 2022-10-01 | 2022-10-01
| DENVER CITY INTERCHANGE N. - XTO_RUSSEL 3115.00 115KV CKT 1 | 2022-10-01 | 2022-10-01
| FLOYD COUNTY INTERCHANGE - TUCO INTERCHANGE 115KV CKT 1 | 2022-06-01 | 2022-06-01
| TOLK STATION TAP - TOLK STATION WEST 230KV CKT @1 | 2022-06-01 | 2022-12-31
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84740127 | Harrington Mid - Nichols 230 kV Ckt 2 | 2012-12-01 | 2012-12-01 |  |  | 5863.31 | 9059.72
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01 |  |  | 6177.44 | 9544.78
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 9417.53 | 51326.3
| Kingfisher Co Tap - Mathewson 345kV CKT 1 | 2018-03-01 | 2018-03-01 |  |  | 29557.95 | 40798.76
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 60343.49 | 397102.19
| TUCO Interchange 345/230kV CKT 1 Replacement | 2018-06-01 | 2018-06-01 |  |  | 233987.67 | 319803.85
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 1852.2 | 8748.46
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 347199.59 | 836384.06
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
AEPE | AG1-2017-007
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84740859 | NPPD | NPPD | 36 | 2019-01-01 | 2024-01-01 | 2019-01-01 | 2024-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84740859 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change.
Customer | Study Number
AEPE | AG1-2017-008
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84746514 | NPPD | NPPD | 32 | 2019-01-01 | 2022-01-01 | 2019-01-01 | 2022-01-01 | 0 | 0 | 23600.28 | 68540.4
[9 empty] | 0 | 0 | 23600.28 | 68540.4
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84746514 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84746514 | CLIFTON - GREENLEAF 115KV CKT 1 | 2011-06-01 | 2013-06-01 |  |  | 11659.25 | 49609.8
| GREENLEAF - KNOB HILL 115KV CKT 1 (MKEC) | 2013-06-01 | 2013-06-01 |  |  | 1202.7 | 5117.4
| Neligh - Petersburg North 115kV Ckt 1 | 2012-11-09 | 2012-11-09 |  |  | 10738.33 | 13813.2
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 23600.28 | 68540.4
Customer | Study Number
AEPE | AG1-2017-009
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84746608 | WAUE | NPPD | 3 | 2019-01-01 | 2024-01-01 | 2019-01-01 | 2024-01-01 | 0 | 0 | 2785.63 | 3588
[9 empty] | 0 | 0 | 2785.63 | 3588
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84746608 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84746608 | STORLA (KV1A) 230/115/13.2KV TRANSFORMER CKT 1 | 2018-10-01 | 2019-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84746608 | Albion - Petersburg 115kV Ckt 1 Hansford Upgrade | 2012-12-31 | 2012-12-31 |  |  | 537.53 | 714
| Kelly - Madison County 230kV Ckt 1 | 2014-11-01 | 2014-11-01 |  |  | 2248.1 | 2874
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 2785.63 | 3588
Customer | Study Number
AEPE | AG1-2017-010
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPE | 84755770 | LES | NPPD | 18 | 2019-01-01 | 2022-01-01 | 2019-01-01 | 2022-01-01 | 0 | 0 | 10131.22 | 43107.84
[9 empty] | 0 | 0 | 10131.22 | 43107.84
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84755770 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84755770 | CLIFTON - GREENLEAF 115KV CKT 1 | 2011-06-01 | 2013-06-01 |  |  | 9183.86 | 39076.92
| GREENLEAF - KNOB HILL 115KV CKT 1 (MKEC) | 2013-06-01 | 2013-06-01 |  |  | 947.36 | 4030.92
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 10131.22 | 43107.84
Customer | Study Number
AEPM | AG1-2017-011
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 84903862 | CSWS | CSWS | 400 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 0 | 1777778.74 | 3906524.508
[9 empty] | 0 | 0 | 1777778.74 | 3906524.508
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84903862 | ARSENAL HILL - RAINES 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 1464936 | 10000000 | 2825437.548
| HUGO POWER PLANT - VALLIANT 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 19607 | 150000 | 29084.76
[5 empty] | Total | 1484543 | 10150000 | 2854522.31
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84903862 | ONETA - ONETA ENERGY CENTER 345KV CKT 1 | 2022-06-01 | 2022-06-01
| ONETA - ONETA ENERGY CENTER 345KV CKT 2 | 2022-06-01 | 2022-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84903862 | HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 161454.47 | 786546
| Kingfisher Co Tap - Mathewson 345kV CKT 1 | 2018-03-01 | 2018-03-01 |  |  | 100115.72 | 131055.6
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 31665.55 | 134400.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 293235.74 | 1052002.2
Customer | Study Number
AEPM | AG1-2017-012
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 84904082 | CSWS | CSWS | 610 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 0 | 7675532.49 | 12519380.19
[9 empty] | 0 | 0 | 7675532.49 | 12519380.19
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84904082 | ARSENAL HILL - RAINES 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 2359506 | 10000000 | 4550804.19
[5 empty] | Total | 2359506 | 10000000 | 4550804.19
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84904082 | Beaver County 345kV Substation | 2014-09-29 | 2014-09-29 |  |  | 3972022.72 | 5536221.6
| Beaver County 345kV Substation Addition | 2014-11-14 | 2014-11-14 |  |  | 120480.22 | 164341.2
| Beaver County Substation - Add 345kV terminal for Ochiltree | 2017-09-27 | 2017-09-27 |  |  | 1032429.95 | 1356729.6
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 159760.32 | 778293
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 31333.28 | 132990.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 5316026.49 | 7968576
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
AEPM | AG1-2017-013
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 84904145 | OKGE | CSWS | 612 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 11874.07 | 0 | 6280881.73 | 22002331.506
[9 empty] | 11874.07 | 0 | 6280881.73 | 22002331.506
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84904145 | ARSENAL HILL - RAINES 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 2249999 | 10000000 | 4339596.876
| HUGO POWER PLANT - VALLIANT 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 36023 | 150000 | 53436.03
[5 empty] | Total | 2286022 | 10150000 | 4393032.91
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84904145 | HOYT - JEFFREY ENERGY CENTER 345KV CKT 2 | 2018-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84904145 | HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 321881.61 | 1568087.4
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 2407783.76 | 14169295.8
| Power System Stabilizers in SPS | 2014-11-30 | 2014-11-30 |  |  | 11874.07 | 16461
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 63129.6 | 267946.8
| Woodward EHV 138kV Phase Shifting Transformer circuit #1 | 2017-08-02 | 2017-08-02 |  |  | 1110069.46 | 1469007
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01 |  |  | 80121.23 | 118500.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 3994859.73 | 17609298.6
Customer | Study Number
AEPM | AG1-2017-014
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 84904230 | OKGE | CSWS | 450 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 0 | 3416183.64 | 11029514.706
[9 empty] | 0 | 0 | 3416183.64 | 11029514.706
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84904230 | ARSENAL HILL - RAINES 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 1787810 | 10000000 | 3448168.038
| HUGO POWER PLANT - VALLIANT 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 62579 | 150000 | 92828.868
[5 empty] | Total | 1850389 | 10150000 | 3540996.91
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84904230 | HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 1044408.6 | 5087969.4
| HUGO 345/138KV TRANSFORMER CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 316549.54 | 1531142.4
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 204836.5 | 869406
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 1565794.64 | 7488517.8
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
AEPM | AG1-2017-015
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 84904264 | CSWS | CSWS | 435 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 0 | 0 | 5677660.7 | 9414352.656
[9 empty] | 0 | 0 | 5677660.7 | 9414352.656
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84904264 | ARSENAL HILL - RAINES 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 1588721 | 10000000 | 3064182.996
| HUGO POWER PLANT - VALLIANT 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 21683 | 150000 | 32164.26
[5 empty] | Total | 1610404 | 10150000 | 3096347.26
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84904264 | Beaver County 345kV Substation | 2014-09-29 | 2014-09-29 |  |  | 2832508 | 3947961.6
| Beaver County 345kV Substation Addition | 2014-11-14 | 2014-11-14 |  |  | 85916.23 | 117193.8
| Beaver County Substation - Add 345kV terminal for Ochiltree | 2017-09-27 | 2017-09-27 |  |  | 736241.03 | 967503.6
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 180085.89 | 877311.6
| Kingfisher Co Tap - Mathewson 345kV CKT 1 | 2018-03-01 | 2018-03-01 |  |  | 197185.88 | 258124.2
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 35319.67 | 149910.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 4067256.7 | 6318005.4
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
AEPM | AG1-2017-016
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 84904431 | OKGE | CSWS | 500 | 2022-06-01 | 2027-06-01 | 2022-06-01 | 2027-06-01 | 20000 | 0 | 11640871.31 | 19964007.9
[9 empty] | 20000 | 0 | 11640871.31 | 19964007.9
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84904431 | None |  |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total Revenue Requirements
84904431 | Sunnyside Relays for Grady Interconnection | 2016-11-23 | 2016-11-23 |  |  | 20000 | 0 | 20000 | 34101
| Terry Road 345kV Station (NU) | 2016-11-16 | 2016-11-16 |  |  | 0 | 11620871.31 | 11620871.31 | 19929906.9
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 20000 | 11620871.31 | 11640871.31 | 19964007.9
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
AEPM | AG1-2017-017
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 84904909 | CSWS | CSWS | 147 | 2017-12-01 | 2022-12-01 | 2020-06-01 | 2025-06-01 | 26460000 | 0 | 44521888.04 | 56647566.666
[9 empty] | 26460000 | 0 | 44521888.04 | 56647566.666
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84904909 | 52ND & DELAWARE WEST TAP - RIVERSIDE STATION 138KV CKT 1 | 2019-06-01 | 2022-06-01 |  |  | 7528253.67 | 17471746.33 | 25000000 | 25000000 | 31103902.662
| 52ND & DELAWARE WEST TAP - TULSA POWER STATION 138KV CKT 1 | 2019-06-01 | 2022-06-01 |  |  | 16111111 |  | 16111111 | 16111111 | 20027670.84
| ARSENAL HILL - RAINES 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 549028 |  | 549028 | 10000000 | 734669.298
| HUGO POWER PLANT - VALLIANT 138KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 10107 |  | 10107 | 150000 | 12349.08
| MUSTANG - SW 5TH 138KV CKT 1 | 2018-06-01 | 2020-06-01 |  | Yes | 261500.33 | 128798.67 | 390299 | 500000 | 565761.198
| THOMAS TAP - WEATHERFORD 69KV CKT 1 | 2018-06-01 | 2020-06-01 |  | Yes | 2000000 |  | 2000000 | 2000000 | 3055971.588
[5 empty] | Total | 26460000 | 17600545 | 44060545 | 53761111 | 55500324.67
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84904909 | HARRINGTON STATION EAST BUS - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 2019-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total Revenue Requirements
84904909 | Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15 |  |  | 0 | 25788.41 | 25788.41 | 34240.2
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 0 | 201424.51 | 201424.51 | 667384.2
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 0 | 29590.08 | 29590.08 | 118615.8
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 0 | 38676.54 | 38676.54 | 113791.2
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12 |  |  | 0 | 165863.5 | 165863.5 | 213210.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 0 | 461343.04 | 461343.04 | 1147242
Customer | Study Number
BEPM | AG1-2017-018
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BEPM | 84885588 | WAUE | WAUE | 140 | 2017-12-01 | 2023-10-01 | 2018-10-01 | 2023-10-01 | 80000 | 0 | 617235.67 | 815264.438
[9 empty] | 80000 | 0 | 617235.67 | 815264.438
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885588 | DENISON - J6BOYER8 69.000 69KV CKT 1 | 2017-12-01 | 2018-10-01 |  |  | 80000 | 80000 | 153291.383
| EASTRUTH-CP7115.00 - MALLARD 115KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 379206 | 500000 | 461553.855
[5 empty] | Total | 459206 | 580000 | 614845.24
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84885588 | Fort Randall - Madison County 230kV Ckt 1 | 2013-12-23 | 2013-12-23 |  |  | 158029.67 | 200419.2
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 158029.67 | 200419.2
Customer | Study Number
BEPM | AG1-2017-019
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BEPM | 84885627 | WAUE | WAUE | 5 | 2018-04-01 | 401769 | 2018-04-01 | 401769 | 0 | 0 | 24364.54 | 912556.26
[9 empty] | 0 | 0 | 24364.54 | 912556.26
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885627 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84885627 | EVERLYN - K409HARTLYM869.000 69KV CKT 1 | 2022-10-01 | 2022-10-01
| EVERLYN - SPENCER 69KV CKT 1 | 2022-10-01 | 2022-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84885627 | Daglum - Dickinson 230kV CKT 1 | 2019-03-01 | 2019-03-01 |  |  | 23110.77 | 866610.36
| Kelly - Madison County 230kV Ckt 1 | 2014-11-01 | 2014-11-01 |  |  | 1253.77 | 45945.9
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 24364.54 | 912556.26
Customer | Study Number
BEPM | AG1-2017-020
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BEPM | 84885635 | WAUE | WAUE | 45 | 2017-12-01 | 2023-10-01 | 2017-12-01 | 2023-10-01 | 0 | 0 | 136079.64 | 155046.787
[9 empty] | 0 | 0 | 136079.64 | 155046.787
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885635 | EASTRUTH-CP7115.00 - MALLARD 115KV CKT 1 | 2022-10-01 | 2022-10-01 |  |  | 120794 | 500000 | 135928.387
[5 empty] | Total | 120794 | 500000 | 135928.39
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84885635 | Kelly - Madison County 230kV Ckt 1 | 2014-11-01 | 2014-11-01 |  |  | 15285.64 | 19118.4
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 15285.64 | 19118.4
Customer | Study Number
BRPS | AG1-2017-021
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BRPS | 84912692 | NPPD | NPPD | 19 | 2018-01-01 | 2028-01-01 | 2018-01-01 | 2028-01-01 | 1331706.13 | 0 | 1331706.13 | 1632432
[9 empty] | 1331706.13 | 0 | 1331706.13 | 1632432
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84912692 | None |  |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total Revenue Requirements
84912692 | Antelope - County Line - 115kV Rebuild | 2017-05-01 | 2017-05-01 |  |  | 29295.3 | 0 | 29295.3 | 35769.6
| Battle Creek - County Line 115kV Rebuild | 2017-05-01 | 2017-05-01 |  |  | 27945.17 | 0 | 27945.17 | 34120.8
| Neligh - Petersburg North 115kV Ckt 1 | 2012-11-09 | 2012-11-09 |  |  | 16319.05 | 0 | 16319.05 | 22671.6
| Rosemont 115kV Substation | 2017-11-01 | 2017-11-01 |  |  | 1258146.61 | 0 | 1258146.61 | 1539870
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 1331706.13 | 0 | 1331706.13 | 1632432
Customer | Study Number
FREM | AG1-2017-022
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
FREM | 84911097 | OPPD | OPPD | 5 | 2018-10-01 | 2028-10-01 | 2018-10-01 | 2028-10-01 | 0 | 1631073.6 | 0 | 0
[9 empty] | 0 | 1631073.6 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84911097 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change.
Customer | Study Number
KCPS | AG1-2017-023
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 84873359 | WPEK | KCPL | 50 | 2017-12-01 | 2031-12-01 | 2021-06-01 | 2031-12-01 | 0 | 0 | 1917459.43 | 3568742.1
[9 empty] | 0 | 0 | 1917459.43 | 3568742.1
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84873359 | None |  |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84873359 | WALKEMEYER TAP 345 KV SUBSTATION (SEPC) | 2017-12-01 | 2018-06-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84873359 | HOYT - JEFFREY ENERGY CENTER 345KV CKT 2 | 2018-06-01 | 2021-06-01
| LEXINGTON 161/69KV TRANSFORMER CKT 1 | 2019-06-01 | 2020-06-01 | 2019-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total Revenue Requirements
84873359 | FLATRDG3 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 0 | 20232.05 | 20232.05 | 150102.54
| Ft. Dodge - North Ft. Dodge 115 kV Ckt 2 | 2015-05-01 | 2015-05-01 |  |  | 0 | 257623.89 | 257623.89 | 370511.82
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 0 | 16363.93 | 16363.93 | 176505.84
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 0 | 1288.04 | 1288.04 | 8681.4
| MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 0 | 10045.99 | 10045.99 | 77852.88
| North Ft. Dodge - Spearville 115kV Ckt 2 | 2015-05-01 | 2015-05-01 |  |  | 0 | 557538.97 | 557538.97 | 801847.62
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 0 | 89653.85 | 89653.85 | 597039.66
| Spearville 345/115 kV Transformer CKT 1 | 2015-05-01 | 2015-05-01 |  |  | 0 | 927451.66 | 927451.66 | 1333852.38
| Woodward EHV 138kV Phase Shifting Transformer circuit #1 | 2017-08-02 | 2017-08-02 |  |  | 0 | 37261.05 | 37261.05 | 52347.96
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 0 | 1917459.43 | 1917459.43 | 3568742.1
Customer | Study Number
KCPS | AG1-2017-024
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 84885455 | WR | KCPL | 1 | 2017-12-01 | 2030-06-01 | 2017-12-01 | 2030-06-01 | 3380.61 | 0 | 3380.61 | 17166
[9 empty] | 3380.61 | 0 | 3380.61 | 17166
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885455 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84885455 | HOYT - JEFFREY ENERGY CENTER 345KV CKT 2 | 2018-06-01 | 2021-06-01
| LAWRENCE HILL (LAWH TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01
| LEXINGTON 161/69KV TRANSFORMER CKT 1 | 2019-06-01 | 2020-06-01 | 2019-10-01
| MIDLADS3 115.00 - MIDLAND JUNCTION 115KV CKT Z1 | 2022-06-01 | 2022-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84885455 | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | 2008-09-18 | 2008-09-18 |  |  | 633.44 | 3247.5
| 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | 2010-02-03 | 2010-02-03 |  |  | 678.13 | 3876
| JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1298.44 | 6520.5
| Kingfisher Co Tap - Mathewson 345kV CKT 1 | 2018-03-01 | 2018-03-01 |  |  | 369.19 | 465
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 287.64 | 2454
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 113.77 | 603
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 3380.61 | 17166
Customer | Study Number
KMEA | AG1-2017-025
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84875443 | MPS | SECI | 30 | 2018-03-01 | 2038-03-01 | 2018-03-01 | 2038-03-01 | 98340.08 | 0 | 98340.08 | 630470.4
[9 empty] | 98340.08 | 0 | 98340.08 | 630470.4
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84875443 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84875443 | Kingfisher Co Tap - Mathewson 345kV CKT 1 | 2018-03-01 | 2018-03-01 |  |  | 9636.7 | 13996.8
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 88703.38 | 616473.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 98340.08 | 630470.4
Customer | Study Number
KMEA | AG1-2017-026
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84877536 | MPS | SECI | 5 | 2019-01-01 | 2029-01-01 | 2019-01-01 | 2029-01-01 | 148604.75 | 0 | 148604.75 | 359114.4
[9 empty] | 148604.75 | 0 | 148604.75 | 359114.4
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84877536 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84877536 | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 6244.47 | 33124.8
| Ft. Dodge - North Ft. Dodge 115 kV Ckt 2 | 2015-05-01 | 2015-05-01 |  |  | 39907.84 | 52672.8
| Kingfisher Co Tap - Mathewson 345kV CKT 1 | 2018-03-01 | 2018-03-01 |  |  | 1552.21 | 1950
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 19713.16 | 100986
| MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 1959.52 | 11541.6
| North Ft. Dodge - Spearville 115kV Ckt 2 | 2015-05-01 | 2015-05-01 |  |  | 20074.54 | 26494.8
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 13191.5 | 70186.8
| Rice County 230/115 kV transformer Ckt 1 | 2012-10-01 | 2012-10-01 |  |  | 12568.04 | 18082.8
| Spearville 345/115 kV Transformer CKT 1 | 2015-05-01 | 2015-05-01 |  |  | 33393.47 | 44074.8
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 148604.75 | 359114.4
Customer | Study Number
KMEA | AG1-2017-027
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84884608 | SPA | WR | 1 | 2017-12-01 | 2028-06-01 | 2017-12-01 | 2028-06-01 | 52644.63 | 0 | 52644.63 | 132385.3146
[9 empty] | 52644.63 | 0 | 52644.63 | 132385.31
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84884608 | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 |  | 50297 | 6000000 | 120484.6146
[5 empty] | Total | 50297 | 6000000 | 120484.61
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84884608 | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01
| WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84884608 | COFFEYVILLE TAP - DEARING 138KV CKT 1 (WR) #2 | 2010-06-09 | 2010-06-09 |  |  | 1 | 1.26
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 260.57 | 1064.7
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 237.51 | 1882.44
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 1682.04 | 8309.7
| SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 117.15 | 462.42
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 50.04 | 180.18
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 2348.31 | 11900.7
Customer | Study Number
KMEA | AG1-2017-028
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84885203 | NPPD | WR | 1 | 2017-12-01 | 2054-10-01 | 2017-12-01 | 2054-10-01 | 21169.04 | 0 | 21169.04 | 101470.7356
[9 empty] | 21169.04 | 0 | 21169.04 | 101470.74
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885203 | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 |  | 20920 | 6000000 | 100233.1356
[5 empty] | Total | 20920 | 6000000 | 100233.14
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84885203 | STORLA (KV1A) 230/115/13.2KV TRANSFORMER CKT 1 | 2018-10-01 | 2019-10-01
| WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01
| WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84885203 | Kelly - Madison County 230kV Ckt 1 | 2014-11-01 | 2014-11-01 |  |  | 200.33 | 388.96
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 48.71 | 848.64
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 249.04 | 1237.6
Customer | Study Number
KMEA | AG1-2017-029
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84885381 | MPS | KCPL | 5 | 2018-03-01 | 2028-03-01 | 2018-03-01 | 2028-03-01 | 868.7 | 0 | 868.7 | 6908.4
[9 empty] | 868.7 | 0 | 868.7 | 6908.4
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885381 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84885381 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 868.7 | 6908.4
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 868.7 | 6908.4
Customer | Study Number
KMEA | AG1-2017-030
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84885945 | MPS | KCPL | 20 | 2019-01-01 | 2029-01-01 | 2019-01-01 | 2029-01-01 | 3118.46 | 0 | 3118.46 | 26688
[9 empty] | 3118.46 | 0 | 3118.46 | 26688
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885945 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84885945 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 3118.46 | 26688
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 3118.46 | 26688
Customer | Study Number
KMEA | AG1-2017-031
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84906139 | MPS | WR | 1 | 2020-01-01 | 2040-01-01 | 2020-01-01 | 2040-01-01 | 91.29 | 0 | 91.29 | 741.6
[9 empty] | 91.29 | 0 | 91.29 | 741.6
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84906139 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84906139 | NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 91.29 | 741.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 91.29 | 741.6
Customer | Study Number
KMEA | AG1-2017-032
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 84906152 | MPS | WR | 1 | 2020-01-01 | 2040-01-01 | 2020-01-01 | 2040-01-01 | 91.29 | 0 | 91.29 | 741.6
[9 empty] | 91.29 | 0 | 91.29 | 741.6
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84906152 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84906152 | NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 91.29 | 741.6
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 91.29 | 741.6
Customer | Study Number
MEAN | AG1-2017-033
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MEAN | 84903949 | NPPD | MEC | 10 | 2018-01-01 | 2019-01-01 | 2018-01-01 | 2019-01-01 | 0 | 392493.96 | 0 | 0
[9 empty] | 0 | 392493.96 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84903949 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Customer | Study Number
MIDW | AG1-2017-034
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 84911381 | SPA | WR | 1 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 2183.53 | 0 | 2183.53 | 13405.85
[9 empty] | 2183.53 | 0 | 2183.53 | 13405.85
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84911381 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84911381 | HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 176.29 | 890.44
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 83.01 | 817.55
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 1890.37 | 11548.14
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 33.86 | 149.72
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 2183.53 | 13405.85
Customer | Study Number
MIDW | AG1-2017-035
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 84912544 | WR | WR | 1 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 2013.32 | 0 | 2013.32 | 12265.22
[9 empty] | 2013.32 | 0 | 2013.32 | 12265.22
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84912544 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84912544 | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 421.87 | 2616.16
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 1458.93 | 8736.95
| MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 132.52 | 912.11
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 2013.32 | 12265.22
Customer | Study Number
MIDW | AG1-2017-036
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 84912549 | SPA | WR | 1 | 2018-01-01 | 2034-06-01 | 2018-01-01 | 2034-06-01 | 1411.51 | 0 | 1411.51 | 8642.39
[9 empty] | 1411.51 | 0 | 1411.51 | 8642.39
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84912549 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84912549 | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 140.96 | 874.68
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 72.53 | 366.42
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 32 | 315.2
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 395.9 | 2371.88
| MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01 |  |  | 44.28 | 305.35
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 711.91 | 4347.79
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 13.93 | 61.07
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 1411.51 | 8642.39
Customer | Study Number
NPPM | AG1-2017-037
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
NPPM | 84863769 | NPPD | NPPD | 32 | 2018-01-01 | 2025-04-01 | 2020-06-01 | 2027-09-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84863769 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84863769 | FT RANDAL - SPENCER 115KV CKT 1 | 2018-06-01 | 2020-06-01
Customer | Study Number
NPPM | AG1-2017-038
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
NPPM | 84863943 | NPPD | NPPD | 36 | 2018-01-01 | 2025-04-01 | 2020-06-01 | 2027-09-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84863943 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84863943 | FT RANDAL - SPENCER 115KV CKT 1 | 2018-06-01 | 2020-06-01
Customer | Study Number
OTPW | AG1-2017-039
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OTPW | 84906479 | OTP | WAUE | 49 | 2018-01-01 | 401769 | 2018-01-01 | 401769 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84906479 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Customer | Study Number
OTPW | AG1-2017-040
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OTPW | 84906636 | OTP | WAUE | 49 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84906636 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Customer | Study Number
OTPW | AG1-2017-041
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OTPW | 84906754 | OTP | WAUE | 15 | 2018-01-01 | 401769 | 2018-01-01 | 401769 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84906754 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Customer | Study Number
OTPW | AG1-2017-042
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OTPW | 84910586 | OTP | WAUE | 15 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84910586 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Customer | Study Number
PEC | AG1-2017-043
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
PEC | 84885681 | WFEC | WFEC | 50 | 2018-01-01 | 2023-01-01 | 2018-01-01 | 2023-01-01 | 178.52 | 0 | 8865717.61 | 9699400.734
[9 empty] | 178.52 | 0 | 8865717.61 | 9699400.734
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84885681 | MUSTANG - SW 5TH 138KV CKT 1 | 2018-06-01 | 2020-06-01 |  |  | 0 | 109701 | 109701 | 500000 | 160257.534
| GLASSES - RUSSETT 138KV CKT 1 | 2022-06-01 | 2022-06-01 |  |  | 0 | 8000000 | 8000000 | 8000000 | 8207179.2
[5 empty] | Total | 0 | 8109701 | 8109701 | 8500000 | 8367436.734
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84885681 | HARRINGTON STATION EAST BUS - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 2019-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total Revenue Requirements
84885681 | BROWN - EXPLORER TAP 138KV CKT 1 | 2008-06-01 | 2008-06-01 |  |  | 178.52 | 0 | 178.52 | 999.6
| Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15 |  |  | 0 | 10034.67 | 10034.67 | 13359.6
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 0 | 21947.7 | 21947.7 | 73240.8
| HUGO 345/138KV TRANSFORMER CKT 1 | 2012-07-01 | 2012-07-01 |  |  | 0 | 48202.89 | 48202.89 | 159711.6
| Lake Creek - Lone Wolf 69kV Ckt 1 Current Transformers | 2015-08-08 | 2015-08-08 |  |  | 0 | 484510.92 | 484510.92 | 569775
| NORTHWEST - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01 |  |  | 0 | 96674.09 | 96674.09 | 390295.2
| Valliant 345 kV (AEP) | 2012-04-17 | 2012-04-17 |  |  | 0 | 4215.93 | 4215.93 | 12488.4
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12 |  |  | 0 | 64544.58 | 64544.58 | 83193.6
| Woodward EHV 138kV Phase Shifting Transformer circuit #1 | 2017-08-02 | 2017-08-02 |  |  | 0 | 25707.31 | 25707.31 | 28900.2
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 178.52 | 755838.09 | 756016.61 | 1331964
Customer | Study Number
SPSM | AG1-2017-044
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 84730363 | SPS | SPS | 16 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 16121.51 | 0 | 16121.51 | 20336.79
[9 empty] | 16121.51 | 0 | 16121.51 | 20336.79
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84730363 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84730363 | CARLISLE INTERCHANGE - MURPHY SUB 115KV CKT 1 | 2022-06-01 | 2022-06-01
| DENVER CITY INTERCHANGE N. - XTO_RUSSEL 3115.00 115KV CKT 1 | 2022-10-01 | 2022-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84730363 | Harrington Mid - Nichols 230 kV Ckt 2 | 2012-12-01 | 2012-12-01 |  |  | 4480.47 | 6021.31
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01 |  |  | 4625.88 | 6216.51
| Plant X - Tolk 230kV rebuild circuit #1 | 2017-12-31 | 2017-12-31 |  |  | 1117.41 | 1288.93
| Plant X - Tolk 230kV rebuild circuit #2 | 2017-12-31 | 2017-12-31 |  |  | 1103.29 | 1272.46
| Power System Stabilizers in SPS | 2014-11-30 | 2014-11-30 |  |  | 66.47 | 83.57
| TUCO Interchange 345/230kV CKT 1 Replacement | 2018-06-01 | 2018-06-01 |  |  | 4727.99 | 5454.01
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 16121.51 | 20336.79
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
SPSM | AG1-2017-045
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 84734700 | SPS | SPS | 17 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 9749.82 | 0 | 9749.82 | 13096.09
[9 empty] | 9749.82 | 0 | 9749.82 | 13096.09
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84734700 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84734700 | CARLISLE INTERCHANGE - MURPHY SUB 115KV CKT 1 | 2022-06-01 | 2022-06-01
| DENVER CITY INTERCHANGE N. - XTO_RUSSEL 3115.00 115KV CKT 1 | 2022-10-01 | 2022-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84734700 | Harrington Mid - Nichols 230 kV Ckt 2 | 2012-12-01 | 2012-12-01 |  |  | 4760.21 | 6397.07
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01 |  |  | 4914.85 | 6605.08
| Power System Stabilizers in SPS | 2014-11-30 | 2014-11-30 |  |  | 74.76 | 93.94
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 9749.82 | 13096.09
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
SPSM | AG1-2017-046
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 84734856 | SPS | SPS | 21 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 12127.61 | 0 | 12127.61 | 16283.95
[9 empty] | 12127.61 | 0 | 12127.61 | 16283.95
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84734856 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84734856 | CARLISLE INTERCHANGE - MURPHY SUB 115KV CKT 1 | 2022-06-01 | 2022-06-01
| DENVER CITY INTERCHANGE N. - XTO_RUSSEL 3115.00 115KV CKT 1 | 2022-10-01 | 2022-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84734856 | Harrington Mid - Nichols 230 kV Ckt 2 | 2012-12-01 | 2012-12-01 |  |  | 5881.48 | 7904.38
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01 |  |  | 6072.13 | 8160.58
| Power System Stabilizers in SPS | 2014-11-30 | 2014-11-30 |  |  | 174 | 218.99
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 12127.61 | 16283.95
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
SPSM | AG1-2017-047
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 84734992 | SPS | SPS | 58 | 2019-06-01 | 2024-07-01 | 2019-06-01 | 2024-07-01 | 33492.73 | 0 | 33492.73 | 44971.03
[9 empty] | 33492.73 | 0 | 33492.73 | 44971.03
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84734992 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84734992 | CARLISLE INTERCHANGE - MURPHY SUB 115KV CKT 1 | 2022-06-01 | 2022-06-01
| DENVER CITY INTERCHANGE N. - XTO_RUSSEL 3115.00 115KV CKT 1 | 2022-10-01 | 2022-10-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total Revenue Requirements
84734992 | Harrington Mid - Nichols 230 kV Ckt 2 | 2012-12-01 | 2012-12-01 |  |  | 16243.89 | 21830.68
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01 |  |  | 16768.29 | 22535.23
| Power System Stabilizers in SPS | 2014-11-30 | 2014-11-30 |  |  | 480.55 | 605.12
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 33492.73 | 44971.03
**Note: CPOs for creditable upgrade(s) may be required based on completion of GI review.
Customer | Study Number
WRGS | AG1-2017-048
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 84877548 | WR | WR | 50 | 2017-12-01 | 2024-01-01 | 2019-10-01 | 2025-11-01 | 3324.52 | 0 | 9483991.9 | 14614136.742
[9 empty] | 3324.52 | 0 | 9483991.9 | 14614136.742
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84877548 | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 | Yes | 0 | 3900515 | 3900515 | 6000000 | 8072495.782
[5 empty] | Total | 0 | 3900515 | 3900515 | 6000000 | 8072495.78
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84877548 | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 | Yes
| WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 | Yes
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total Revenue Requirements
84877548 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 0 | 14294.83 | 14294.83 | 95512.47
| Tap Wichita - Thistle 345 kV Ckt 1 & 2 - Pratt Addition (NU) | 2016-12-31 | 2016-12-31 |  |  | 3324.52 | 0 | 3324.52 | 3847.83
| Tap Wichita - Thistle 345 kV Ckt 1 & 2 - Pratt Co Addition (NU) | 2016-10-16 | 2016-10-16 |  |  | 0 | 5565857.55 | 5565857.55 | 6442280.66
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change. |  |  |  |  | Total | 3324.52 | 5580152.38 | 5583476.9 | 6541640.96
Customer | Study Number
WRGS | AG1-2017-049
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 84877556 | WR | WR | 26 | 2017-12-01 | 2023-12-01 | 2019-10-01 | 2025-10-01 | 3439.43 | 0 | 3478625.26 | 5906198.736
[9 empty] | 3439.43 | 0 | 3478625.26 | 5906198.736
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
84877556 | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 | Yes | 0 | 2028268 | 2028268 | 6000000 | 4188903.696
[5 empty] | Total | 0 | 2028268 | 2028268 | 6000000 | 4188903.7
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
84877556 | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 | Yes
| WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | 2018-06-01 | 2020-06-01 | 2019-10-01 | Yes
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total Revenue Requirements
84877556 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01 |  |  | 0 | 7433.45 | 7433.45 | 49501.44
| Tap Wichita - Thistle 345 kV Ckt 1 & 2 - Pratt Addition (NU) | 2016-12-31 | 2016-12-31 |  |  | 3439.43 | 0 | 3439.43 | 3975.12
| Tap Wichita - Thistle 345 kV Ckt 1 & 2 - Pratt Co Addition (NU) | 2016-10-16 | 2016-10-16 |  |  | 0 | 1439484.38 | 1439484.38 | 1663818.48
[5 empty] | Total | 3439.43 | 1446917.83 | 1450357.26 | 1717295.04
*Note: CPOs may be calculated based on estimated upgrade cost and are subject to change.

## Table4
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
AEPW | 52ND & DELAWARE WEST TAP - RIVERSIDE STATION 138KV CKT 1 | Rebuild to 1272 ACSR and replace station equipment on both ends. | 2019-06-01 | 2022-06-01 | 25000000
AEPW | 52ND & DELAWARE WEST TAP - TULSA POWER STATION 138KV CKT 1 | Rebuild to 1272 ACSR and replace station equipment on both ends. | 2019-06-01 | 2022-06-01 | 16111111
AEPW | ARSENAL HILL - RAINES 138KV CKT 1 | Rebuild to 1272 ACSR and replace station equipment on both ends. | 2022-10-01 | 2022-10-01 | 10000000
AEPW | THOMAS TAP - WEATHERFORD 69KV CKT 1 | Rebuild to 477 ACSR and replace station equipment on both ends. | 2018-06-01 | 2020-06-01 | 2000000
BEPC | EASTRUTH-CP7115.00 - MALLARD 115KV CKT 1 | Rebuild 9.5 miles of 115 kV transmission line from East Ruth to Mallard. | 2022-10-01 | 2022-10-01 | 500000
OKGE | GLASSES - RUSSETT 138KV CKT 1 | Rebuild & re-conductor transmission line to 795mcm conductor. Replace wavetrap and line relays. | 2022-06-01 | 2022-06-01 | 8000000
OKGE | MUSTANG - SW 5TH 138KV CKT 1 | Replace switches, traps, and CTs within Mustang & SW 5th Substations. | 2018-06-01 | 2020-06-01 | 500000
WAPA | DENISON - J6BOYER8 69.000 69KV CKT 1 | Replace Denison bus jumpers (terminal for NIPCO J6 line). | 2017-12-01 | 2018-10-01 | 80000
WERE | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | Replace Wichita (WICH TX-11) 345/138/13.8 kV transformer with 616 MVA transformer. | 2018-06-01 | 2020-06-01 | 6000000
WFEC | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | Upgrade Hugo switch relay, Breaker 472 Bushing CTs, and Breaker 3472 Bushing CTs from 1200 to 2000A. | 2022-10-01 | 2022-10-01 | 150000
Expansion Plan Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
SUNC | WALKEMEYER TAP 345 KV SUBSTATION (SEPC) | Tap the existing 345 kV line from Finney to Hitchland to construct the new Walkemeyer Tap substation. Install any necessary 345 kV terminal equipment. Install new 345/115 kV transformer at the new Walkemeyer Tap substation. Install any necessary 115 kV terminal equipment. Construct new 1-mile 115 kV line from Walkemeyer to the new Walkemeyer Tap substation. Install any 115 kV terminal equipment at the existing Walkemeyer substation necessary to accommodate terminations of new 115 kV lines from the new Walkemeyer Tap substation and North Liberal. Construct new 21-mile 115 kV line from North Liberal to Walkemeyer. Install any 115 kV terminal equipment at the existing North Liberal substation necessary to accommodate termination of new 115 kV line from Walkemeyer. | 2017-12-01 | 2018-06-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AEPW | ONETA - ONETA ENERGY CENTER 345KV CKT 1 | Rebuild to 2-1590 ACSR and replace station equipment. | 2022-06-01 | 2022-06-01
AEPW | ONETA - ONETA ENERGY CENTER 345KV CKT 2 | Rebuild to 2-1590 ACSR and replace station equipment. | 2022-06-01 | 2022-06-01
BEPC | EVERLYN - K409HARTLYM869.000 69KV CKT 1 | Reconductor 7.5 miles of 69 kV line from Everlyn to Hartley. | 2022-10-01 | 2022-10-01
BEPC | STORLA (KV1A) 230/115/13.2KV TRANSFORMER CKT 1 | Replace 230/115/13.2 kV transformer with 200/250 MVA. | 2018-10-01 | 2019-10-01
KCPL | LEXINGTON 161/69KV TRANSFORMER CKT 1 | Replace Lexington 161/69 kV transformer with 100/110 MVA transformer. | 2019-06-01 | 2020-06-01
SPS | CARLISLE INTERCHANGE - MURPHY SUB 115KV CKT 1 | Upgrade terminal limitations on circuit V40, Carlisle-Murphy. | 2022-06-01 | 2022-06-01
SPS | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | Replace terminal equipment. | 2022-10-01 | 2022-10-01
SPS | DENVER CITY INTERCHANGE N. - XTO_RUSSEL 3115.00 115KV CKT 1 | Upgrade terminal limitations on circuit T89, Denver City to XTO-Russell. | 2022-10-01 | 2022-10-01
SPS | FLOYD COUNTY INTERCHANGE - TUCO INTERCHANGE 115KV CKT 1 | Upgrade terminal limitations on circuit T68, Tuco-Floyd County. | 2022-06-01 | 2022-06-01
SPS | HARRINGTON STATION EAST BUS - POTTER COUNTY INTERCHANGE 230KV CKT 1 | Upgrade terminal equipment at both Potter Co. and Harrington 230 kV substations. | 2019-06-01 | 2019-06-01
SPS | TOLK STATION TAP - TOLK STATION WEST 230KV CKT @1 | Rebuild Tolk 230 kV bus to double-bus, double-breaker. | 2022-06-01 | 2022-12-31
WAPA | EVERLYN - SPENCER 69KV CKT 1 | Change relay setting. Replace breaker and CTs at WAPA Spencer 69 kV. | 2022-10-01 | 2022-10-01
WAPA | FT RANDAL - SPENCER 115KV CKT 1 | Add 2nd Ft. Randall-Spencer 115 kV line. | 2018-06-01 | 2020-06-01
WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 2 | Add 2nd Hoyt - Jeffrey Energy Center 345 kV transmission line. | 2018-06-01 | 2021-06-01
WERE | LAWRENCE HILL (LAWH TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | Replace existing TX with a 440 MVA emergency rated dual high side LAWH 345/230-115 kV TX. | 2018-06-01 | 2020-06-01
WERE | MIDLADS3 115.00 - MIDLAND JUNCTION 115KV CKT Z1 | Replace limiting 750 CU Bus (201/240 MVA) with 1590 AAC Bus (255/308 MVA). | 2022-06-01 | 2022-06-01
WERE | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | Replace Wichita (WICH TX-11) 345/138/13.8 kV transformer with 616 MVA transformer. | 2018-06-01 | 2020-06-01
WERE | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | Replace Wichita (WICH TX-12) 345/138/13.8 kV transformer with 616 MVA transformer. | 2018-06-01 | 2020-06-01
Network Upgrades requiring credits per Attachment Z2 of the SPP OATT.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC) | Total Gross CPO Allocation
AEPM | Terry Road 345kV Station (NU) | Construct the 345 kV Terry Road switching station including a three breaker ring bus configured for future expansion to breaker-and-a-half. The Terry Road switching station will be located on property acceptable to Transmission Owner in the vicinity of t | 2016-11-16 | 2016-11-16 | 19929906.9
AEPM | Valliant 345 kV (AEP) | Install 345 kV terminal equipment at Valliant substation. | 2012-04-17 | 2012-04-17 | 1690073.63
BEPM | Daglum - Dickinson 230kV CKT 1 | Build new 230kV line from Daglum - Dickinson | 2019-03-01 | 2019-03-01 | 866610.36
EDE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | Reconductor 11.9 miles of Oronogo Jct. to Riverton 161kV Ckt. 1 from 556 ACSR to 795 ACSR, change CT settings @ Oronogo, and replace wavetrap. | 2011-06-01 | 2011-06-01 | 462.42
ITCM | HUGO - VALLIANT 345KV CKT 1 | Install new line from Valliant 345 kV to Hugo Power Plant with 19 miles of bundled 1590 ACSR conductior. | 2012-07-01 | 2012-07-01 | 9892480.26
ITCM | HUGO 345/138KV TRANSFORMER CKT 1 | Install new line from Valliant 345 kV to Hugo Power Plant with 19 miles of bundled 1590 ACSR conductior. Note that ITC is building the line from Valiant to Hugo. | 2012-07-01 | 2012-07-01 | 1690854
KCPL | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | 2006-06-01 | 2006-06-01 | 361433.98
MIDW | Rice County 230/115 kV transformer Ckt 1 | Install 230/115 kV transformer at Rice County. | 2012-10-01 | 2012-10-01 | 18082.8
MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | 2011-06-01 | 2013-06-01 | 88686.72
MKEC | FLATRDG3 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 2009-12-01 | 2013-06-01 | 150102.54
MKEC | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | 2009-12-01 | 2013-06-01 | 36615.64
MKEC | Ft. Dodge - North Ft. Dodge 115 kV Ckt 2 | Build appoximately 0.5 mile 115 kV line | 2015-05-01 | 2015-05-01 | 423184.62
MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 (MKEC) | Rebuild 43.5% Ownership of 20.9 miles | 2013-06-01 | 2013-06-01 | 9148.32
MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | 2009-12-01 | 2013-06-01 | 120776.23
MKEC | MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 | Upgrade transformer | 2009-12-01 | 2013-06-01 | 90611.94
MKEC | North Ft. Dodge - Spearville 115kV Ckt 2 | Build appoximately 20 mile 115 kV line | 2015-05-01 | 2015-05-01 | 828342.42
MKEC | Spearville 345/115 kV Transformer CKT 1 | Spearville Substation - Add 345/115kV autotransformer and 345kV and 115kV terminal positions for autotransformer. | 2015-05-01 | 2015-05-01 | 1377927.18
NPPD | Albion - Petersburg 115kV Ckt 1 Hansford Upgrade | Replace Breaker Switch 1106-D & jumpers; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | 2012-12-31 | 2012-12-31 | 951
NPPD | Antelope - County Line - 115kV Rebuild | Rebuild/Upgrade the Antelope – County Line 115kV to rerate line segments to greater than 125 MVA. | 2017-05-01 | 2017-05-01 | 35769.6
NPPD | Battle Creek - County Line 115kV Rebuild | Rebuild/Upgrade the Battle Creek – County Line 115kV to rerate line segments to greater than 125 MVA. | 2017-05-01 | 2017-05-01 | 34120.8
NPPD | Fort Randall - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320 MVA | 2013-12-23 | 2013-12-23 | 200419.2
NPPD | Kelly - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320MVA | 2014-11-01 | 2014-11-01 | 68327.26
NPPD | Neligh - Petersburg North 115kV Ckt 1 | Replace Breaker 1106, jumpers, & 115kV Switch 1106-D2; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | 2012-11-09 | 2012-11-09 | 36484.8
NPPD | Rosemont 115kV Substation | 115kV Substation addition to accommodate new 115kV interconnection & 115kV breakers at Guide Rock due to addition of Rosemont 115kV Substation | 2017-11-01 | 2017-11-01 | 1539870
OKGE | Beaver County 345kV Substation | 345kV ring bus substation including: five (5) 345kV circuit breakers, line relaying, disconnect switches, and associated equipment. | 2014-09-29 | 2014-09-29 | 9484183.2
OKGE | Beaver County 345kV Substation Addition | 345kV line terminal including one (1) 345kV circuit breaker, line relaying, disconnect switches, and associated equipment | 2014-11-14 | 2014-11-14 | 281535
OKGE | Beaver County Substation - Add 345kV terminal for Ochiltree | Convert from ring bus to breaker-and-a-half configuration by installing additional rung to the existing bus layout and install five (5) 345 kV, 3000 Amp breakers, line relaying, disconnect switches, and associated equipment. | 2017-09-27 | 2017-09-27 | 2324233.2
OKGE | BROWN - EXPLORER TAP 138KV CKT 1 | UPGRADE CT AT BROWN NEXT LIMIT CONDUCTOR 133/156 | 2008-06-01 | 2008-06-01 | 999.6
OKGE | Gracemont 138kV line terminal addition | 138kV line terminal at Gracemont substation, including breaker, line relaying, disconnect switches and associated equipment, dead end structures, revenue metering with CT's and PT's. | 2011-10-15 | 2011-10-15 | 47599.8
OKGE | Kingfisher Co Tap - Mathewson 345kV CKT 1 | Replace terminal equipment to achieve conductor limit | 2018-03-01 | 2018-03-01 | 446390.36
OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 345 kV line | 2010-01-01 | 2010-01-01 | 16385300.88
OKGE | Sunnyside Relays for Grady Interconnection | Sunnyside (OG&E) 345kV Substation: Verify relay settings are compatible with relays at Transmission Owner 345 kV Interconnection Substation. | 2016-11-23 | 2016-11-23 | 34101
OKGE | Woodward EHV 138kV Phase Shifting Transformer circuit #1 | Install one (1) 138 kV phase shifting transformer along with upgrading relay, protective, and metering equipment, and all associated and miscellaneous materials. | 2017-08-02 | 2017-08-02 | 1550255.16
SPS | Harrington Mid - Nichols 230 kV Ckt 2 | Reconductor Harrington Mid - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | 2012-12-01 | 2012-12-01 | 51213.16
SPS | Harrington West - Nichols 230kV Ckt 1 | Reconductor Harrington West - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | 2012-12-01 | 2012-12-01 | 171562.78
SPS | Plant X - Tolk 230kV rebuild circuit #1 | Rebuild Plant X – Tolk 230kV transmission circuit #1 which is approximately 10 miles in length. The existing 795 MCM ACSR conductor will be replaced with 995 MCM ACCS conductor along with upgrading associated disconnect switches, structural steel, foundat | 2017-12-31 | 2017-12-31 | 1288.93
SPS | Plant X - Tolk 230kV rebuild circuit #2 | Rebuild Plant X – Tolk 230kV transmission circuit #2 which is approximately 10 miles in length. The existing 795 MCM ACSR conductor will be replaced with 995 MCM ACCS conductor along with upgrading associated disconnect switches, structural steel, foundat | 2017-12-31 | 2017-12-31 | 1272.46
SPS | Power System Stabilizers in SPS | Install Power System Stabilizers (PSS) at Tolk (Units: 1,2) and Jones (Units: 1,2,3). | 2014-11-30 | 2014-11-30 | 17462.62
SPS | TUCO Interchange 345/230kV CKT 1 Replacement | The existing 345/230kV 560/560MVA autotransformer at Tuco Substation will be replaced with a new transformer unit to match the other transformer at this site. The new transformer can be installed at Tuco Substation by removing the existing transformer fro | 2018-06-01 | 2018-06-01 | 325257.86
WERE | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | Rebuild 166th Street - Jaggard Junction 115 kV line. | 2008-09-18 | 2008-09-18 | 3247.5
WERE | 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | Rebuild Jarbalo - 166th Street 115 kV line. | 2010-02-03 | 2010-02-03 | 3876
WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 (WR) #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers with a minimum 2000 amp emergency rating equipment | 2010-06-09 | 2010-06-09 | 1.26
WERE | JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | Rebuild Jaggard Junction - Pentagon 115 kV line. | 2009-06-01 | 2009-06-01 | 6520.5
WERE | Tap Wichita - Thistle 345 kV Ckt 1 & 2 - Pratt Addition (NU) | Pratt relaying settings changes at the new 345kV switching station identified for Pratt Co. | 2016-12-31 | 2016-12-31 | 7822.95
WERE | Tap Wichita - Thistle 345 kV Ckt 1 & 2 - Pratt Co Addition (NU) | 345 kV Breaker and Half Substation (No metering or customer equipment); Eight (8) 345 kV Breakers; Twenty (20) 345 kV switches; Two (2) 345 kV reactor switches; Fourteen (14) VTs; Two (2) 345 kV 50 Mvar line reactors; New redundant primary relaying, relay | 2016-10-16 | 2016-10-16 | 8106099.14
WFEC | Lake Creek - Lone Wolf 69kV Ckt 1 Current Transformers | Replace current transformers at Lake Creek and Lone Wolf substation | 2015-08-08 | 2015-08-08 | 569775
WFEC | WASHITA - GRACEMONT 138 KV CKT 2 | BUILD WASHITA - GRACEMONT 138KV CKT 2 (APPROXIMATELY 7 MILES). ADD LINE TERMINAL AT WASHITA AND PROCURE RIGHT OF WAY. | 2012-10-12 | 2012-10-12 | 296404.2
*Note: CPOs may be calculated based on upgrade(s) currently in study and/or estimated upgrade cost(s), which may be subject to change.

## Table5
Transmission Owner | UpgradeName | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
None

## Table6
Upgrade: | MUSTANG - SW 5TH 138KV CKT 1
Limiting Facility: | MUSTANG - SW 5TH 138KV CKT 1
Direction: | FROM->TO
Line Outage: | DAYTON - HOBBY LOBBY 138KV CKT 1
Flowgate: | 2017AG1AFS11T7815518SP
Date Redispatch Needed: | Starting 2018 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2018 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
84904909 | 2.4 | 2.4
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.31708 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.31708 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.31708 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.31708 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.31708 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.31708 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.31708 | 8
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28404 | 9
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28404 | 9
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28404 | 9
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28404 | 9
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28404 | 9
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.28404 | 9
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.28404 | 9
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25978 | 9
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25978 | 9
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25978 | 9
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25978 | 9
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25978 | 9
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.25978 | 9
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.25978 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25786 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25786 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25786 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25786 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25786 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.25786 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.25786 | 9
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28517 | 9
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28517 | 9
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28517 | 9
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28517 | 9
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.28517 | 9
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.28517 | 9
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.28517 | 9
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.01024 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25552 | 10
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.01024 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25552 | 10
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.01024 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25552 | 10
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.01024 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25552 | 10
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.01024 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25552 | 10
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.01024 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.25552 | 10
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.01024 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.25552 | 10
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24198 | 10
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24198 | 10
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24198 | 10
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24198 | 10
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24198 | 10
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24198 | 10
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24198 | 10
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24862 | 10
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24862 | 10
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24862 | 10
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24862 | 10
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24862 | 10
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24862 | 10
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24862 | 10
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24863 | 10
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24863 | 10
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24863 | 10
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24863 | 10
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24863 | 10
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24863 | 10
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24863 | 10
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00958 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25486 | 10
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00958 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25486 | 10
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00958 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25486 | 10
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00958 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25486 | 10
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00958 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25486 | 10
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00958 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.25486 | 10
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00958 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.25486 | 10
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23357 | 10
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23357 | 10
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23357 | 10
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23357 | 10
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23357 | 10
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23357 | 10
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23357 | 10
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24045 | 10
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24045 | 10
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2478 | 10
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2478 | 10
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2478 | 10
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2478 | 10
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2478 | 10
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2478 | 10
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2478 | 10
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23837 | 10
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23837 | 10
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23837 | 10
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23837 | 10
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23837 | 10
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23837 | 10
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23837 | 10
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24024 | 10
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24024 | 10
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24024 | 10
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24024 | 10
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24024 | 10
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24223 | 10
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24223 | 10
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23855 | 10
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23855 | 10
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23855 | 10
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23855 | 10
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23855 | 10
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23855 | 10
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23855 | 10
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24045 | 10
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24045 | 10
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24045 | 10
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24223 | 10
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24223 | 10
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24223 | 10
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24202 | 10
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24202 | 10
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24202 | 10
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24202 | 10
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24202 | 10
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24202 | 10
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24202 | 10
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23814 | 10
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23814 | 10
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23814 | 10
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23814 | 10
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23814 | 10
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23814 | 10
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23814 | 10
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2381 | 10
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2381 | 10
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2381 | 10
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2381 | 10
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2381 | 10
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2381 | 10
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2381 | 10
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2383 | 10
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2383 | 10
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23928 | 10
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23928 | 10
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23928 | 10
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23928 | 10
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23928 | 10
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23928 | 10
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23928 | 10
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2439 | 10
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2439 | 10
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2439 | 10
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2439 | 10
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2439 | 10
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2439 | 10
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2439 | 10
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24714 | 10
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24714 | 10
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24714 | 10
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24714 | 10
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24714 | 10
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24714 | 10
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24714 | 10
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24896 | 10
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24896 | 10
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24591 | 10
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24591 | 10
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24591 | 10
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24591 | 10
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24591 | 10
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24591 | 10
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24591 | 10
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23951 | 10
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23951 | 10
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23951 | 10
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23951 | 10
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23951 | 10
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23951 | 10
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23951 | 10
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23778 | 10
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23778 | 10
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24762 | 10
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24762 | 10
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24762 | 10
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24762 | 10
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24762 | 10
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24762 | 10
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24762 | 10
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24553 | 10
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24553 | 10
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24553 | 10
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24553 | 10
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24553 | 10
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24553 | 10
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24553 | 10
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24925 | 10
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24925 | 10
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24925 | 10
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24925 | 10
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24925 | 10
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24925 | 10
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24925 | 10
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23774 | 10
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23774 | 10
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23774 | 10
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23774 | 10
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23774 | 10
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23774 | 10
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23774 | 10
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24517 | 10
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24517 | 10
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24517 | 10
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24517 | 10
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24517 | 10
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24517 | 10
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24517 | 10
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23561 | 10
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23561 | 10
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23561 | 10
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23561 | 10
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23561 | 10
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23561 | 10
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23561 | 10
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23813 | 10
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23813 | 10
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2398 | 10
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2398 | 10
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2398 | 10
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2398 | 10
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2398 | 10
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2398 | 10
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2398 | 10
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23982 | 10
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23982 | 10
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23982 | 10
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23982 | 10
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23982 | 10
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23982 | 10
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23982 | 10
SWPA | KENNETT 69KV | 5.3 | 9e-05 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24519 | 10
SWPA | KENNETT 69KV | 5.3 | 9e-05 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24519 | 10
SWPA | KENNETT 69KV | 5.3 | 9e-05 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24519 | 10
SWPA | KENNETT 69KV | 5.3 | 9e-05 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24519 | 10
SWPA | KENNETT 69KV | 5.3 | 9e-05 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24519 | 10
SWPA | KENNETT 69KV | 5.3 | 9e-05 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24519 | 10
SWPA | KENNETT 69KV | 5.3 | 9e-05 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24519 | 10
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24551 | 10
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24551 | 10
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24551 | 10
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24551 | 10
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24551 | 10
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24551 | 10
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24893 | 10
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24893 | 10
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24893 | 10
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24893 | 10
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24893 | 10
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24893 | 10
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24893 | 10
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24042 | 10
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24042 | 10
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24042 | 10
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24042 | 10
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24042 | 10
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24042 | 10
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24042 | 10
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24033 | 10
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24033 | 10
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24033 | 10
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24033 | 10
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24033 | 10
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24033 | 10
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24033 | 10
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24898 | 10
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24898 | 10
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24898 | 10
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24898 | 10
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24898 | 10
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24898 | 10
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24898 | 10
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2487 | 10
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2487 | 10
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2487 | 10
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2487 | 10
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2487 | 10
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2487 | 10
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2487 | 10
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24919 | 10
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24919 | 10
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24919 | 10
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24919 | 10
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24919 | 10
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24919 | 10
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24919 | 10
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0048 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24048 | 10
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0048 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24048 | 10
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0048 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24048 | 10
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0048 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24048 | 10
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0048 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24048 | 10
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0048 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24048 | 10
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0048 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24048 | 10
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24907 | 10
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24907 | 10
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24907 | 10
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24907 | 10
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24907 | 10
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24907 | 10
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24907 | 10
AEPW | NORTH MARSHALL 69KV | 5 | -0.00363 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24891 | 10
AEPW | NORTH MARSHALL 69KV | 5 | -0.00363 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24891 | 10
AEPW | NORTH MARSHALL 69KV | 5 | -0.00363 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24891 | 10
AEPW | NORTH MARSHALL 69KV | 5 | -0.00363 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24891 | 10
AEPW | NORTH MARSHALL 69KV | 5 | -0.00363 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24891 | 10
AEPW | NORTH MARSHALL 69KV | 5 | -0.00363 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24891 | 10
AEPW | NORTH MARSHALL 69KV | 5 | -0.00363 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24891 | 10
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24521 | 10
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24521 | 10
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24521 | 10
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24521 | 10
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24521 | 10
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24521 | 10
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24521 | 10
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24601 | 10
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24601 | 10
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24601 | 10
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24601 | 10
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24601 | 10
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24601 | 10
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24601 | 10
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24693 | 10
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24693 | 10
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24693 | 10
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24693 | 10
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24693 | 10
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24693 | 10
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24693 | 10
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23764 | 10
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23764 | 10
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23764 | 10
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23764 | 10
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23764 | 10
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23764 | 10
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23764 | 10
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.0099 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23538 | 10
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.0099 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23538 | 10
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.0099 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23538 | 10
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.0099 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23538 | 10
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.0099 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23538 | 10
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.0099 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23538 | 10
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.0099 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23538 | 10
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00173 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24355 | 10
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00173 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24355 | 10
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00173 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24355 | 10
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00173 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24355 | 10
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00173 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24355 | 10
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00173 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24355 | 10
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00173 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24355 | 10
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23906 | 10
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23906 | 10
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23906 | 10
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23906 | 10
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23906 | 10
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23906 | 10
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23906 | 10
WERE | OXFORD 138KV | 4.5 | 0.00698 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | OXFORD 138KV | 4.5 | 0.00698 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | OXFORD 138KV | 4.5 | 0.00698 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | OXFORD 138KV | 4.5 | 0.00698 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | OXFORD 138KV | 4.5 | 0.00698 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2383 | 10
WERE | OXFORD 138KV | 4.5 | 0.00698 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2383 | 10
WERE | OXFORD 138KV | 4.5 | 0.00698 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2383 | 10
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24537 | 10
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24537 | 10
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24537 | 10
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24537 | 10
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24537 | 10
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24537 | 10
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24537 | 10
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2452 | 10
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2452 | 10
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2452 | 10
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2452 | 10
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2452 | 10
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2452 | 10
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2452 | 10
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24525 | 10
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24525 | 10
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24525 | 10
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24525 | 10
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24525 | 10
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24525 | 10
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24525 | 10
SWPA | PIGGOTT 69KV | 7.5 | 0.00013 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24515 | 10
SWPA | PIGGOTT 69KV | 7.5 | 0.00013 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24515 | 10
SWPA | PIGGOTT 69KV | 7.5 | 0.00013 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24515 | 10
SWPA | PIGGOTT 69KV | 7.5 | 0.00013 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24515 | 10
SWPA | PIGGOTT 69KV | 7.5 | 0.00013 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24515 | 10
SWPA | PIGGOTT 69KV | 7.5 | 0.00013 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24515 | 10
SWPA | PIGGOTT 69KV | 7.5 | 0.00013 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24515 | 10
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24896 | 10
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24896 | 10
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24896 | 10
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24488 | 10
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24488 | 10
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24488 | 10
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24488 | 10
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24488 | 10
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24488 | 10
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24488 | 10
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24758 | 10
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24758 | 10
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24758 | 10
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24758 | 10
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24758 | 10
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24758 | 10
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24758 | 10
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23877 | 10
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23877 | 10
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23877 | 10
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23877 | 10
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23877 | 10
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23877 | 10
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23877 | 10
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24551 | 10
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24551 | 10
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24551 | 10
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23947 | 10
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23947 | 10
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23947 | 10
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23947 | 10
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23947 | 10
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23947 | 10
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23947 | 10
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23715 | 10
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23715 | 10
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23715 | 10
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23715 | 10
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23715 | 10
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23715 | 10
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23715 | 10
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23875 | 10
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23875 | 10
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23875 | 10
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23875 | 10
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23875 | 10
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23875 | 10
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23875 | 10
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24776 | 10
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24776 | 10
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24776 | 10
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24776 | 10
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24776 | 10
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24776 | 10
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24776 | 10
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24018 | 10
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24018 | 10
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24018 | 10
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24018 | 10
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24018 | 10
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24018 | 10
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24018 | 10
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2459 | 10
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2459 | 10
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2459 | 10
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2459 | 10
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2459 | 10
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2459 | 10
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2459 | 10
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24727 | 10
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24727 | 10
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24727 | 10
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24727 | 10
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24727 | 10
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24727 | 10
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24727 | 10
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24982 | 10
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24982 | 10
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24982 | 10
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24982 | 10
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24982 | 10
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24982 | 10
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24982 | 10
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23775 | 10
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23775 | 10
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23775 | 10
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23775 | 10
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23775 | 10
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23775 | 10
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23775 | 10
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25479 | 10
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25479 | 10
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25479 | 10
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25479 | 10
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.25479 | 10
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.25479 | 10
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.25479 | 10
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2494 | 10
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2494 | 10
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2494 | 10
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2494 | 10
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.2494 | 10
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.2494 | 10
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.2494 | 10
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24914 | 10
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24914 | 10
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24914 | 10
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24914 | 10
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24914 | 10
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24914 | 10
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24914 | 10
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24906 | 10
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24906 | 10
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24906 | 10
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24906 | 10
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.24906 | 10
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.24906 | 10
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.24906 | 10
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23087 | 11
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23087 | 11
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23087 | 11
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23087 | 11
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23087 | 11
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23087 | 11
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23087 | 11
OMPA | OMPA-LAVERNE 69KV | 4 | 0.0143 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23098 | 11
OMPA | OMPA-LAVERNE 69KV | 4 | 0.0143 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23098 | 11
OMPA | OMPA-LAVERNE 69KV | 4 | 0.0143 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23098 | 11
OMPA | OMPA-LAVERNE 69KV | 4 | 0.0143 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23098 | 11
OMPA | OMPA-LAVERNE 69KV | 4 | 0.0143 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23098 | 11
OMPA | OMPA-LAVERNE 69KV | 4 | 0.0143 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23098 | 11
OMPA | OMPA-LAVERNE 69KV | 4 | 0.0143 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23098 | 11
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23 | 11
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23 | 11
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23 | 11
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23 | 11
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.23 | 11
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.23 | 11
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.23 | 11
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03574 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.20954 | 12
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03574 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.20954 | 12
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03574 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.20954 | 12
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03574 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.20954 | 12
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03574 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.20954 | 12
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03574 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.20954 | 12
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03574 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.20954 | 12
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.1576 | 15
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.1576 | 15
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.1576 | 15
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.08768 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.1576 | 15
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.15948 | 15
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.15948 | 15
OKGE | MUSTANG 69KV | 110 | 0.08768 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | MUSTANG 69KV | 110 | 0.08768 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | MUSTANG 69KV | 110 | 0.08768 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | MUSTANG 69KV | 110 | 0.08768 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | MUSTANG 69KV | 110 | 0.08768 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.24528 | -0.1576 | 15
OKGE | MUSTANG 69KV | 110 | 0.08768 | OKGE | MUSTANG 138KV | 221 | 0.24528 | -0.1576 | 15
OKGE | MUSTANG 69KV | 110 | 0.08768 | OKGE | SMITH COGEN 138KV | 107 | 0.24528 | -0.1576 | 15
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.12644 | 19
OKGE | HORSESHOE LAKE 138KV | 615 | -0.03876 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.12644 | 19
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.12757 | 19
OKGE | TINKER 5G 138KV | 62 | -0.03989 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.12757 | 19
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.10218 | 24
OKGE | SEMINOLE 138KV | 371.0858 | -0.0145 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.10218 | 24
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.10026 | 24
OKGE | SEMINOLE 345KV | 618.814 | -0.01258 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.10026 | 24
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | WTH WIND 34.500 34KV | 147 | 0.02647 | -0.09827 | 25
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09719 | 25
AEPW | WELEETKA 138KV | 152.4 | -0.00951 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09719 | 25
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.02137 | -0.09317 | 26
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09222 | 26
AEPW | TURK 138KV | 38 | -0.00454 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09222 | 26
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09102 | 27
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00334 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09102 | 27
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09103 | 27
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00335 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09103 | 27
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0902 | 27
GRDA | BOOMER 69KV | 24 | -0.00252 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0902 | 27
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08954 | 27
AEPW | COGENTRIX 345KV | 64 | -0.00186 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08954 | 27
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09136 | 27
AEPW | EASTMAN 138KV | 335.01 | -0.00368 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09136 | 27
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09002 | 27
AEPW | FITZHUGH 161KV | 168 | -0.00234 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09002 | 27
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09165 | 27
AEPW | FULTON 115KV | 153.5 | -0.00397 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09165 | 27
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09133 | 27
AEPW | KNOXLEE 138KV | 229.3353 | -0.00365 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09133 | 27
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09138 | 27
AEPW | LEBROCK 345KV | 559 | -0.0037 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09138 | 27
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0911 | 27
AEPW | LIEBERMAN 138KV | 251.4 | -0.00342 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0911 | 27
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09159 | 27
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00391 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09159 | 27
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | CANDN12 34.500 345KV | 298.2 | 0.01878 | -0.09058 | 27
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09147 | 27
OKGE | MUSKOGEE 345KV | 132.5 | -0.00379 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09147 | 27
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08933 | 27
AEPW | OEC 345KV | 50 | -0.00165 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08933 | 27
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09136 | 27
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00368 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09136 | 27
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08998 | 27
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.0023 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08998 | 27
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09016 | 27
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.00248 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09016 | 27
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08967 | 27
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00199 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08967 | 27
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0918 | 27
AEPW | WELSH 345KV | 598.3 | -0.00412 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0918 | 27
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09154 | 27
AEPW | WILKES 138KV | 254.3407 | -0.00386 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09154 | 27
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09146 | 27
AEPW | WILKES 345KV | 15.2 | -0.00378 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.09146 | 27
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0863 | 28
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00138 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0863 | 28
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08831 | 28
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00063 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08831 | 28
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08793 | 28
AEPW | FLINT CREEK 161KV | 22.4 | -0.00025 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08793 | 28
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08757 | 28
GRDA | GRDA1 345KV | 162.3132 | 0.00011 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08757 | 28
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
GRDA | KERR_U3 13.200 115KV | 57 | -0.00023 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
GRDA | KERR1 13.800 115KV | 28.5 | -0.00023 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
GRDA | KERR2 13.800 115KV | 28.5 | -0.00023 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | CENT 21 34.500 138KV | 120 | 0.01398 | -0.08578 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.01466 | -0.08646 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | FPLWND11 34.500 138KV | 102 | 0.01441 | -0.08621 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | GRADY CO SUB 345KV | 99 | 0.01484 | -0.08664 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WFEC | HAMMON CO SUB 138KV | 114 | 0.01419 | -0.08599 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | MNCWND31 34.500 345KV | 100 | 0.01484 | -0.08664 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WFEC | MORLND4 18.000 138KV | 69.1219 | 0.01441 | -0.08621 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | OU SPIRIT 138KV | 102 | 0.01381 | -0.08561 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | SILNGW21 34.500 345KV | 100 | 0.01466 | -0.08646 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WFEC | SLEEPING BEAR 138KV | 80 | 0.01434 | -0.08614 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | SLINGW11 34.500 345KV | 199 | 0.01466 | -0.08646 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.01528 | -0.08708 | 28
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01381 | -0.08561 | 28
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08761 | 28
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 7e-05 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08761 | 28
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08841 | 28
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00073 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08841 | 28
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08777 | 28
SWPA | PARAGOULD 161KV | 31 | -9e-05 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08777 | 28
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0876 | 28
GRDA | PENSA_U3 13.200 69KV | 63 | 8e-05 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0876 | 28
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08765 | 28
GRDA | PENSA_U6 13.200 161KV | 63 | 3e-05 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08765 | 28
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08728 | 28
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.0004 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08728 | 28
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.00023 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08791 | 28
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0883 | 28
AEPW | TONTITOWN 161KV | 304.5 | -0.00062 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0883 | 28
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08438 | 29
WFEC | ANADARKO 69KV | 70 | 0.0033 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08438 | 29
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08285 | 29
WERE | BERWICK3 115.00 115KV | 12.7 | 0.00483 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08285 | 29
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08463 | 29
WERE | CHANUTE 69KV | 33.84 | 0.00305 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08463 | 29
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08285 | 29
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00483 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08285 | 29
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08463 | 29
WERE | CITY OF ERIE 69KV | 25.53 | 0.00305 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08463 | 29
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08442 | 29
WERE | CITY OF IOLA 69KV | 24.733 | 0.00326 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08442 | 29
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08282 | 29
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00486 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08282 | 29
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08273 | 29
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00495 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08273 | 29
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01171 | -0.08351 | 29
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.01223 | -0.08403 | 29
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01171 | -0.08351 | 29
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08077 | 30
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00691 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08077 | 30
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08264 | 30
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08264 | 30
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08264 | 30
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00504 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08264 | 30
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08095 | 30
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00673 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08095 | 30
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08054 | 30
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00714 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08054 | 30
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0805 | 30
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.00718 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0805 | 30
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0807 | 30
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00698 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0807 | 30
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08168 | 30
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.006 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08168 | 30
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08191 | 30
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00577 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08191 | 30
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08018 | 30
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.0075 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08018 | 30
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08018 | 30
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0075 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08018 | 30
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08014 | 30
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00754 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08014 | 30
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08053 | 30
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00715 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08053 | 30
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08053 | 30
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00715 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08053 | 30
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08053 | 30
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00715 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08053 | 30
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0822 | 30
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00548 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0822 | 30
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08222 | 30
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.00546 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08222 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | BRKWND11 34.500 138KV | 70 | 0.00885 | -0.08065 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.01042 | -0.08222 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00862 | -0.08042 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00862 | -0.08042 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00862 | -0.08042 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00862 | -0.08042 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WFEC | GOTEBO 2 69.000 69KV | 74 | 0.01022 | -0.08202 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | GRNTWDG2 0.6900 34KV | 152 | 0.00967 | -0.08147 | 30
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00973 | -0.08153 | 30
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08004 | 30
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00764 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08004 | 30
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08146 | 30
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00622 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08146 | 30
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08117 | 30
WERE | SALINA MAIN 115KV | 10.18 | 0.00651 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08117 | 30
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08187 | 30
OKGE | SOONER 138KV | 32 | 0.00581 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08187 | 30
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08115 | 30
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.00653 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08115 | 30
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08258 | 30
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.0051 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08258 | 30
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08015 | 30
WERE | WACO S 4 138.00 138KV | 30 | 0.00753 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.08015 | 30
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07801 | 31
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00967 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07801 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | 0.00779 | -0.07959 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | COMANCHE 138KV | 164.7 | 0.00625 | -0.07805 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.00577 | -0.07757 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | KAYWNDG2 0.6900 34KV | 280 | 0.00745 | -0.07925 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WFEC | MEERS CO SUB 138KV | 74.25 | 0.00699 | -0.07879 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OMPA | OMPA-PONCA CITY 69KV | 24.3194 | 0.00622 | -0.07802 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | SLATEGEN1 0.6900 34KV | 150 | 0.00698 | -0.07878 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WFEC | SLICKHILLS4 138.00 138KV | 99 | 0.00699 | -0.07879 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | SOONER 138KV | 535 | 0.00581 | -0.07761 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | SOONER 345KV | 537 | 0.00813 | -0.07993 | 31
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00653 | -0.07833 | 31
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07955 | 31
OKGE | SOONER 345KV | 30 | 0.00813 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07955 | 31
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07597 | 32
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01171 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07597 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WFEC | ANADARKO 138KV | 362.8809 | 0.00497 | -0.07677 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | CANEYWF1 0.6900 34KV | 199.8 | 0.00524 | -0.07704 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | COMANCHE 69KV | 64 | 0.00531 | -0.07711 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | ELK RIVER 345KV | 150 | 0.00553 | -0.07733 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00548 | -0.07728 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.00546 | -0.07726 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.00486 | -0.07666 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.00495 | -0.07675 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.00505 | -0.07685 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | S ALMA 3 115.00 115KV | 11.6 | 0.00555 | -0.07735 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.0051 | -0.0769 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | 0.00551 | -0.07731 | 32
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | SWPA | CARTHAGE 69KV | 20 | 0.00122 | -0.07302 | 33
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07327 | 33
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01441 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.07327 | 33
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | FLINT CREEK 161KV | 528 | -0.00025 | -0.07155 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | GRDA | GRDA1 345KV | 357.6868 | 0.00011 | -0.07191 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | GRDA | GRECCTG_1 20.000 345KV | 250 | 0.00011 | -0.07191 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | GRDA | GRECSTG_1 17.500 345KV | 150 | 0.00011 | -0.07191 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | SWPA | KENNETT 69KV | 29 | 9e-05 | -0.07189 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | SWPA | MALDEN 69KV | 12 | 0.00019 | -0.07199 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | NORTHEASTERN STATION 138KV | 841 | 7e-05 | -0.07187 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00073 | -0.07107 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | SWPA | POPLAR BLUFF 161KV | 20.9 | 0.0004 | -0.0722 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | REDBUD 345KV | 1224 | 0.00053 | -0.07233 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | GRDA | SALINA_U6 13.400 161KV | 40.8997 | -0.00023 | -0.07157 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | SWPA | SIKESTON 161KV | 235 | 0.0004 | -0.0722 | 34
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0724 | 34
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01528 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.08768 | -0.0724 | 34
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | AES 161KV | 320 | -0.00283 | -0.06897 | 35
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | COGENTRIX 345KV | 830 | -0.00186 | -0.06994 | 35
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | OEC 345KV | 1160 | -0.00165 | -0.07015 | 35
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.0023 | -0.0695 | 35
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | ARSENAL HILL 138KV | 509 | -0.00334 | -0.06846 | 36
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | EASTMAN 138KV | 150 | -0.00368 | -0.06812 | 36
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | KNOXLEE 138KV | 254.3647 | -0.00365 | -0.06815 | 36
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.00379 | -0.06801 | 36
OKGE | MCCLAIN 138KV | 47.4023 | -0.0718 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00368 | -0.06812 | 36
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG - SW 5TH 138KV CKT 1
Limiting Facility: | MUSTANG - SW 5TH 138KV CKT 1
Direction: | FROM->TO
Line Outage: | COUNCIL - MUSTANG 138KV CKT 1
Flowgate: | 2017AG1AFS11T7795518SP
Date Redispatch Needed: | Starting 2018 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2018 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
84904909 | 2.1 | 2.1
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.28454 | 7
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.28454 | 7
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.28454 | 7
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.28454 | 7
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.28454 | 7
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.28454 | 7
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.26877 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.26877 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.26877 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.26877 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.26877 | 8
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.26877 | 8
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24806 | 8
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24806 | 8
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24806 | 8
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24806 | 8
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24806 | 8
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24806 | 8
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.27068 | 8
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.27068 | 8
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.27068 | 8
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.27068 | 8
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.27068 | 8
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.27068 | 8
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24389 | 9
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24389 | 9
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24389 | 9
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24389 | 9
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24389 | 9
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24389 | 9
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22873 | 9
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22873 | 9
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22873 | 9
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22873 | 9
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22873 | 9
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.22873 | 9
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23889 | 9
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23889 | 9
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00645 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24322 | 9
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00645 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24322 | 9
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00645 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24322 | 9
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00645 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24322 | 9
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00645 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24322 | 9
WFEC | ASHLAND4 138.00 138KV | 5 | -0.00645 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24322 | 9
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22601 | 9
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22601 | 9
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22601 | 9
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22601 | 9
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22601 | 9
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.22601 | 9
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23287 | 9
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23287 | 9
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23287 | 9
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23287 | 9
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23287 | 9
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23287 | 9
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24279 | 9
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24279 | 9
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24279 | 9
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24279 | 9
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24279 | 9
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24279 | 9
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23106 | 9
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23106 | 9
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23106 | 9
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23106 | 9
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23106 | 9
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23106 | 9
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23292 | 9
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23292 | 9
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23292 | 9
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23478 | 9
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23149 | 9
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23312 | 9
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23312 | 9
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23312 | 9
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23312 | 9
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23312 | 9
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23312 | 9
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23478 | 9
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23478 | 9
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23456 | 9
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23456 | 9
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23456 | 9
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23456 | 9
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23456 | 9
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23456 | 9
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2311 | 9
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2311 | 9
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2311 | 9
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2311 | 9
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2311 | 9
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.2311 | 9
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23127 | 9
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23127 | 9
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23127 | 9
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23127 | 9
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23127 | 9
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23127 | 9
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23156 | 9
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23156 | 9
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23156 | 9
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23156 | 9
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23156 | 9
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23156 | 9
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23189 | 9
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23189 | 9
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23189 | 9
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23189 | 9
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23189 | 9
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23189 | 9
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23643 | 9
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23643 | 9
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23643 | 9
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23643 | 9
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23643 | 9
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23643 | 9
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23954 | 9
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23954 | 9
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23954 | 9
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23954 | 9
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23954 | 9
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23954 | 9
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23908 | 9
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23798 | 9
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23798 | 9
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23798 | 9
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23798 | 9
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23798 | 9
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23798 | 9
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23212 | 9
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23212 | 9
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23212 | 9
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23212 | 9
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23212 | 9
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23212 | 9
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23069 | 9
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23069 | 9
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23893 | 9
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23767 | 9
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23767 | 9
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23767 | 9
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23767 | 9
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23767 | 9
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23767 | 9
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23927 | 9
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23927 | 9
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23927 | 9
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23927 | 9
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23927 | 9
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23927 | 9
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23071 | 9
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23749 | 9
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23749 | 9
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23749 | 9
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23749 | 9
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23749 | 9
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23749 | 9
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22898 | 9
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22898 | 9
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22898 | 9
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22898 | 9
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22898 | 9
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.22898 | 9
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23086 | 9
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23086 | 9
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23236 | 9
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23236 | 9
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23236 | 9
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23236 | 9
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23236 | 9
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23236 | 9
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23237 | 9
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23237 | 9
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23237 | 9
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23237 | 9
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23237 | 9
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23237 | 9
SWPA | KENNETT 69KV | 5.3 | 1e-05 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23676 | 9
SWPA | KENNETT 69KV | 5.3 | 1e-05 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23676 | 9
SWPA | KENNETT 69KV | 5.3 | 1e-05 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23676 | 9
SWPA | KENNETT 69KV | 5.3 | 1e-05 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23676 | 9
SWPA | KENNETT 69KV | 5.3 | 1e-05 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23676 | 9
SWPA | KENNETT 69KV | 5.3 | 1e-05 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23676 | 9
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23777 | 9
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23777 | 9
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23777 | 9
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23906 | 9
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23906 | 9
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23906 | 9
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23906 | 9
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23906 | 9
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23906 | 9
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23291 | 9
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23291 | 9
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23291 | 9
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23291 | 9
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23291 | 9
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23291 | 9
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23283 | 9
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23283 | 9
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23283 | 9
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23283 | 9
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23283 | 9
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23283 | 9
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23909 | 9
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23909 | 9
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23909 | 9
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23909 | 9
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23909 | 9
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23909 | 9
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23893 | 9
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23893 | 9
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23921 | 9
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23921 | 9
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23921 | 9
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23921 | 9
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23921 | 9
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23921 | 9
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22363 | 9
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22363 | 9
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22363 | 9
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22363 | 9
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22363 | 9
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.22363 | 9
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.00381 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23296 | 9
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.00381 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23296 | 9
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.00381 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23296 | 9
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.00381 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23296 | 9
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.00381 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23296 | 9
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.00381 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23296 | 9
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24032 | 9
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24032 | 9
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24032 | 9
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24032 | 9
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24032 | 9
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24032 | 9
AEPW | NORTH MARSHALL 69KV | 5 | -0.00228 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23905 | 9
AEPW | NORTH MARSHALL 69KV | 5 | -0.00228 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23905 | 9
AEPW | NORTH MARSHALL 69KV | 5 | -0.00228 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23905 | 9
AEPW | NORTH MARSHALL 69KV | 5 | -0.00228 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23905 | 9
AEPW | NORTH MARSHALL 69KV | 5 | -0.00228 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23905 | 9
AEPW | NORTH MARSHALL 69KV | 5 | -0.00228 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23905 | 9
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23772 | 9
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23772 | 9
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23772 | 9
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23772 | 9
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23772 | 9
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23772 | 9
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23656 | 9
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23656 | 9
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23656 | 9
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23656 | 9
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23656 | 9
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23656 | 9
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23912 | 9
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23912 | 9
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23912 | 9
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23912 | 9
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23912 | 9
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23912 | 9
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23108 | 9
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23108 | 9
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23108 | 9
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23108 | 9
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23108 | 9
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23108 | 9
OMPA | OMPA-LAVERNE 69KV | 4 | 0.01301 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22376 | 9
OMPA | OMPA-LAVERNE 69KV | 4 | 0.01301 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22376 | 9
OMPA | OMPA-LAVERNE 69KV | 4 | 0.01301 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22376 | 9
OMPA | OMPA-LAVERNE 69KV | 4 | 0.01301 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22376 | 9
OMPA | OMPA-LAVERNE 69KV | 4 | 0.01301 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22376 | 9
OMPA | OMPA-LAVERNE 69KV | 4 | 0.01301 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.22376 | 9
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.01201 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22476 | 9
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.01201 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22476 | 9
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.01201 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22476 | 9
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.01201 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22476 | 9
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.01201 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22476 | 9
OMPA | OMPA-MANGUM 69KV | 5.198 | 0.01201 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.22476 | 9
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00013 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23664 | 9
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00013 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23664 | 9
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00013 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23664 | 9
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00013 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23664 | 9
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00013 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23664 | 9
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00013 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23664 | 9
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23288 | 9
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23288 | 9
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23288 | 9
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23288 | 9
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23288 | 9
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23288 | 9
WERE | OXFORD 138KV | 4.5 | 0.00528 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | OXFORD 138KV | 4.5 | 0.00528 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | OXFORD 138KV | 4.5 | 0.00528 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | OXFORD 138KV | 4.5 | 0.00528 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | OXFORD 138KV | 4.5 | 0.00528 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23149 | 9
WERE | OXFORD 138KV | 4.5 | 0.00528 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23149 | 9
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2369 | 9
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2369 | 9
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2369 | 9
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2369 | 9
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2369 | 9
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.2369 | 9
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23747 | 9
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23747 | 9
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23747 | 9
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23747 | 9
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23747 | 9
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23747 | 9
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23753 | 9
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23753 | 9
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23753 | 9
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23753 | 9
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23753 | 9
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23753 | 9
SWPA | PIGGOTT 69KV | 7.5 | 4e-05 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23673 | 9
SWPA | PIGGOTT 69KV | 7.5 | 4e-05 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23673 | 9
SWPA | PIGGOTT 69KV | 7.5 | 4e-05 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23673 | 9
SWPA | PIGGOTT 69KV | 7.5 | 4e-05 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23673 | 9
SWPA | PIGGOTT 69KV | 7.5 | 4e-05 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23673 | 9
SWPA | PIGGOTT 69KV | 7.5 | 4e-05 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23673 | 9
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23908 | 9
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23908 | 9
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23654 | 9
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23654 | 9
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23654 | 9
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23654 | 9
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23654 | 9
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23654 | 9
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23992 | 9
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23992 | 9
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23992 | 9
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23992 | 9
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23992 | 9
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23992 | 9
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23142 | 9
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23142 | 9
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23142 | 9
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23142 | 9
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23142 | 9
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23142 | 9
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23777 | 9
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23777 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24561 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24561 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24561 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24561 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24561 | 9
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24561 | 9
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23349 | 9
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23349 | 9
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23349 | 9
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23349 | 9
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23349 | 9
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23349 | 9
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23083 | 9
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23083 | 9
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23083 | 9
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23083 | 9
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23083 | 9
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23083 | 9
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22674 | 9
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22674 | 9
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22674 | 9
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22674 | 9
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.22674 | 9
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.22674 | 9
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2248 | 9
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2248 | 9
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2248 | 9
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2248 | 9
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2248 | 9
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.2248 | 9
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24267 | 9
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24267 | 9
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24267 | 9
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24267 | 9
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24267 | 9
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24267 | 9
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2327 | 9
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2327 | 9
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2327 | 9
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2327 | 9
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2327 | 9
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.2327 | 9
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23797 | 9
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23797 | 9
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23797 | 9
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23797 | 9
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23797 | 9
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23797 | 9
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2397 | 9
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2397 | 9
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2397 | 9
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2397 | 9
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.2397 | 9
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.2397 | 9
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23959 | 9
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23959 | 9
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23959 | 9
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23959 | 9
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23959 | 9
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23959 | 9
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23071 | 9
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23071 | 9
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24458 | 9
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24458 | 9
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24458 | 9
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24458 | 9
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.24458 | 9
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.24458 | 9
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23934 | 9
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23934 | 9
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23934 | 9
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23934 | 9
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23934 | 9
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23934 | 9
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23919 | 9
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23919 | 9
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23919 | 9
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23919 | 9
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23919 | 9
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23919 | 9
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23914 | 9
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23914 | 9
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23914 | 9
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23914 | 9
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.23914 | 9
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.23914 | 9
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03388 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.20289 | 10
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03388 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.20289 | 10
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03388 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.20289 | 10
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03388 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.20289 | 10
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03388 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.20289 | 10
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.03388 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.20289 | 10
OKGE | SMITH COGEN 138KV | 16 | 0.06525 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.17152 | 12
OKGE | SMITH COGEN 138KV | 16 | 0.06525 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.17152 | 12
OKGE | SMITH COGEN 138KV | 16 | 0.06525 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.17152 | 12
OKGE | SMITH COGEN 138KV | 16 | 0.06525 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.17152 | 12
OKGE | SMITH COGEN 138KV | 16 | 0.06525 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.17152 | 12
OKGE | SMITH COGEN 138KV | 16 | 0.06525 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.17152 | 12
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.14747 | 14
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.0893 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.14747 | 14
OKGE | MUSTANG 69KV | 110 | 0.0893 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | MUSTANG 69KV | 110 | 0.0893 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | MUSTANG 69KV | 110 | 0.0893 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | MUSTANG 69KV | 110 | 0.0893 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | MUSTANG 69KV | 110 | 0.0893 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.23677 | -0.14747 | 14
OKGE | MUSTANG 69KV | 110 | 0.0893 | OKGE | MUSTANG 138KV | 221 | 0.23677 | -0.14747 | 14
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.13707 | 15
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.13707 | 15
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.1213 | 17
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.1213 | 17
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.12321 | 17
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.12321 | 17
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.11302 | 19
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.10059 | 21
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.10059 | 21
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09814 | 21
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09814 | 21
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.09916 | 21
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09642 | 22
WFEC | ALLEN 4 138.00 138KV | 7.5 | -0.00712 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09642 | 22
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09532 | 22
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09532 | 22
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.09725 | 22
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0952 | 22
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0952 | 22
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09711 | 22
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09711 | 22
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09142 | 23
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09142 | 23
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09142 | 23
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09142 | 23
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09207 | 23
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09207 | 23
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09161 | 23
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09161 | 23
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09051 | 23
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09051 | 23
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09146 | 23
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09146 | 23
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0902 | 23
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0902 | 23
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0918 | 23
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0918 | 23
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09002 | 23
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09002 | 23
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09159 | 23
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09159 | 23
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09162 | 23
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09162 | 23
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09146 | 23
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09146 | 23
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09174 | 23
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09174 | 23
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09285 | 23
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09285 | 23
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09025 | 23
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09025 | 23
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09165 | 23
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09165 | 23
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09 | 23
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09 | 23
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09006 | 23
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09006 | 23
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09161 | 23
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09161 | 23
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09245 | 23
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09245 | 23
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0903 | 23
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0905 | 23
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0905 | 23
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09223 | 23
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09223 | 23
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09212 | 23
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09212 | 23
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09187 | 23
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09187 | 23
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09172 | 23
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09172 | 23
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09167 | 23
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.09167 | 23
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08731 | 24
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08731 | 24
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08731 | 24
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08731 | 24
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08709 | 24
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08709 | 24
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08896 | 24
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08896 | 24
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08909 | 24
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08909 | 24
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08943 | 24
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08943 | 24
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08907 | 24
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08907 | 24
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08602 | 24
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08602 | 24
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0854 | 25
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0854 | 25
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08359 | 25
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08359 | 25
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08545 | 25
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08545 | 25
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08545 | 25
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00385 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08545 | 25
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08402 | 25
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08402 | 25
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08565 | 25
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08565 | 25
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08363 | 25
WERE | CITY OF MULVANE 69KV | 10.665 | 0.00567 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08363 | 25
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0838 | 25
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0838 | 25
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08409 | 25
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08409 | 25
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08442 | 25
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08442 | 25
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08465 | 25
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08465 | 25
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08322 | 25
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08322 | 25
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08322 | 25
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08322 | 25
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08324 | 25
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08324 | 25
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08339 | 25
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08339 | 25
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08339 | 25
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08339 | 25
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08339 | 25
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08339 | 25
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08489 | 25
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08489 | 25
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0849 | 25
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.0849 | 25
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08544 | 25
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08544 | 25
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08536 | 25
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08536 | 25
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08361 | 25
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08361 | 25
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08541 | 25
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08541 | 25
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08395 | 25
WERE | SALINA MAIN 115KV | 10.18 | 0.00535 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08395 | 25
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08336 | 25
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08336 | 25
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08523 | 25
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08523 | 25
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08324 | 25
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08324 | 25
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08126 | 26
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08126 | 26
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08151 | 26
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.08151 | 26
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07854 | 27
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07854 | 27
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07927 | 27
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07927 | 27
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07733 | 27
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07733 | 27
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | WTH WIND 34.500 34KV | 147 | 0.02778 | -0.07555 | 28
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07616 | 28
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.0893 | -0.07616 | 28
OKGE | SEMINOLE 138KV | 371.0858 | -0.01129 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.07654 | 28
OKGE | SEMINOLE 345KV | 618.814 | -0.00884 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.07409 | 28
AEPW | WELEETKA 138KV | 152.4 | -0.00781 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.07306 | 29
GRDA | BOOMER 69KV | 24 | -0.00602 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.07127 | 30
GRDA | STILL_GEN1 12.470 69KV | 56.1 | -0.0059 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.07115 | 30
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00212 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06737 | 31
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00212 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06737 | 31
AEPW | COGENTRIX 345KV | 64 | -0.00277 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06802 | 31
AEPW | EASTMAN 138KV | 335.01 | -0.00231 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06756 | 31
AEPW | FITZHUGH 161KV | 168 | -0.00216 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06741 | 31
AEPW | FULTON 115KV | 153.5 | -0.0025 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06775 | 31
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.02054 | -0.06831 | 31
AEPW | KNOXLEE 138KV | 229.3353 | -0.00229 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06754 | 31
AEPW | LEBROCK 345KV | 559 | -0.00232 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06757 | 31
AEPW | LIEBERMAN 138KV | 251.4 | -0.00216 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06741 | 31
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00244 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06769 | 31
OKGE | MUSKOGEE 345KV | 132.5 | -0.00355 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.0688 | 31
AEPW | OEC 345KV | 50 | -0.00235 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.0676 | 31
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.00231 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06756 | 31
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00315 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.0684 | 31
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00293 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06818 | 31
AEPW | TURK 138KV | 38 | -0.00282 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06807 | 31
AEPW | WELSH 345KV | 598.3 | -0.00257 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06782 | 31
AEPW | WILKES 138KV | 254.3407 | -0.00242 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06767 | 31
AEPW | WILKES 345KV | 15.2 | -0.00237 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06762 | 31
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00034 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06491 | 32
AEPW | ELKINS GENERATOR 69KV | 60.3 | -0.00121 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06646 | 32
AEPW | FLINT CREEK 161KV | 22.4 | -0.0009 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06615 | 32
GRDA | GRDA1 345KV | 162.3132 | -0.00072 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06597 | 32
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | CANDN12 34.500 345KV | 298.2 | 0.01791 | -0.06568 | 32
GRDA | KERR_U3 13.200 115KV | 57 | -0.001 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06625 | 32
GRDA | KERR1 13.800 115KV | 28.5 | -0.001 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06625 | 32
GRDA | KERR2 13.800 115KV | 28.5 | -0.001 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06625 | 32
AEPW | NORTHEASTERN STATION 138KV | 41.7 | -0.00095 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.0662 | 32
AEPW | NORTHEASTERN STATION 345KV | 532.8 | 0.00021 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06504 | 32
SWPA | PARAGOULD 161KV | 31 | -0.00013 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06538 | 32
GRDA | PENSA_U3 13.200 69KV | 63 | -0.0007 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06595 | 32
GRDA | PENSA_U6 13.200 161KV | 63 | -0.00076 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06601 | 32
SWPA | POPLAR BLUFF 161KV | 12.9 | 0.00023 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06502 | 32
GRDA | SALINA_U6 13.400 161KV | 217.1003 | -0.001 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06625 | 32
AEPW | TONTITOWN 161KV | 304.5 | -0.0012 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06645 | 32
WERE | CHANUTE 69KV | 33.84 | 0.00199 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06326 | 33
WERE | CITY OF ERIE 69KV | 25.53 | 0.00199 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06326 | 33
WERE | CITY OF IOLA 69KV | 24.733 | 0.00221 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06304 | 33
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WFEC | HAMMON CO SUB 138KV | 114 | 0.01512 | -0.06289 | 33
WERE | BERWICK3 115.00 115KV | 12.7 | 0.0039 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06135 | 34
WERE | CITY OF BURLINGTON 69KV | 12.5 | 0.00365 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.0616 | 34
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | GRADY CO SUB 345KV | 99 | 0.01505 | -0.06282 | 34
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | MNCWND31 34.500 345KV | 100 | 0.01505 | -0.06282 | 34
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00386 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06139 | 34
WERE | LAWRENCE ENERGY CENTER 230KV | 33.1737 | 0.00394 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06131 | 34
OMPA | OMPA-PONCA CITY 69KV | 116.3836 | 0.00389 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06136 | 34
OKGE | SOONER 138KV | 32 | 0.00328 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06197 | 34
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 0.00407 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06118 | 34
OKGE | TINKER 5G 138KV | 62 | -0.03391 | AEPW | WTH WIND 34.500 34KV | 147 | 0.02778 | -0.06169 | 34
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | 0.00571 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05954 | 35
WERE | CITY OF AUGUSTA 69KV | 19.156 | 0.00528 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05997 | 35
WERE | CITY OF WELLINGTON 69KV | 38.625 | 0.0055 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05975 | 35
WERE | CITY OF WINFIELD 69KV | 36.8 | 0.00521 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06004 | 35
WERE | CLAYGEN1 13.200 115KV | 29.67 | 0.00488 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06037 | 35
WERE | EMPORIA ENERGY CENTER 345KV | 471.6182 | 0.00465 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.0606 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.01314 | -0.06091 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | CENT 21 34.500 138KV | 120 | 0.01275 | -0.06052 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.01311 | -0.06088 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | FPLWND11 34.500 138KV | 102 | 0.01313 | -0.0609 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WFEC | GOTEBO 2 69.000 69KV | 74 | 0.01237 | -0.06014 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WFEC | MORLND4 18.000 138KV | 69.1219 | 0.01314 | -0.06091 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | OU SPIRIT 138KV | 102 | 0.01258 | -0.06035 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.01207 | -0.05984 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | SILNGW21 34.500 345KV | 100 | 0.01311 | -0.06088 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WFEC | SLEEPING BEAR 138KV | 80 | 0.01306 | -0.06083 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | SLINGW11 34.500 345KV | 199 | 0.01311 | -0.06088 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.01197 | -0.05974 | 35
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01258 | -0.06035 | 35
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0.00591 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05934 | 35
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0.00591 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05934 | 35
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0.00591 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05934 | 35
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 0.00441 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06084 | 35
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 0.0044 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.06085 | 35
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | AEPW | WTH WIND 34.500 34KV | 147 | 0.02778 | -0.05978 | 35
OMPA | OMCDLEC1 13.800 345KV | 85.3 | 0.00569 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05956 | 35
OKGE | SOONER 345KV | 30 | 0.00594 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05931 | 35
WERE | EVANS ENERGY CENTER 138KV | 696 | 0.00608 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05917 | 36
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.00608 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05917 | 36
WERE | GILL ENERGY CENTER 138KV | 192 | 0.00606 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05919 | 36
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01076 | -0.05853 | 36
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WFEC | MEERS CO SUB 138KV | 74.25 | 0.0103 | -0.05807 | 36
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01076 | -0.05853 | 36
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WFEC | SLICKHILLS4 138.00 138KV | 99 | 0.0103 | -0.05807 | 36
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.01003 | -0.0578 | 36
WERE | WACO S 4 138.00 138KV | 30 | 0.00606 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05919 | 36
WFEC | ANADARKO 69KV | 70 | 0.00804 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05721 | 37
OKGE | GRNTWDG2 0.6900 34KV | 148 | 0.00779 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05746 | 37
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WFEC | ANADARKO 138KV | 362.8809 | 0.00867 | -0.05644 | 37
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.0084 | -0.05617 | 37
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | COMANCHE 138KV | 164.7 | 0.0087 | -0.05647 | 37
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | COMANCHE 69KV | 64 | 0.00818 | -0.05595 | 38
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.007 | -0.05477 | 38
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.007 | -0.05477 | 38
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.007 | -0.05477 | 38
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.007 | -0.05477 | 38
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | GRNTWDG2 0.6900 34KV | 152 | 0.00779 | -0.05556 | 38
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | 0.01003 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05522 | 38
OKGE | BALKOWG2 0.6900 34KV | 99.7 | 0.01076 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05449 | 39
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | 0.00565 | -0.05342 | 39
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | BRKWND11 34.500 138KV | 70 | 0.00589 | -0.05366 | 39
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | KAYWNDG2 0.6900 34KV | 280 | 0.0056 | -0.05337 | 39
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | SOONER 345KV | 537 | 0.00594 | -0.05371 | 39
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.02054 | -0.05445 | 39
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | ELK RIVER 345KV | 150 | 0.00421 | -0.05198 | 40
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.00465 | -0.05242 | 40
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00441 | -0.05218 | 40
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.0044 | -0.05217 | 40
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | SLATEGEN1 0.6900 34KV | 150 | 0.0051 | -0.05287 | 40
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | 0.00429 | -0.05206 | 40
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.02054 | -0.05254 | 40
WFEC | MORLND4 18.000 138KV | 552.8781 | 0.01314 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05211 | 40
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 36 | 0.01197 | OKGE | SMITH COGEN 138KV | 107 | 0.06525 | -0.05328 | 40
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | CANEYWF1 0.6900 34KV | 199.8 | 0.00394 | -0.05171 | 41
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.00386 | -0.05163 | 41
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.00394 | -0.05171 | 41
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.0041 | -0.05187 | 41
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OMPA | OMPA-PONCA CITY 69KV | 24.3194 | 0.00389 | -0.05166 | 41
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | OKGE | SOONER 138KV | 535 | 0.00328 | -0.05105 | 41
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.00407 | -0.05184 | 41
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | CANDN12 34.500 345KV | 298.2 | 0.01791 | -0.05182 | 41
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | CANDN12 34.500 345KV | 298.2 | 0.01791 | -0.04991 | 42
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | GRADY CO SUB 345KV | 99 | 0.01505 | -0.04896 | 43
OKGE | TINKER 5G 138KV | 62 | -0.03391 | WFEC | HAMMON CO SUB 138KV | 114 | 0.01512 | -0.04903 | 43
OKGE | TINKER 5G 138KV | 62 | -0.03391 | OKGE | MNCWND31 34.500 345KV | 100 | 0.01505 | -0.04896 | 43
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | SWPA | CARTHAGE 69KV | 20 | 0.00046 | -0.04823 | 44
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | SWPA | KENNETT 69KV | 29 | 1e-05 | -0.04778 | 44
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0.00021 | -0.04798 | 44
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | SWPA | POPLAR BLUFF 161KV | 20.9 | 0.00023 | -0.048 | 44
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | SWPA | SIKESTON 161KV | 235 | 0.00025 | -0.04802 | 44
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | FLINT CREEK 161KV | 528 | -0.0009 | -0.04687 | 45
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | GRDA | GRDA1 345KV | 357.6868 | -0.00072 | -0.04705 | 45
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | GRDA | GRECCTG_1 20.000 345KV | 250 | -0.00072 | -0.04705 | 45
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | GRDA | GRECSTG_1 17.500 345KV | 150 | -0.00072 | -0.04705 | 45
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.00095 | -0.04682 | 45
OKGE | HORSESHOE LAKE 138KV | 615 | -0.04777 | GRDA | SALINA_U6 13.400 161KV | 40.8997 | -0.001 | -0.04677 | 45
OKGE | MCCLAIN 138KV | 47.4023 | -0.032 | OKGE | GRADY CO SUB 345KV | 99 | 0.01505 | -0.04705 | 45
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | THOMAS TAP - WEATHERFORD 69KV CKT 1
Limiting Facility: | THOMAS TAP - WEATHERFORD 69KV CKT 1
Direction: | TO->FROM
Line Outage: | CLINTON NATURAL GAS TAP - WEATHERFORD WIND FARM 138KV CKT 1
Flowgate: | 2017AG1AFS11T6305018SP
Date Redispatch Needed: | Starting 2018 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2018 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
84904909 | 1.5 | 1.5
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.23784 | 6
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.25821 | 6
OMPA | OMPA-MANGUM 69KV | 5.198 | -0.02312 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.24242 | 6
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.23303 | 6
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.23124 | 6
OKGE | 10OKLAHOMACITY13.800 138KV | 10.4 | 0.0046 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2147 | 7
OKGE | 11OKLAHOMACITY13.800 138KV | 10.4 | 0.0046 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2147 | 7
OKGE | 12OKLAHOMACITY13.800 138KV | 10.4 | 0.0046 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2147 | 7
OKGE | 6OKLAHOMACITY13.800 69KV | 10.4 | 0.00526 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21404 | 7
OKGE | 7OKLAHOMACITY13.800 69KV | 10.4 | 0.00526 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21404 | 7
OKGE | 8OKLAHOMACITY13.800 138KV | 10.4 | 0.0046 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2147 | 7
OKGE | 9OKLAHOMACITY13.800 138KV | 10.4 | 0.0046 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2147 | 7
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22723 | 7
AEPW | ARSENAL HILL 138KV | 14.6 | -0.00043 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21973 | 7
AEPW | ARSENAL HILL 69KV | 18.7474 | -0.00044 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21974 | 7
OKGE | BALKOWG2 0.6900 34KV | 289.7 | -0.00221 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22151 | 7
WERE | BERWICK3 115.00 115KV | 12.7 | 2e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21928 | 7
GRDA | BOOMER 69KV | 24 | 0.00114 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21816 | 7
WERE | BPU - CITY OF MCPHERSON 115KV | 238 | -3e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21933 | 7
SPS | CARLSBAD 69KV | 10 | -0.00581 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22511 | 7
WERE | CC5SHAR1 12.470 69KV | 10 | 0.00029 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21901 | 7
WERE | CC6SHAR1 12.470 69KV | 10 | 0.00029 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21901 | 7
SPS | CHANNING 134.500 230KV | 4.2 | -0.00619 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22549 | 7
WERE | CHANUTE 69KV | 33.84 | 0.00037 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21893 | 7
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22514 | 7
WERE | CITY OF AUGUSTA 69KV | 10.89 | 0.00032 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21898 | 7
WERE | CITY OF BURLINGTON 69KV | 3.816 | 0.00029 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21901 | 7
WERE | CITY OF ERIE 69KV | 25.53 | 0.00037 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21893 | 7
WERE | CITY OF IOLA 69KV | 24.733 | 0.00035 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21895 | 7
WERE | CITY OF MULVANE 69KV | 7.59 | 0.0003 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.219 | 7
WERE | CITY OF WELLINGTON 69KV | 4 | 0.00042 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21888 | 7
WERE | CITY OF WINFIELD 69KV | 7.65 | 0.00049 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21881 | 7
WERE | CLAYGEN1 13.200 115KV | 29.67 | 5e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21925 | 7
GRDA | COFFGEN6_1 12.470 69KV | 107 | 0.00051 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21879 | 7
AEPW | COGENTRIX 345KV | 125 | 0.00067 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21863 | 7
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22509 | 7
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2251 | 7
AEPW | EASTMAN 138KV | 139.01 | -0.0005 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2198 | 7
WERE | EEC DG 1 4.1600 4KV | 2.75 | 0.0002 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2191 | 7
WERE | ELK RIVER 345KV | 104 | 0.00036 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21894 | 7
AEPW | ELKINS GENERATOR 69KV | 11.69 | 0.00047 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21883 | 7
WERE | EMPORIA ENERGY CENTER 345KV | 114.1831 | 0.00011 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21919 | 7
WERE | EVANS ENERGY CENTER 138KV | 176 | 0.0002 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2191 | 7
WERE | EVANS ENERGY CENTER 4KV | 148 | 0.0002 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2191 | 7
SPS | FIREWHEEL2 134.500 345KV | 299 | -0.00268 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22198 | 7
AEPW | FITZHUGH 161KV | 3 | 0.00023 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21907 | 7
AEPW | FLINT CREEK 161KV | 22.4 | 0.00047 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21883 | 7
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22509 | 7
WERE | GILL ENERGY CENTER 138KV | 12 | 0.00027 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21903 | 7
OKGE | GRNTWDG2 0.6900 34KV | 292.5 | 0.00062 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21868 | 7
SPS | HARRINGTON 230KV | 84 | -0.00704 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22634 | 7
WERE | HEC DG 1 4.1600 13KV | 2.75 | 0 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2193 | 7
SPS | HOBBS PLANT #2 (CT) 115KV | 33.376 | -0.00579 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22509 | 7
SPS | HOBBS PLANT #3 (ST) 230KV | 35.582 | -0.00579 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22509 | 7
OKGE | HORSESHOE LAKE 138KV | 301 | 0.0022 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2171 | 7
SPS | HUBRCO2 69KV | 11 | -0.00668 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22598 | 7
WERE | HUTCHINSON ENERGY CENTER 115KV | 118 | 0 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2193 | 7
WERE | HUTCHINSON ENERGY CENTER 4KV | 56 | 0 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2193 | 7
WERE | HUTCHINSON ENERGY CENTER 69KV | 56 | 0 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2193 | 7
WERE | JEFFREY ENERGY CENTER 230KV | 55 | 8e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21922 | 7
WERE | JEFFREY ENERGY CENTER 345KV | 110 | 8e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21922 | 7
SWPA | KENNETT 69KV | 5.3 | 5e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21925 | 7
GRDA | KERR_U3 13.200 115KV | 57 | 0.00052 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21878 | 7
GRDA | KERR2 13.800 115KV | 28.5 | 0.00052 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21878 | 7
AEPW | KNOXLEE 138KV | 141.7 | -0.00049 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21979 | 7
EMDE | LARUSSEL 161KV | 166 | 0.00035 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21895 | 7
WERE | LAWRENCE ENERGY CENTER 115KV | 18 | 0.00011 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21919 | 7
WERE | LAWRENCE ENERGY CENTER 230KV | 33 | 0.00011 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21919 | 7
AEPW | LEBROCK 345KV | 212 | -0.0005 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2198 | 7
AEPW | LIEBERMAN 138KV | 34.4 | -0.00045 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21975 | 7
AEPW | LONESTAR POWER PLANT 69KV | 51.6 | -0.00053 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21983 | 7
SPS | LP-BRND2 69KV | 20 | -0.00557 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22487 | 7
SPS | LP-HOLL2 69KV | 6 | -0.00557 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22487 | 7
SPS | LP-MACK2 69KV | 76 | -0.00557 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22487 | 7
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22487 | 7
SPS | MADOX 115KV | 13 | -0.00579 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22509 | 7
OKGE | MCCLAIN 138KV | 47.4023 | 0.00363 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21567 | 7
WFEC | MORLND4 18.000 138KV | 350 | -0.00235 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22165 | 7
WERE | MUSCOTA2 69.000 69KV | 5.55 | 0.0001 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2192 | 7
OKGE | MUSKOGEE 345KV | 132.5 | 0.00047 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21883 | 7
SPS | MUSTANG 115KV | 28 | -0.00577 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22507 | 7
OKGE | MUSTANG 138KV | 169 | 0.0046 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2147 | 7
OKGE | MUSTANG 69KV | 110 | 0.00526 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21404 | 7
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22507 | 7
SPS | NICHOLS 115KV | 55.8 | -0.00726 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22656 | 7
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22641 | 7
AEPW | NORTH MARSHALL 69KV | 5 | -0.00049 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21979 | 7
AEPW | NORTHEASTERN STATION 138KV | 41.7 | 0.0006 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2187 | 7
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00233 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22163 | 7
AEPW | OEC 345KV | 50 | 0.0006 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2187 | 7
OMPA | OMCDLEC1 13.800 345KV | 17.848 | 0.00076 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21854 | 7
OMPA | OMPA-KINGFISHER BOWMAN 69KV | 8.592 | 0.00755 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21175 | 7
OMPA | OMPA-LAVERNE 69KV | 4 | -0.00175 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22105 | 7
OMPA | OMPA-PAWHUSKA NORTHEAST 138KV | 6.7 | 0.00071 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21859 | 7
OMPA | OMPA-PONCA CITY 69KV | 128.703 | 0.00083 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21847 | 7
WERE | OXFORD 138KV | 4.5 | 0.00045 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21885 | 7
SWPA | PARAGOULD 161KV | 31 | 5e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21925 | 7
GRDA | PENSA_U3 13.200 69KV | 63 | 0.00049 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21881 | 7
GRDA | PENSA_U6 13.200 161KV | 42 | 0.0005 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2188 | 7
SWPA | PIGGOTT 69KV | 7.5 | 5e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21925 | 7
AEPW | PIRKEY GENERATION 138KV | 48.9 | -0.0005 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2198 | 7
SPS | PLANTX 115KV | 54.2 | -0.00593 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22523 | 7
SPS | PLANTX 230KV | 23.6 | -0.00591 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22521 | 7
SPS | QUAY_CNTY 113.800 115KV | 20.5 | -0.0059 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2252 | 7
AEPW | RIVERSIDE STATION 138KV | 185.5999 | 0.00066 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21864 | 7
EMDE | RIVERTON 161KV | 66.8377 | 0.0004 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2189 | 7
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22514 | 7
WERE | SALINA MAIN 115KV | 7.18 | 0 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2193 | 7
GRDA | SALINA_U6 13.400 161KV | 57.0828 | 0.00052 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21878 | 7
OKGE | SEMINOLE 138KV | 275 | 0.00039 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21891 | 7
OKGE | SEMINOLE 345KV | 557.771 | 0.00077 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21853 | 7
SPS | SIDRCH 69KV | 15 | -0.00668 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22598 | 7
OKGE | SMITH COGEN 138KV | 16 | 0.00428 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21502 | 7
OKGE | SOONER 138KV | 32 | 0.00096 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21834 | 7
OKGE | SOONER 345KV | 30 | 0.00096 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21834 | 7
OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 111 | 0.0016 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2177 | 7
EMDE | STATE LINE 161KV | 94 | 0.00039 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21891 | 7
GRDA | STILL_GEN1 12.470 69KV | 56.1 | 0.00112 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21818 | 7
WERE | TECUMSEH ENERGY CENTER 115KV | 12 | 9e-05 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21921 | 7
OKGE | TINKER 5G 138KV | 62 | 0.00179 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21751 | 7
SPS | TOLK 230KV | 102.9 | -0.00586 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.22516 | 7
AEPW | TONTITOWN 161KV | 304.5 | 0.00047 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21883 | 7
SPS | TUCUMCARI 115KV | 22 | -0.0059 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.2252 | 7
AEPW | TULSA POWER STATION 138KV | 34.3 | 0.00066 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21864 | 7
AEPW | TURK 138KV | 38 | -0.00064 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21994 | 7
WERE | WACO S 4 138.00 138KV | 30 | 0.00027 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21903 | 7
AEPW | WELEETKA 138KV | 152.4 | 0.00034 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21896 | 7
AEPW | WELSH 345KV | 598.3 | -0.00058 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21988 | 7
AEPW | WILKES 138KV | 86.2 | -0.00053 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21983 | 7
AEPW | WILKES 345KV | 15.2 | -0.00051 | AEPW | WTH WIND 34.500 34KV | 147 | 0.2193 | -0.21981 | 7
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.04351 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.04351 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.04351 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.04417 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.04417 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.04351 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.04351 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.04351 | 34
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.04254 | 35
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.04319 | 35
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.04111 | 36
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | HORSESHOE LAKE 69KV | 16 | 0.00205 | -0.04096 | 37
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | REDBUD 345KV | 1224 | 0.00155 | -0.04046 | 37
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 225 | 0.0016 | -0.04051 | 37
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | AES 161KV | 320 | 0.00025 | -0.03916 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | EMDE | ASBURY 161KV | 189 | 0.00038 | -0.03929 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | BLKWLWD1 34.500 69KV | 15 | 0.00068 | -0.03959 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SWPA | CARTHAGE 69KV | 20 | 0.00036 | -0.03927 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | CITY OF AUGUSTA 69KV | 16.45 | 0.00032 | -0.03923 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | COGENTRIX 345KV | 769 | 0.00067 | -0.03958 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | ELK RIVER 345KV | 46 | 0.00036 | -0.03927 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | ELKINS GENERATOR 69KV | 48.61 | 0.00047 | -0.03938 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | EMPORIA ENERGY CENTER 345KV | 530.8169 | 0.00011 | -0.03902 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | EVANS ENERGY CENTER 138KV | 520 | 0.0002 | -0.03911 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | FITZHUGH 161KV | 165 | 0.00023 | -0.03914 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | FLINT CREEK 161KV | 528 | 0.00047 | -0.03938 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | GILL ENERGY CENTER 138KV | 180 | 0.00027 | -0.03918 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | GRDA | GRDA1 345KV | 520 | 0.00052 | -0.03943 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | GRDA | GRECCTG_1 20.000 345KV | 250 | 0.00052 | -0.03943 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | GRDA | GRECSTG_1 17.500 345KV | 150 | 0.00052 | -0.03943 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 8e-05 | -0.03899 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 8e-05 | -0.03899 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SWPA | KENNETT 69KV | 29 | 5e-05 | -0.03896 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | GRDA | KERR1 13.800 115KV | 28.5 | 0.00052 | -0.03943 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | EMDE | LARUSSEL 161KV | 96 | 0.00035 | -0.03926 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.00011 | -0.03902 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | LAWRENCE ENERGY CENTER 230KV | 373 | 0.00011 | -0.03902 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00047 | -0.03938 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | NORTHEASTERN STATION 138KV | 841 | 0.0006 | -0.03951 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | OEC 345KV | 1160 | 0.0006 | -0.03951 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OMPA | OMCDLEC1 13.800 345KV | 67.452 | 0.00076 | -0.03967 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | EMDE | OZARK BEACH 161KV | 16 | 0.00028 | -0.03919 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | GRDA | PENSA_U6 13.200 161KV | 21 | 0.0005 | -0.03941 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SWPA | POPLAR BLUFF 161KV | 32 | 7e-05 | -0.03898 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0.00066 | -0.03957 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | EMDE | RIVERTON 161KV | 108.1623 | 0.0004 | -0.03931 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | GRDA | SALINA_U6 13.400 161KV | 200.9172 | 0.00052 | -0.03943 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | SEMINOLE 138KV | 246 | 0.00039 | -0.0393 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | SEMINOLE 345KV | 494.229 | 0.00077 | -0.03968 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SWPA | SIKESTON 161KV | 235 | 5e-05 | -0.03896 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | SILNGW21 34.500 345KV | 25 | 0.00032 | -0.03923 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | SLATEGEN1 0.6900 34KV | 15 | 0.00054 | -0.03945 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | SOONER 138KV | 535 | 0.00096 | -0.03987 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | SOONER 345KV | 537 | 0.00096 | -0.03987 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | EMDE | STATE LINE 161KV | 500 | 0.00039 | -0.0393 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 9e-05 | -0.039 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | TULSA POWER STATION 138KV | 306 | 0.00066 | -0.03957 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WERE | WAVERGEN1 0.6900 34KV | 15 | 0.00026 | -0.03917 | 38
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | ARSENAL HILL 138KV | 509 | -0.00043 | -0.03848 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | ARSENAL HILL 69KV | 95.9526 | -0.00044 | -0.03847 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | EASTMAN 138KV | 346 | -0.0005 | -0.03841 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | FULTON 115KV | 153 | -0.00053 | -0.03838 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | KNOXLEE 138KV | 342 | -0.00049 | -0.03842 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | LEBROCK 345KV | 347 | -0.0005 | -0.03841 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | LIEBERMAN 138KV | 217 | -0.00045 | -0.03846 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WFEC | PEC BTMG62.5138.00 138KV | 62.5 | -0.00087 | -0.03804 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.0005 | -0.03841 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | TURK 138KV | 643 | -0.00064 | -0.03827 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | WELSH 345KV | 1056 | -0.00058 | -0.03833 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | WILKES 138KV | 468 | -0.00053 | -0.03838 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | WILKES 345KV | 348 | -0.00051 | -0.0384 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | WOODWARD CO SUB 2 138KV | 17 | -0.00032 | -0.03859 | 39
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WFEC | HUGO 138KV | 440 | -0.00101 | -0.0379 | 40
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | GRADY CO SUB 345KV | 18 | -0.00262 | -0.03629 | 41
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | OKGE | MNCWND31 34.500 345KV | 23 | -0.00262 | -0.03629 | 41
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WFEC | MORLND4 18.000 138KV | 272 | -0.00235 | -0.03656 | 41
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00233 | -0.03658 | 41
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | ANTELOPE 230KV | 160.794 | -0.00548 | -0.03343 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | ASGI10-010 113.800 115KV | 42 | -0.00579 | -0.03312 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | CUNNINGHAM 115KV | 121 | -0.00579 | -0.03312 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | CUNNINGHAM 230KV | 254 | -0.0058 | -0.03311 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | ELK_1 118.000 345KV | 195 | -0.00526 | -0.03365 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | ELK_2 1 18.000 345KV | 195 | -0.00526 | -0.03365 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | HOBBS PLANT #2 (CT) 115KV | 280 | -0.00579 | -0.03312 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | HOBBS PLANT #3 (ST) 230KV | 200 | -0.00579 | -0.03312 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | LUBBOCK CO SUB 230KV | 623 | -0.00557 | -0.03334 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | MADOX 115KV | 169.7 | -0.00579 | -0.03312 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | MUSTANG 115KV | 290 | -0.00577 | -0.03314 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | MUSTANG_6 118.000 230KV | 536.801 | -0.00577 | -0.03314 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | PLANTX 115KV | 184 | -0.00593 | -0.03298 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | PLANTX 230KV | 175 | -0.00591 | -0.033 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | SNJN-WTG14 10.6000 34KV | 30.64 | -0.00586 | -0.03305 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | SPNSPUR_WND134.500 345KV | 16.14 | -0.00534 | -0.03357 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | TOLK 230KV | 1018 | -0.00586 | -0.03305 | 45
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | BLACKHAWK 115KV | 220 | -0.0066 | -0.03231 | 46
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | HARRINGTON 230KV | 1017 | -0.00704 | -0.03187 | 47
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | NICHOLS 115KV | 180 | -0.00726 | -0.03165 | 47
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | SPS | NICHOLS 230KV | 161.5259 | -0.00711 | -0.0318 | 47
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | COMANCHE 138KV | 164.7 | -0.0079 | -0.03101 | 48
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | COMANCHE 69KV | 64 | -0.00828 | -0.03063 | 49
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WFEC | ANADARKO 138KV | 340.3314 | -0.01111 | -0.0278 | 54
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | SOUTHWESTERN STATION 138KV | 311 | -0.01194 | -0.02697 | 56
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0238 | 63
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0238 | 63
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.02314 | 65
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.02314 | 65
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.02314 | 65
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.02314 | 65
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.02314 | 65
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.02314 | 65
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.02282 | 66
WFEC | GOTEBO 2 69.000 69KV | 22.8 | -0.01854 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.02217 | 68
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | WFEC | GOTEBO 2 69.000 69KV | 51.2 | -0.01854 | -0.02037 | 74
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01899 | 79
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01899 | 79
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01833 | 82
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01833 | 82
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01833 | 82
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01833 | 82
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01833 | 82
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01833 | 82
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01801 | 83
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.01736 | 86
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0172 | 87
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0172 | 87
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01654 | 91
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01654 | 91
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01654 | 91
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01654 | 91
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01654 | 91
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01654 | 91
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01622 | 92
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.01593 | 94
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.01557 | 96
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | REDBUD 345KV | 1224 | 0.00155 | -0.01528 | 98
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 225 | 0.0016 | -0.01533 | 98
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | SOONER 138KV | 535 | 0.00096 | -0.01469 | 102
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | SOONER 345KV | 537 | 0.00096 | -0.01469 | 102
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | SEMINOLE 345KV | 494.229 | 0.00077 | -0.0145 | 103
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | COGENTRIX 345KV | 769 | 0.00067 | -0.0144 | 104
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OMPA | OMCDLEC1 13.800 345KV | 67.452 | 0.00076 | -0.01449 | 104
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0.00066 | -0.01439 | 104
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | TULSA POWER STATION 138KV | 306 | 0.00066 | -0.01439 | 104
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | GRDA | GRDA1 345KV | 520 | 0.00052 | -0.01425 | 105
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | GRDA | GRECCTG_1 20.000 345KV | 250 | 0.00052 | -0.01425 | 105
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | GRDA | GRECSTG_1 17.500 345KV | 150 | 0.00052 | -0.01425 | 105
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | NORTHEASTERN STATION 138KV | 841 | 0.0006 | -0.01433 | 105
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | OEC 345KV | 1160 | 0.0006 | -0.01433 | 105
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | GRDA | SALINA_U6 13.400 161KV | 200.9172 | 0.00052 | -0.01425 | 105
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | EMDE | ASBURY 161KV | 189 | 0.00038 | -0.01411 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | ELK RIVER 345KV | 46 | 0.00036 | -0.01409 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | ELKINS GENERATOR 69KV | 48.61 | 0.00047 | -0.0142 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | FLINT CREEK 161KV | 528 | 0.00047 | -0.0142 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00047 | -0.0142 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | EMDE | RIVERTON 161KV | 108.1623 | 0.0004 | -0.01413 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | SEMINOLE 138KV | 246 | 0.00039 | -0.01412 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | EMDE | STATE LINE 161KV | 500 | 0.00039 | -0.01412 | 106
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.01414 | 106
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | OKGE | AES 161KV | 320 | 0.00025 | -0.01398 | 107
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | FITZHUGH 161KV | 165 | 0.00023 | -0.01396 | 107
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | GILL ENERGY CENTER 138KV | 180 | 0.00027 | -0.014 | 107
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | EMDE | LARUSSEL 161KV | 96 | 0.00035 | -0.01408 | 107
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | EMPORIA ENERGY CENTER 345KV | 530.8169 | 0.00011 | -0.01384 | 108
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | EVANS ENERGY CENTER 138KV | 520 | 0.0002 | -0.01393 | 108
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.00011 | -0.01384 | 108
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | LAWRENCE ENERGY CENTER 230KV | 373 | 0.00011 | -0.01384 | 108
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 8e-05 | -0.01381 | 109
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 8e-05 | -0.01381 | 109
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SWPA | SIKESTON 161KV | 235 | 5e-05 | -0.01378 | 109
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 9e-05 | -0.01382 | 109
WFEC | HAMMON CO SUB 138KV | 108 | -0.03891 | AEPW | RKYRDGW1-1 34.500 138KV | 45 | -0.02539 | -0.01352 | 111
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | REDBUD 345KV | 1224 | 0.00155 | -0.01349 | 111
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 225 | 0.0016 | -0.01354 | 111
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | ARSENAL HILL 138KV | 509 | -0.00043 | -0.0133 | 113
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | ARSENAL HILL 69KV | 95.9526 | -0.00044 | -0.01329 | 113
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | EASTMAN 138KV | 346 | -0.0005 | -0.01323 | 113
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | KNOXLEE 138KV | 342 | -0.00049 | -0.01324 | 113
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | LEBROCK 345KV | 347 | -0.0005 | -0.01323 | 113
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | LIEBERMAN 138KV | 217 | -0.00045 | -0.01328 | 113
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.0005 | -0.01323 | 113
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | WILKES 345KV | 348 | -0.00051 | -0.01322 | 113
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01319 | 114
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01319 | 114
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | FULTON 115KV | 153 | -0.00053 | -0.0132 | 114
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | WELSH 345KV | 1056 | -0.00058 | -0.01315 | 114
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | WILKES 138KV | 468 | -0.00053 | -0.0132 | 114
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | TURK 138KV | 643 | -0.00064 | -0.01309 | 115
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | SOONER 138KV | 535 | 0.00096 | -0.0129 | 116
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | SOONER 345KV | 537 | 0.00096 | -0.0129 | 116
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WFEC | PEC BTMG62.5138.00 138KV | 62.5 | -0.00087 | -0.01286 | 117
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WFEC | HUGO 138KV | 440 | -0.00101 | -0.01272 | 118
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OMPA | OMCDLEC1 13.800 345KV | 67.452 | 0.00076 | -0.0127 | 118
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | SEMINOLE 345KV | 494.229 | 0.00077 | -0.01271 | 118
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | COGENTRIX 345KV | 769 | 0.00067 | -0.01261 | 119
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0.00066 | -0.0126 | 119
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | TULSA POWER STATION 138KV | 306 | 0.00066 | -0.0126 | 119
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01253 | 120
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01253 | 120
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01253 | 120
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01253 | 120
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01253 | 120
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01253 | 120
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01252 | 120
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01252 | 120
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | GRDA | GRDA1 345KV | 520 | 0.00052 | -0.01246 | 120
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | GRDA | GRECCTG_1 20.000 345KV | 250 | 0.00052 | -0.01246 | 120
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | GRDA | GRECSTG_1 17.500 345KV | 150 | 0.00052 | -0.01246 | 120
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | NORTHEASTERN STATION 138KV | 841 | 0.0006 | -0.01254 | 120
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | OEC 345KV | 1160 | 0.0006 | -0.01254 | 120
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | GRDA | SALINA_U6 13.400 161KV | 200.9172 | 0.00052 | -0.01246 | 120
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01237 | 121
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01237 | 121
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | ELKINS GENERATOR 69KV | 48.61 | 0.00047 | -0.01241 | 121
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | FLINT CREEK 161KV | 528 | 0.00047 | -0.01241 | 121
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00047 | -0.01241 | 121
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0123 | 122
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0123 | 122
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | EMDE | ASBURY 161KV | 189 | 0.00038 | -0.01232 | 122
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | ELK RIVER 345KV | 46 | 0.00036 | -0.0123 | 122
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | EMDE | LARUSSEL 161KV | 96 | 0.00035 | -0.01229 | 122
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | EMDE | RIVERTON 161KV | 108.1623 | 0.0004 | -0.01234 | 122
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | SEMINOLE 138KV | 246 | 0.00039 | -0.01233 | 122
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | EMDE | STATE LINE 161KV | 500 | 0.00039 | -0.01233 | 122
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01221 | 123
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | OKGE | AES 161KV | 320 | 0.00025 | -0.01219 | 123
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | FITZHUGH 161KV | 165 | 0.00023 | -0.01217 | 123
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | GILL ENERGY CENTER 138KV | 180 | 0.00027 | -0.01221 | 123
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | EMPORIA ENERGY CENTER 345KV | 530.8169 | 0.00011 | -0.01205 | 124
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | EVANS ENERGY CENTER 138KV | 520 | 0.0002 | -0.01214 | 124
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.00011 | -0.01205 | 124
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | LAWRENCE ENERGY CENTER 230KV | 373 | 0.00011 | -0.01205 | 124
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 8e-05 | -0.01202 | 125
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 8e-05 | -0.01202 | 125
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | SWPA | SIKESTON 161KV | 235 | 5e-05 | -0.01199 | 125
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 9e-05 | -0.01203 | 125
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01186 | 126
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01186 | 126
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01186 | 126
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01186 | 126
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01186 | 126
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01186 | 126
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01171 | 128
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01171 | 128
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01171 | 128
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01171 | 128
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01171 | 128
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01171 | 128
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01164 | 129
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01164 | 129
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01164 | 129
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01164 | 129
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01164 | 129
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01164 | 129
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.01156 | 130
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01154 | 130
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | ARSENAL HILL 138KV | 509 | -0.00043 | -0.01151 | 130
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | ARSENAL HILL 69KV | 95.9526 | -0.00044 | -0.0115 | 130
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | EASTMAN 138KV | 346 | -0.0005 | -0.01144 | 131
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | FULTON 115KV | 153 | -0.00053 | -0.01141 | 131
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | KNOXLEE 138KV | 342 | -0.00049 | -0.01145 | 131
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | LEBROCK 345KV | 347 | -0.0005 | -0.01144 | 131
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | LIEBERMAN 138KV | 217 | -0.00045 | -0.01149 | 131
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.0005 | -0.01144 | 131
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | WILKES 138KV | 468 | -0.00053 | -0.01141 | 131
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | WILKES 345KV | 348 | -0.00051 | -0.01143 | 131
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01132 | 132
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01139 | 132
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | WFEC | MORLND4 18.000 138KV | 272 | -0.00235 | -0.01138 | 132
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00233 | -0.0114 | 132
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | WELSH 345KV | 1056 | -0.00058 | -0.01136 | 132
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | TURK 138KV | 643 | -0.00064 | -0.0113 | 133
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01119 | 134
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01119 | 134
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0111 | 135
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0111 | 135
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0111 | 135
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.0111 | 135
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WFEC | PEC BTMG62.5138.00 138KV | 62.5 | -0.00087 | -0.01107 | 135
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01112 | 135
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01112 | 135
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01105 | 136
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01105 | 136
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01106 | 136
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01106 | 136
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01105 | 136
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01105 | 136
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01103 | 136
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01103 | 136
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WFEC | HUGO 138KV | 440 | -0.00101 | -0.01093 | 137
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01083 | 138
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01083 | 138
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01083 | 138
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | 0.00526 | -0.01083 | 138
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.01089 | 138
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.01074 | 140
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.01067 | 141
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01053 | 142
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01053 | 142
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01053 | 142
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01053 | 142
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01053 | 142
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01053 | 142
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01046 | 143
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01046 | 143
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01046 | 143
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01046 | 143
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01046 | 143
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01046 | 143
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01044 | 144
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01039 | 144
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.0104 | 144
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.0104 | 144
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.0104 | 144
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.0104 | 144
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.0104 | 144
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.0104 | 144
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01039 | 144
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01039 | 144
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01044 | 144
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01044 | 144
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01037 | 145
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01037 | 145
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01037 | 145
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01037 | 145
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01037 | 145
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01037 | 145
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01017 | 147
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | 0.0046 | -0.01017 | 147
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | MUSTANG 138KV | 221 | 0.0046 | -0.01017 | 147
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01021 | 147
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.01013 | 148
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01012 | 148
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01012 | 148
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01014 | 148
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01007 | 149
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01008 | 149
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01007 | 149
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.01005 | 149
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.00985 | 152
SPS | LUBBOCK CO SUB 230KV | 51 | -0.00557 | OKGE | SMITH COGEN 138KV | 107 | 0.00428 | -0.00985 | 152
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | WFEC | MORLND4 18.000 138KV | 272 | -0.00235 | -0.00959 | 156
AEPW | SOUTHWESTERN STATION 138KV | 323.7 | -0.01194 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00233 | -0.00961 | 156
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 225 | 0.0016 | -0.00953 | 157
SPS | PLANTX 115KV | 54.2 | -0.00593 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.00956 | 157
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | REDBUD 345KV | 1224 | 0.00155 | -0.00948 | 158
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.00947 | 158
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.00947 | 158
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.00949 | 158
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.00942 | 159
SPS | CUNNINGHAM 230KV | 58 | -0.0058 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.00943 | 159
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.00942 | 159
SPS | NICHOLS 115KV | 55.8 | -0.00726 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00946 | 159
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.0094 | 160
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00931 | 161
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00924 | 162
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | MCCLAIN 138KV | 481.5977 | 0.00363 | -0.0092 | 163
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | SOONER 138KV | 535 | 0.00096 | -0.00889 | 169
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | SOONER 345KV | 537 | 0.00096 | -0.00889 | 169
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | SEMINOLE 345KV | 494.229 | 0.00077 | -0.0087 | 172
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 225 | 0.0016 | -0.00871 | 172
WFEC | ANADARKO 69KV | 70 | -0.00793 | OMPA | OMCDLEC1 13.800 345KV | 67.452 | 0.00076 | -0.00869 | 173
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | REDBUD 345KV | 1224 | 0.00155 | -0.00866 | 173
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | COGENTRIX 345KV | 769 | 0.00067 | -0.0086 | 174
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 225 | 0.0016 | -0.00864 | 174
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0.00066 | -0.00859 | 175
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | TULSA POWER STATION 138KV | 306 | 0.00066 | -0.00859 | 175
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | REDBUD 345KV | 1224 | 0.00155 | -0.00859 | 175
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | NORTHEASTERN STATION 138KV | 841 | 0.0006 | -0.00853 | 176
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | OEC 345KV | 1160 | 0.0006 | -0.00853 | 176
WFEC | ANADARKO 69KV | 70 | -0.00793 | GRDA | GRDA1 345KV | 520 | 0.00052 | -0.00845 | 177
WFEC | ANADARKO 69KV | 70 | -0.00793 | GRDA | GRECCTG_1 20.000 345KV | 250 | 0.00052 | -0.00845 | 177
WFEC | ANADARKO 69KV | 70 | -0.00793 | GRDA | GRECSTG_1 17.500 345KV | 150 | 0.00052 | -0.00845 | 177
WFEC | ANADARKO 69KV | 70 | -0.00793 | GRDA | SALINA_U6 13.400 161KV | 200.9172 | 0.00052 | -0.00845 | 177
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | ELK_1 118.000 345KV | 195 | -0.00526 | -0.00847 | 177
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | ELK_2 1 18.000 345KV | 195 | -0.00526 | -0.00847 | 177
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | FLINT CREEK 161KV | 528 | 0.00047 | -0.0084 | 179
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00047 | -0.0084 | 179
WFEC | ANADARKO 69KV | 70 | -0.00793 | EMDE | ASBURY 161KV | 189 | 0.00038 | -0.00831 | 180
WFEC | ANADARKO 69KV | 70 | -0.00793 | EMDE | RIVERTON 161KV | 108.1623 | 0.0004 | -0.00833 | 180
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | SEMINOLE 138KV | 246 | 0.00039 | -0.00832 | 180
WFEC | ANADARKO 69KV | 70 | -0.00793 | EMDE | STATE LINE 161KV | 500 | 0.00039 | -0.00832 | 180
WFEC | ANADARKO 69KV | 70 | -0.00793 | EMDE | LARUSSEL 161KV | 96 | 0.00035 | -0.00828 | 181
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | ANTELOPE 230KV | 160.794 | -0.00548 | -0.00825 | 182
WFEC | ANADARKO 69KV | 70 | -0.00793 | OKGE | AES 161KV | 320 | 0.00025 | -0.00818 | 183
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | GILL ENERGY CENTER 138KV | 180 | 0.00027 | -0.0082 | 183
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | EVANS ENERGY CENTER 138KV | 520 | 0.0002 | -0.00813 | 184
WFEC | ANADARKO 69KV | 70 | -0.00793 | AEPW | FITZHUGH 161KV | 165 | 0.00023 | -0.00816 | 184
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | LUBBOCK CO SUB 230KV | 623 | -0.00557 | -0.00816 | 184
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | SOONER 138KV | 535 | 0.00096 | -0.00807 | 186
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | SOONER 345KV | 537 | 0.00096 | -0.00807 | 186
SPS | TOLK 230KV | 102.9 | -0.00586 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00806 | 186
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | EMPORIA ENERGY CENTER 345KV | 530.8169 | 0.00011 | -0.00804 | 187
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 8e-05 | -0.00801 | 187
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 8e-05 | -0.00801 | 187
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.00011 | -0.00804 | 187
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | LAWRENCE ENERGY CENTER 230KV | 373 | 0.00011 | -0.00804 | 187
WFEC | ANADARKO 69KV | 70 | -0.00793 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 9e-05 | -0.00802 | 187
SPS | CHVS_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00804 | 187
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | SOONER 138KV | 535 | 0.00096 | -0.008 | 187
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | SOONER 345KV | 537 | 0.00096 | -0.008 | 187
SPS | RSWL_SOLAR1134.500 115KV | 63 | -0.00584 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00804 | 187
WFEC | ANADARKO 69KV | 70 | -0.00793 | SWPA | SIKESTON 161KV | 235 | 5e-05 | -0.00798 | 188
SPS | CUNNINGHAM 115KV | 63 | -0.00579 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00799 | 188
SPS | GAINES_GEN1124.000 230KV | 225 | -0.00579 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00799 | 188
SPS | MUSTANG_6 118.000 230KV | 87.199 | -0.00577 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00797 | 188
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | MUSTANG 115KV | 290 | -0.00577 | -0.00796 | 188
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | MUSTANG_6 118.000 230KV | 536.801 | -0.00577 | -0.00796 | 188
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | CUNNINGHAM 115KV | 121 | -0.00579 | -0.00794 | 189
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | CUNNINGHAM 230KV | 254 | -0.0058 | -0.00793 | 189
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | HOBBS PLANT #2 (CT) 115KV | 280 | -0.00579 | -0.00794 | 189
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | HOBBS PLANT #3 (ST) 230KV | 200 | -0.00579 | -0.00794 | 189
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | MADOX 115KV | 169.7 | -0.00579 | -0.00794 | 189
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OKGE | SEMINOLE 345KV | 494.229 | 0.00077 | -0.00788 | 190
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | OMPA | OMCDLEC1 13.800 345KV | 67.452 | 0.00076 | -0.00787 | 191
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | TOLK 230KV | 1018 | -0.00586 | -0.00787 | 191
SPS | HARRINGTON 230KV | 84 | -0.00704 | OMPA | OMCDLEC1 13.800 345KV | 67.452 | 0.00076 | -0.0078 | 192
SPS | HARRINGTON 230KV | 84 | -0.00704 | OKGE | SEMINOLE 345KV | 494.229 | 0.00077 | -0.00781 | 192
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | PLANTX 115KV | 184 | -0.00593 | -0.0078 | 192
WFEC | SLICKHILLS4 138.00 138KV | 99 | -0.01373 | SPS | PLANTX 230KV | 175 | -0.00591 | -0.00782 | 192
SPS | LP-MACK2 69KV | 76 | -0.00557 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.0022 | -0.00777 | 193
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | AEPW | COGENTRIX 345KV | 769 | 0.00067 | -0.00778 | 193
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0.00066 | -0.00777 | 193
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | AEPW | TULSA POWER STATION 138KV | 306 | 0.00066 | -0.00777 | 193
SPS | HARRINGTON 230KV | 84 | -0.00704 | AEPW | COGENTRIX 345KV | 769 | 0.00067 | -0.00771 | 195
SPS | HARRINGTON 230KV | 84 | -0.00704 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0.00066 | -0.0077 | 195
SPS | HARRINGTON 230KV | 84 | -0.00704 | AEPW | TULSA POWER STATION 138KV | 306 | 0.00066 | -0.0077 | 195
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | AEPW | NORTHEASTERN STATION 138KV | 841 | 0.0006 | -0.00771 | 195
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | AEPW | OEC 345KV | 1160 | 0.0006 | -0.00771 | 195
SPS | HARRINGTON 230KV | 84 | -0.00704 | AEPW | NORTHEASTERN STATION 138KV | 841 | 0.0006 | -0.00764 | 196
SPS | HARRINGTON 230KV | 84 | -0.00704 | AEPW | OEC 345KV | 1160 | 0.0006 | -0.00764 | 196
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | GRDA | GRDA1 345KV | 520 | 0.00052 | -0.00763 | 197
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | GRDA | GRECCTG_1 20.000 345KV | 250 | 0.00052 | -0.00763 | 197
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | GRDA | GRECSTG_1 17.500 345KV | 150 | 0.00052 | -0.00763 | 197
SPS | NICHOLS 230KV | 98.1741 | -0.00711 | GRDA | SALINA_U6 13.400 161KV | 200.9172 | 0.00052 | -0.00763 | 197
SPS | HARRINGTON 230KV | 84 | -0.00704 | GRDA | GRDA1 345KV | 520 | 0.00052 | -0.00756 | 198
SPS | HARRINGTON 230KV | 84 | -0.00704 | GRDA | GRECCTG_1 20.000 345KV | 250 | 0.00052 | -0.00756 | 198
SPS | HARRINGTON 230KV | 84 | -0.00704 | GRDA | GRECSTG_1 17.500 345KV | 150 | 0.00052 | -0.00756 | 198
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1
Limiting Facility: | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1
Direction: | FROM->TO
Line Outage: | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1
Flowgate: | 2017AG1AFS11T10275518SP
Date Redispatch Needed: | Starting 2018 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2018 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
84877548 | 5.7 | 8.6
84877556 | 2.9 | 8.6
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01795 | -0.45539 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | AINSWORTH WIND 34KV | 60 | 0.00947 | -0.44691 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | ARIES 161KV | 402 | 0.00345 | -0.44089 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | AUBURN 69KV | 9 | 0.00838 | -0.44582 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01593 | -0.45337 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | BELOIT 115KV | 12.13 | 0.01831 | -0.45575 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01085 | -0.44829 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.4569 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.4569 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00475 | -0.44219 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.0073 | -0.44474 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | CENT 21 34.500 138KV | 120 | 0.01236 | -0.4498 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.46013 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | CITY OF OSAGE CITY 115KV | 10.271 | 0.01304 | -0.45048 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | COLBY 115KV | 9.046 | 0.01777 | -0.45521 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | COLBY 69KV | 6.3537 | 0.01777 | -0.45521 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00829 | -0.44573 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.01916 | -0.4566 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00746 | -0.4449 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00894 | -0.44638 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | CW BURDICKGT3 115KV | 15.71 | 0.01026 | -0.4477 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | DENVER 115KV | 23.453 | 0.01064 | -0.44808 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00793 | -0.44537 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00746 | -0.4449 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.45971 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | ENERGY CENTER 115KV | 77 | 0.0106 | -0.44804 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.0106 | -0.44804 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.45963 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02107 | -0.45851 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00744 | -0.44488 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | FREMONT 8 69KV | 88.21 | 0.00761 | -0.44505 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00638 | -0.44382 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00545 | -0.44289 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.01993 | -0.45737 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01271 | -0.45015 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01288 | -0.45032 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | GMECG2 1 13.800 115KV | 22.3658 | 0.01921 | -0.45665 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.46094 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | GREENSBURG 115KV | 12.5 | 0.02212 | -0.45956 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00496 | -0.4424 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.45746 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | IATAN 345KV | 1606 | 0.00719 | -0.44463 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.46269 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.01552 | -0.45296 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01554 | -0.45298 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.46094 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00675 | -0.44419 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | LARNED3 115.00 115KV | 9.729 | 0.01632 | -0.45376 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.0105 | -0.44794 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01135 | -0.44879 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | LYONS 115KV | 9 | 0.01313 | -0.45057 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01209 | -0.44953 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | MONTROSE 161KV | 335 | 0.00243 | -0.43987 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.45711 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KACY | NEARMAN 20KV | 235 | 0.00533 | -0.44277 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00728 | -0.44472 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00728 | -0.44472 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00724 | -0.44468 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00724 | -0.44468 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | NORTH PLATTE HYDRO 115KV | 12 | 0.01253 | -0.44997 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | OU SPIRIT 138KV | 102 | 0.01392 | -0.45136 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01593 | -0.45337 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00836 | -0.4458 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | PLATTE 115KV | 90 | 0.01034 | -0.44778 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | PRATT 115KV | 13.49 | 0.01825 | -0.45569 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01267 | -0.45011 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KACY | QUINDARO 161KV | 117.9024 | 0.00531 | -0.44275 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KACY | QUINDARO 69KV | 36.1403 | 0.0053 | -0.44274 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00236 | -0.4398 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.45707 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | RUSSELL 115KV | 12.55 | 0.01674 | -0.45418 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | S ALMA 3 115.00 115KV | 11.6 | 0.01554 | -0.45298 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.01075 | -0.44819 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00726 | -0.4447 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00726 | -0.4447 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.00966 | -0.4471 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.45665 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00857 | -0.44601 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | SIBLEY 161KV | 354 | 0.00441 | -0.44185 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | SIBLEY 69KV | 97 | 0.0045 | -0.44194 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00894 | -0.44638 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00894 | -0.44638 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.4566 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | SOUTH OTTAWA 161KV | 26.7 | 0.0027 | -0.44014 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.46159 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.45984 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | SUB H 13KV | 14 | 0.01026 | -0.4477 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01242 | -0.44986 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00836 | -0.4458 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01079 | -0.44823 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | WEST GARDNER 161KV | 10.4 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01392 | -0.45136 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00217 | -0.43961 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01795 | -0.45539 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | AINSWORTH WIND 34KV | 60 | 0.00947 | -0.44691 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | ARIES 161KV | 402 | 0.00345 | -0.44089 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | AUBURN 69KV | 9 | 0.00838 | -0.44582 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01593 | -0.45337 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | BELOIT 115KV | 12.13 | 0.01831 | -0.45575 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01085 | -0.44829 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.4569 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.4569 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00475 | -0.44219 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.0073 | -0.44474 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | CENT 21 34.500 138KV | 120 | 0.01236 | -0.4498 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.46013 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | CITY OF OSAGE CITY 115KV | 10.271 | 0.01304 | -0.45048 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | COLBY 115KV | 9.046 | 0.01777 | -0.45521 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | COLBY 69KV | 6.3537 | 0.01777 | -0.45521 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00829 | -0.44573 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.01916 | -0.4566 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00746 | -0.4449 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00894 | -0.44638 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | CW BURDICKGT3 115KV | 15.71 | 0.01026 | -0.4477 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | DENVER 115KV | 23.453 | 0.01064 | -0.44808 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00793 | -0.44537 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00746 | -0.4449 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.45971 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | ENERGY CENTER 115KV | 77 | 0.0106 | -0.44804 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.0106 | -0.44804 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.45963 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02107 | -0.45851 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00744 | -0.44488 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | FREMONT 8 69KV | 88.21 | 0.00761 | -0.44505 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00638 | -0.44382 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00545 | -0.44289 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.01993 | -0.45737 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01271 | -0.45015 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01288 | -0.45032 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | GMECG2 1 13.800 115KV | 22.3658 | 0.01921 | -0.45665 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.46094 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | GREENSBURG 115KV | 12.5 | 0.02212 | -0.45956 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00496 | -0.4424 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.45746 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | IATAN 345KV | 1606 | 0.00719 | -0.44463 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.46269 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.01552 | -0.45296 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01554 | -0.45298 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.46094 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00675 | -0.44419 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | LARNED3 115.00 115KV | 9.729 | 0.01632 | -0.45376 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.0105 | -0.44794 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01135 | -0.44879 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | LYONS 115KV | 9 | 0.01313 | -0.45057 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01209 | -0.44953 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | MONTROSE 161KV | 335 | 0.00243 | -0.43987 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.45711 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KACY | NEARMAN 20KV | 235 | 0.00533 | -0.44277 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00728 | -0.44472 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00728 | -0.44472 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00724 | -0.44468 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00724 | -0.44468 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | NORTH PLATTE HYDRO 115KV | 12 | 0.01253 | -0.44997 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | OU SPIRIT 138KV | 102 | 0.01392 | -0.45136 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01593 | -0.45337 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00836 | -0.4458 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | PLATTE 115KV | 90 | 0.01034 | -0.44778 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | PRATT 115KV | 13.49 | 0.01825 | -0.45569 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01267 | -0.45011 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KACY | QUINDARO 161KV | 117.9024 | 0.00531 | -0.44275 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KACY | QUINDARO 69KV | 36.1403 | 0.0053 | -0.44274 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00236 | -0.4398 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.45707 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | RUSSELL 115KV | 12.55 | 0.01674 | -0.45418 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | S ALMA 3 115.00 115KV | 11.6 | 0.01554 | -0.45298 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.01075 | -0.44819 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00726 | -0.4447 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00726 | -0.4447 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.00966 | -0.4471 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.45665 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00857 | -0.44601 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | SIBLEY 161KV | 354 | 0.00441 | -0.44185 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | SIBLEY 69KV | 97 | 0.0045 | -0.44194 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00894 | -0.44638 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00894 | -0.44638 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.4566 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | SOUTH OTTAWA 161KV | 26.7 | 0.0027 | -0.44014 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.46159 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.45984 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | SUB H 13KV | 14 | 0.01026 | -0.4477 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01242 | -0.44986 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00836 | -0.4458 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01079 | -0.44823 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | WEST GARDNER 161KV | 10.4 | 0.00476 | -0.4422 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01392 | -0.45136 | 19
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00217 | -0.43961 | 19
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.4365 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.4365 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | AES 161KV | 320 | -0.00327 | -0.43417 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00105 | -0.43639 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | ARSENAL HILL 138KV | 509 | -0.00118 | -0.43626 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | EMDE | ASBURY 161KV | 189 | -0.00809 | -0.42935 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | -0.01842 | -0.41902 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00532 | -0.43212 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | CANDN12 34.500 345KV | 298.2 | -9e-05 | -0.43735 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | CENTERVILLE 161KV | 9.7 | -0.00293 | -0.43451 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00201 | -0.43543 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | COGENTRIX 345KV | 830 | -0.00569 | -0.43175 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | COMANCHE 138KV | 164.7 | 0.00129 | -0.43873 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | COMANCHE 69KV | 64 | 0.00119 | -0.43863 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | EASTMAN 138KV | 150 | -0.00121 | -0.43623 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | FLINT CREEK 161KV | 528 | -0.00615 | -0.43129 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | GRADY CO SUB 345KV | 99 | 0.0005 | -0.43794 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00048 | -0.43696 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.0019 | -0.43554 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | HORSESHOE LAKE 69KV | 16 | -0.0018 | -0.43564 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | KNOXLEE 138KV | 254.3647 | -0.0012 | -0.43624 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.0021 | -0.43534 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | EMDE | LARUSSEL 161KV | 95.901 | -0.00623 | -0.43121 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00089 | -0.43655 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | MNCWND31 34.500 345KV | 100 | 0.0005 | -0.43794 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.00458 | -0.43286 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | MUSTANG 138KV | 221 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.00785 | -0.42959 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00232 | -0.43512 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | OEC 345KV | 1160 | -0.00609 | -0.43135 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00082 | -0.43662 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | EMDE | OZARK BEACH 161KV | 16 | -0.00427 | -0.43317 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00121 | -0.43623 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | REDBUD 345KV | 1224 | -0.00204 | -0.4354 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00584 | -0.4316 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SEMINOLE 138KV | 149.9142 | -0.00168 | -0.43576 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SEMINOLE 345KV | 433.186 | -0.0017 | -0.43574 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SMITH COGEN 138KV | 107 | -0.00097 | -0.43647 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SOONER 138KV | 535 | -0.01263 | -0.42481 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SOONER 345KV | 537 | -0.01032 | -0.42712 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00096 | -0.4384 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.002 | -0.43544 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | EMDE | STATE LINE 161KV | 440.6939 | -0.00743 | -0.43001 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | TURK 138KV | 643 | -0.00132 | -0.43612 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01427 | -0.42317 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | WELSH 345KV | 1056 | -0.00125 | -0.43619 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | WILKES 138KV | 299.8593 | -0.00123 | -0.43621 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | AEPW | WILKES 345KV | 348 | -0.00123 | -0.43621 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.4365 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.4365 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | AES 161KV | 320 | -0.00327 | -0.43417 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00105 | -0.43639 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | ARSENAL HILL 138KV | 509 | -0.00118 | -0.43626 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | EMDE | ASBURY 161KV | 189 | -0.00809 | -0.42935 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | -0.01842 | -0.41902 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00532 | -0.43212 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | CANDN12 34.500 345KV | 298.2 | -9e-05 | -0.43735 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | CENTERVILLE 161KV | 9.7 | -0.00293 | -0.43451 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00201 | -0.43543 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | COGENTRIX 345KV | 830 | -0.00569 | -0.43175 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | COMANCHE 138KV | 164.7 | 0.00129 | -0.43873 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | COMANCHE 69KV | 64 | 0.00119 | -0.43863 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | EASTMAN 138KV | 150 | -0.00121 | -0.43623 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | FLINT CREEK 161KV | 528 | -0.00615 | -0.43129 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | GRADY CO SUB 345KV | 99 | 0.0005 | -0.43794 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00048 | -0.43696 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.0019 | -0.43554 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | HORSESHOE LAKE 69KV | 16 | -0.0018 | -0.43564 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | KNOXLEE 138KV | 254.3647 | -0.0012 | -0.43624 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.0021 | -0.43534 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | EMDE | LARUSSEL 161KV | 95.901 | -0.00623 | -0.43121 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00089 | -0.43655 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | MNCWND31 34.500 345KV | 100 | 0.0005 | -0.43794 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.00458 | -0.43286 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | MUSTANG 138KV | 221 | -0.00092 | -0.43652 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.00785 | -0.42959 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00232 | -0.43512 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | OEC 345KV | 1160 | -0.00609 | -0.43135 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00082 | -0.43662 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | EMDE | OZARK BEACH 161KV | 16 | -0.00427 | -0.43317 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00121 | -0.43623 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | REDBUD 345KV | 1224 | -0.00204 | -0.4354 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00584 | -0.4316 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SEMINOLE 138KV | 149.9142 | -0.00168 | -0.43576 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SEMINOLE 345KV | 433.186 | -0.0017 | -0.43574 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SMITH COGEN 138KV | 107 | -0.00097 | -0.43647 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SOONER 138KV | 535 | -0.01263 | -0.42481 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SOONER 345KV | 537 | -0.01032 | -0.42712 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00096 | -0.4384 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.002 | -0.43544 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | EMDE | STATE LINE 161KV | 440.6939 | -0.00743 | -0.43001 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | TURK 138KV | 643 | -0.00132 | -0.43612 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01427 | -0.42317 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | WELSH 345KV | 1056 | -0.00125 | -0.43619 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | WILKES 138KV | 299.8593 | -0.00123 | -0.43621 | 20
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | AEPW | WILKES 345KV | 348 | -0.00123 | -0.43621 | 20
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.02841 | -0.40903 | 21
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | ELK RIVER 345KV | 150 | -0.03024 | -0.4072 | 21
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02258 | -0.41486 | 21
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.02841 | -0.40903 | 21
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | ELK RIVER 345KV | 150 | -0.03024 | -0.4072 | 21
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02258 | -0.41486 | 21
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.43744 | WERE | SLATEGEN1 0.6900 34KV | 150 | -0.07162 | -0.36582 | 23
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.43744 | WERE | SLATEGEN1 0.6900 34KV | 150 | -0.07162 | -0.36582 | 23
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.24145 | 35
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.2432 | 35
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.24145 | 35
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.2421 | 35
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01795 | -0.2359 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | BELOIT 115KV | 12.13 | 0.01831 | -0.23626 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.23741 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.23741 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.24064 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.01916 | -0.23711 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.24022 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.24014 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02107 | -0.23902 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.01993 | -0.23788 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | MIDW | GMECG2 1 13.800 115KV | 22.3658 | 0.01921 | -0.23716 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | GREENSBURG 115KV | 12.5 | 0.02212 | -0.24007 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.23797 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.23762 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | PRATT 115KV | 13.49 | 0.01825 | -0.2362 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.23758 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.23716 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.23711 | 36
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.24035 | 36
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.22981 | 37
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.22871 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01593 | -0.23388 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01085 | -0.2288 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | CENT 21 34.500 138KV | 120 | 0.01236 | -0.23031 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | DENVER 115KV | 23.453 | 0.01064 | -0.22859 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | ENERGY CENTER 115KV | 77 | 0.0106 | -0.22855 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.0106 | -0.22855 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01271 | -0.23066 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01288 | -0.23083 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.01552 | -0.23347 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01554 | -0.23349 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.0105 | -0.22845 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01135 | -0.2293 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01209 | -0.23004 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | OU SPIRIT 138KV | 102 | 0.01392 | -0.23187 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01593 | -0.23388 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01267 | -0.23062 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | SUNC | RUSSELL 115KV | 12.55 | 0.01674 | -0.23469 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.01075 | -0.2287 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01242 | -0.23037 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01079 | -0.22874 | 37
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01392 | -0.23187 | 37
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.22402 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.22402 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.22725 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.01916 | -0.22372 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.22683 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.22675 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02107 | -0.22563 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.01993 | -0.22449 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | MIDW | GMECG2 1 13.800 115KV | 22.3658 | 0.01921 | -0.22377 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.22806 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.22458 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.22806 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.22423 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | PRATT 115KV | 13.49 | 0.01825 | -0.22281 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.22419 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.22377 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.22372 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.22696 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | AINSWORTH WIND 34KV | 60 | 0.00947 | -0.22742 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00475 | -0.2227 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.0073 | -0.22525 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00829 | -0.22624 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00746 | -0.22541 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00894 | -0.22689 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | CW BURDICKGT3 115KV | 15.71 | 0.01026 | -0.22821 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00793 | -0.22588 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00746 | -0.22541 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00744 | -0.22539 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00476 | -0.22271 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00476 | -0.22271 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00476 | -0.22271 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00476 | -0.22271 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | FREMONT 8 69KV | 88.21 | 0.00761 | -0.22556 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00638 | -0.22433 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00545 | -0.2234 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00496 | -0.22291 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | IATAN 345KV | 1606 | 0.00719 | -0.22514 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00675 | -0.2247 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KACY | NEARMAN 20KV | 235 | 0.00533 | -0.22328 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00728 | -0.22523 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00728 | -0.22523 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00724 | -0.22519 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00724 | -0.22519 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00836 | -0.22631 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | PLATTE 115KV | 90 | 0.01034 | -0.22829 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KACY | QUINDARO 161KV | 117.9024 | 0.00531 | -0.22326 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KACY | QUINDARO 69KV | 36.1403 | 0.0053 | -0.22325 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00726 | -0.22521 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00726 | -0.22521 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.00966 | -0.22761 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00857 | -0.22652 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00894 | -0.22689 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00894 | -0.22689 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | NPPD | SUB H 13KV | 14 | 0.01026 | -0.22821 | 38
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00836 | -0.22631 | 38
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01795 | -0.22251 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01593 | -0.22049 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | CENT 21 34.500 138KV | 120 | 0.01236 | -0.21692 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01271 | -0.21727 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01288 | -0.21744 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.01552 | -0.22008 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01554 | -0.2201 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | OU SPIRIT 138KV | 102 | 0.01392 | -0.21848 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01593 | -0.22049 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01267 | -0.21723 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01242 | -0.21698 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01392 | -0.21848 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.21703 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.21703 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.21703 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.21701 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.21701 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.21703 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.21703 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00105 | -0.2169 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | ARIES 161KV | 402 | 0.00345 | -0.2214 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | CANDN12 34.500 345KV | 298.2 | -9e-05 | -0.21786 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | COMANCHE 138KV | 164.7 | 0.00129 | -0.21924 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | COMANCHE 69KV | 64 | 0.00119 | -0.21914 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | GRADY CO SUB 345KV | 99 | 0.0005 | -0.21845 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00048 | -0.21747 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00089 | -0.21706 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | MNCWND31 34.500 345KV | 100 | 0.0005 | -0.21845 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | MONTROSE 161KV | 335 | 0.00243 | -0.22038 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | MUSTANG 138KV | 221 | -0.00092 | -0.21703 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00082 | -0.21713 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00236 | -0.22031 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | SIBLEY 161KV | 354 | 0.00441 | -0.22236 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | SIBLEY 69KV | 97 | 0.0045 | -0.22245 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SMITH COGEN 138KV | 107 | -0.00097 | -0.21698 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | SOUTH OTTAWA 161KV | 26.7 | 0.0027 | -0.22065 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00096 | -0.21891 | 39
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00217 | -0.22012 | 39
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | AINSWORTH WIND 34KV | 60 | 0.00947 | -0.21403 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01085 | -0.21541 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.0073 | -0.21186 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00829 | -0.21285 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00746 | -0.21202 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00894 | -0.2135 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | CW BURDICKGT3 115KV | 15.71 | 0.01026 | -0.21482 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | DENVER 115KV | 23.453 | 0.01064 | -0.2152 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00793 | -0.21249 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00746 | -0.21202 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | ENERGY CENTER 115KV | 77 | 0.0106 | -0.21516 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.0106 | -0.21516 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00744 | -0.212 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | FREMONT 8 69KV | 88.21 | 0.00761 | -0.21217 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | IATAN 345KV | 1606 | 0.00719 | -0.21175 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.0105 | -0.21506 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01135 | -0.21591 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01209 | -0.21665 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00728 | -0.21184 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00728 | -0.21184 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00724 | -0.2118 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00724 | -0.2118 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00836 | -0.21292 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | PLATTE 115KV | 90 | 0.01034 | -0.2149 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.01075 | -0.21531 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00726 | -0.21182 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00726 | -0.21182 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.00966 | -0.21422 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00857 | -0.21313 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00894 | -0.2135 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00894 | -0.2135 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | SUB H 13KV | 14 | 0.01026 | -0.21482 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00836 | -0.21292 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01079 | -0.21535 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | AES 161KV | 320 | -0.00327 | -0.21468 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | ARSENAL HILL 138KV | 509 | -0.00118 | -0.21677 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00532 | -0.21263 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00201 | -0.21594 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | COGENTRIX 345KV | 830 | -0.00569 | -0.21226 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | EASTMAN 138KV | 150 | -0.00121 | -0.21674 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | FLINT CREEK 161KV | 528 | -0.00615 | -0.2118 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.0019 | -0.21605 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | HORSESHOE LAKE 69KV | 16 | -0.0018 | -0.21615 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | KNOXLEE 138KV | 254.3647 | -0.0012 | -0.21675 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.0021 | -0.21585 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | EMDE | LARUSSEL 161KV | 95.901 | -0.00623 | -0.21172 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.00458 | -0.21337 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00232 | -0.21563 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | OEC 345KV | 1160 | -0.00609 | -0.21186 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | EMDE | OZARK BEACH 161KV | 16 | -0.00427 | -0.21368 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00121 | -0.21674 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | REDBUD 345KV | 1224 | -0.00204 | -0.21591 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00584 | -0.21211 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SEMINOLE 138KV | 149.9142 | -0.00168 | -0.21627 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SEMINOLE 345KV | 433.186 | -0.0017 | -0.21625 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.002 | -0.21595 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | TURK 138KV | 643 | -0.00132 | -0.21663 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | WELSH 345KV | 1056 | -0.00125 | -0.2167 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | WILKES 138KV | 299.8593 | -0.00123 | -0.21672 | 40
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | WILKES 345KV | 348 | -0.00123 | -0.21672 | 40
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | ARIES 161KV | 402 | 0.00345 | -0.20801 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00475 | -0.20931 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00476 | -0.20932 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00476 | -0.20932 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00476 | -0.20932 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00476 | -0.20932 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00638 | -0.21094 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00545 | -0.21001 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00496 | -0.20952 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00675 | -0.21131 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | MONTROSE 161KV | 335 | 0.00243 | -0.20699 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KACY | NEARMAN 20KV | 235 | 0.00533 | -0.20989 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KACY | QUINDARO 161KV | 117.9024 | 0.00531 | -0.20987 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KACY | QUINDARO 69KV | 36.1403 | 0.0053 | -0.20986 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00236 | -0.20692 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | SIBLEY 161KV | 354 | 0.00441 | -0.20897 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | SIBLEY 69KV | 97 | 0.0045 | -0.20906 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | SOUTH OTTAWA 161KV | 26.7 | 0.0027 | -0.20726 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00217 | -0.20673 | 41
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | EMDE | ASBURY 161KV | 189 | -0.00809 | -0.20986 | 41
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.00785 | -0.2101 | 41
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SOONER 345KV | 537 | -0.01032 | -0.20763 | 41
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | EMDE | STATE LINE 161KV | 440.6939 | -0.00743 | -0.21052 | 41
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.20364 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.20364 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.20364 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.20362 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.20362 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.20364 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.20364 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00105 | -0.20351 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | ARSENAL HILL 138KV | 509 | -0.00118 | -0.20338 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | CANDN12 34.500 345KV | 298.2 | -9e-05 | -0.20447 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00201 | -0.20255 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | COMANCHE 138KV | 164.7 | 0.00129 | -0.20585 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | COMANCHE 69KV | 64 | 0.00119 | -0.20575 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | EASTMAN 138KV | 150 | -0.00121 | -0.20335 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | GRADY CO SUB 345KV | 99 | 0.0005 | -0.20506 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00048 | -0.20408 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.0019 | -0.20266 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | HORSESHOE LAKE 69KV | 16 | -0.0018 | -0.20276 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | KNOXLEE 138KV | 254.3647 | -0.0012 | -0.20336 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.0021 | -0.20246 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00089 | -0.20367 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | MNCWND31 34.500 345KV | 100 | 0.0005 | -0.20506 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | MUSTANG 138KV | 221 | -0.00092 | -0.20364 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00232 | -0.20224 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00082 | -0.20374 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00121 | -0.20335 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | REDBUD 345KV | 1224 | -0.00204 | -0.20252 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SEMINOLE 138KV | 149.9142 | -0.00168 | -0.20288 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SEMINOLE 345KV | 433.186 | -0.0017 | -0.20286 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SMITH COGEN 138KV | 107 | -0.00097 | -0.20359 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00096 | -0.20552 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.002 | -0.20256 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | TURK 138KV | 643 | -0.00132 | -0.20324 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | WELSH 345KV | 1056 | -0.00125 | -0.20331 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | WILKES 138KV | 299.8593 | -0.00123 | -0.20333 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | WILKES 345KV | 348 | -0.00123 | -0.20333 | 42
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | SOONER 138KV | 535 | -0.01263 | -0.20532 | 42
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01427 | -0.20368 | 42
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | AES 161KV | 320 | -0.00327 | -0.20129 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00532 | -0.19924 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | COGENTRIX 345KV | 830 | -0.00569 | -0.19887 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | FLINT CREEK 161KV | 528 | -0.00615 | -0.19841 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | EMDE | LARUSSEL 161KV | 95.901 | -0.00623 | -0.19833 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.00458 | -0.19998 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | OEC 345KV | 1160 | -0.00609 | -0.19847 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | EMDE | OZARK BEACH 161KV | 16 | -0.00427 | -0.20029 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00584 | -0.19872 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | EMDE | STATE LINE 161KV | 440.6939 | -0.00743 | -0.19713 | 43
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | -0.01842 | -0.19953 | 43
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | EMDE | ASBURY 161KV | 189 | -0.00809 | -0.19647 | 44
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.00785 | -0.19671 | 44
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SOONER 345KV | 537 | -0.01032 | -0.19424 | 44
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02258 | -0.19537 | 44
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | SOONER 138KV | 535 | -0.01263 | -0.19193 | 45
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01427 | -0.19029 | 45
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.02841 | -0.18954 | 45
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | -0.01842 | -0.18614 | 46
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | ELK RIVER 345KV | 150 | -0.03024 | -0.18771 | 46
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02258 | -0.18198 | 47
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.02841 | -0.17615 | 49
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | ELK RIVER 345KV | 150 | -0.03024 | -0.17432 | 49
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.15766 | 54
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.1551 | 55
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.15468 | 55
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.1546 | 55
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.15591 | 55
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.15591 | 55
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.15656 | 55
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.15481 | 55
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.15187 | 56
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.15187 | 56
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02107 | -0.15348 | 56
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.01993 | -0.15234 | 56
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.15243 | 56
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.15208 | 56
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.15204 | 56
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01795 | -0.15036 | 57
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.01916 | -0.15157 | 57
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | MIDW | GMECG2 1 13.800 115KV | 22.3658 | 0.01921 | -0.15162 | 57
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.15162 | 57
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.15157 | 57
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01593 | -0.14834 | 58
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.01552 | -0.14793 | 58
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01554 | -0.14795 | 58
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01593 | -0.14834 | 58
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | CENT 21 34.500 138KV | 120 | 0.01236 | -0.14477 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01271 | -0.14512 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01288 | -0.14529 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01209 | -0.1445 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | OU SPIRIT 138KV | 102 | 0.01392 | -0.14633 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01267 | -0.14508 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01242 | -0.14483 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01392 | -0.14633 | 59
WERE | WACO S 4 138.00 138KV | 30 | -0.21795 | WERE | SLATEGEN1 0.6900 34KV | 150 | -0.07162 | -0.14633 | 59
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | AINSWORTH WIND 34KV | 60 | 0.00947 | -0.14188 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01085 | -0.14326 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | DENVER 115KV | 23.453 | 0.01064 | -0.14305 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | ENERGY CENTER 115KV | 77 | 0.0106 | -0.14301 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.0106 | -0.14301 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.0105 | -0.14291 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01135 | -0.14376 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | PLATTE 115KV | 90 | 0.01034 | -0.14275 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.01075 | -0.14316 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.00966 | -0.14207 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01079 | -0.1432 | 60
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.0073 | -0.13971 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00829 | -0.1407 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00746 | -0.13987 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00894 | -0.14135 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00793 | -0.14034 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00746 | -0.13987 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00744 | -0.13985 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | FREMONT 8 69KV | 88.21 | 0.00761 | -0.14002 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | IATAN 345KV | 1606 | 0.00719 | -0.1396 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00728 | -0.13969 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00728 | -0.13969 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00724 | -0.13965 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00724 | -0.13965 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00836 | -0.14077 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00726 | -0.13967 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00726 | -0.13967 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00857 | -0.14098 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00894 | -0.14135 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00894 | -0.14135 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00836 | -0.14077 | 61
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00475 | -0.13716 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00476 | -0.13717 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00476 | -0.13717 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00476 | -0.13717 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00476 | -0.13717 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00638 | -0.13879 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00545 | -0.13786 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00496 | -0.13737 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00675 | -0.13916 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KACY | NEARMAN 20KV | 235 | 0.00533 | -0.13774 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KACY | QUINDARO 161KV | 117.9024 | 0.00531 | -0.13772 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KACY | QUINDARO 69KV | 36.1403 | 0.0053 | -0.13771 | 62
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | ARIES 161KV | 402 | 0.00345 | -0.13586 | 63
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | SIBLEY 161KV | 354 | 0.00441 | -0.13682 | 63
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | SIBLEY 69KV | 97 | 0.0045 | -0.13691 | 63
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | SOUTH OTTAWA 161KV | 26.7 | 0.0027 | -0.13511 | 63
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | COMANCHE 138KV | 164.7 | 0.00129 | -0.1337 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | COMANCHE 69KV | 64 | 0.00119 | -0.1336 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | GRADY CO SUB 345KV | 99 | 0.0005 | -0.13291 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | MNCWND31 34.500 345KV | 100 | 0.0005 | -0.13291 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | MONTROSE 161KV | 335 | 0.00243 | -0.13484 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00236 | -0.13477 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00096 | -0.13337 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00217 | -0.13458 | 64
WERE | GILL ENERGY CENTER 138KV | 192 | -0.20456 | WERE | SLATEGEN1 0.6900 34KV | 150 | -0.07162 | -0.13294 | 64
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.13149 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.13149 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.13149 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.13147 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.13147 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.13149 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.13149 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00105 | -0.13136 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | ARSENAL HILL 138KV | 509 | -0.00118 | -0.13123 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | CANDN12 34.500 345KV | 298.2 | -9e-05 | -0.13232 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | EASTMAN 138KV | 150 | -0.00121 | -0.1312 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00048 | -0.13193 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | KNOXLEE 138KV | 254.3647 | -0.0012 | -0.13121 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00089 | -0.13152 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | MUSTANG 138KV | 221 | -0.00092 | -0.13149 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00082 | -0.13159 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00121 | -0.1312 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SMITH COGEN 138KV | 107 | -0.00097 | -0.13144 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | TURK 138KV | 643 | -0.00132 | -0.13109 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | WELSH 345KV | 1056 | -0.00125 | -0.13116 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | WILKES 138KV | 299.8593 | -0.00123 | -0.13118 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | WILKES 345KV | 348 | -0.00123 | -0.13118 | 65
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | AES 161KV | 320 | -0.00327 | -0.12914 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00201 | -0.1304 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.0019 | -0.13051 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.0021 | -0.13031 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00232 | -0.13009 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | REDBUD 345KV | 1224 | -0.00204 | -0.13037 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SEMINOLE 138KV | 149.9142 | -0.00168 | -0.13073 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SEMINOLE 345KV | 433.186 | -0.0017 | -0.13071 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.002 | -0.13041 | 66
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00532 | -0.12709 | 67
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.00458 | -0.12783 | 67
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | COGENTRIX 345KV | 830 | -0.00569 | -0.12672 | 68
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | FLINT CREEK 161KV | 528 | -0.00615 | -0.12626 | 68
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | EMDE | LARUSSEL 161KV | 95.901 | -0.00623 | -0.12618 | 68
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | OEC 345KV | 1160 | -0.00609 | -0.12632 | 68
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00584 | -0.12657 | 68
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | EMDE | ASBURY 161KV | 189 | -0.00809 | -0.12432 | 69
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.00785 | -0.12456 | 69
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | EMDE | STATE LINE 161KV | 440.6939 | -0.00743 | -0.12498 | 69
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SOONER 345KV | 537 | -0.01032 | -0.12209 | 70
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | SOONER 138KV | 535 | -0.01263 | -0.11978 | 72
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01427 | -0.11814 | 73
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | -0.01842 | -0.11399 | 75
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02258 | -0.10983 | 78
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.11002 | 78
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.10827 | 79
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.10827 | 79
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.10892 | 79
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.10746 | 80
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.10704 | 80
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.10696 | 80
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.10717 | 80
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02107 | -0.10584 | 81
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.02841 | -0.104 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.10423 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.01946 | -0.10423 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.01916 | -0.10393 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.01993 | -0.1047 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.10479 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.10444 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.1044 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.10398 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.10393 | 82
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01795 | -0.10272 | 83
WERE | CITY OF WELLINGTON 69KV | 38.625 | -0.13241 | WERE | ELK RIVER 345KV | 150 | -0.03024 | -0.10217 | 84
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01593 | -0.1007 | 85
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.01552 | -0.10029 | 85
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01554 | -0.10031 | 85
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01593 | -0.1007 | 85
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | OU SPIRIT 138KV | 102 | 0.01392 | -0.09869 | 87
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01392 | -0.09869 | 87
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | CENT 21 34.500 138KV | 120 | 0.01236 | -0.09713 | 88
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01271 | -0.09748 | 88
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01288 | -0.09765 | 88
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01209 | -0.09686 | 88
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01267 | -0.09744 | 88
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01242 | -0.09719 | 88
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01135 | -0.09612 | 89
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01085 | -0.09562 | 90
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | ENERGY CENTER 115KV | 77 | 0.0106 | -0.09537 | 90
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.0106 | -0.09537 | 90
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.0105 | -0.09527 | 90
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | PLATTE 115KV | 90 | 0.01034 | -0.09511 | 90
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.01075 | -0.09552 | 90
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01079 | -0.09556 | 90
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | AINSWORTH WIND 34KV | 60 | 0.00947 | -0.09424 | 91
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00894 | -0.09371 | 91
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.00966 | -0.09443 | 91
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00894 | -0.09371 | 91
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00894 | -0.09371 | 91
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00829 | -0.09306 | 92
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00793 | -0.0927 | 92
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00836 | -0.09313 | 92
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00857 | -0.09334 | 92
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00836 | -0.09313 | 92
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.0073 | -0.09207 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00746 | -0.09223 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00746 | -0.09223 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00744 | -0.09221 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | FREMONT 8 69KV | 88.21 | 0.00761 | -0.09238 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | IATAN 345KV | 1606 | 0.00719 | -0.09196 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00728 | -0.09205 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00728 | -0.09205 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00724 | -0.09201 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00724 | -0.09201 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00726 | -0.09203 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00726 | -0.09203 | 93
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00638 | -0.09115 | 94
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00675 | -0.09152 | 94
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00545 | -0.09022 | 95
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00496 | -0.08973 | 95
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KACY | NEARMAN 20KV | 235 | 0.00533 | -0.0901 | 95
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KACY | QUINDARO 161KV | 117.9024 | 0.00531 | -0.09008 | 95
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KACY | QUINDARO 69KV | 36.1403 | 0.0053 | -0.09007 | 95
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00475 | -0.08952 | 96
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00476 | -0.08953 | 96
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00476 | -0.08953 | 96
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00476 | -0.08953 | 96
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00476 | -0.08953 | 96
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | SIBLEY 161KV | 354 | 0.00441 | -0.08918 | 96
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | SIBLEY 69KV | 97 | 0.0045 | -0.08927 | 96
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | ARIES 161KV | 402 | 0.00345 | -0.08822 | 97
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | MONTROSE 161KV | 335 | 0.00243 | -0.0872 | 98
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00236 | -0.08713 | 98
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00217 | -0.08694 | 99
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | COMANCHE 138KV | 164.7 | 0.00129 | -0.08606 | 100
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | COMANCHE 69KV | 64 | 0.00119 | -0.08596 | 100
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | GRADY CO SUB 345KV | 99 | 0.0005 | -0.08527 | 100
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | MNCWND31 34.500 345KV | 100 | 0.0005 | -0.08527 | 100
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00096 | -0.08573 | 100
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | CANDN12 34.500 345KV | 298.2 | -9e-05 | -0.08468 | 101
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.08385 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.08385 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.08385 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.08383 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00094 | -0.08383 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.08385 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00092 | -0.08385 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00105 | -0.08372 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | ARSENAL HILL 138KV | 509 | -0.00118 | -0.08359 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00048 | -0.08429 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00089 | -0.08388 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | MUSTANG 138KV | 221 | -0.00092 | -0.08385 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00082 | -0.08395 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | SMITH COGEN 138KV | 107 | -0.00097 | -0.0838 | 102
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | EASTMAN 138KV | 150 | -0.00121 | -0.08356 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.0019 | -0.08287 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | KNOXLEE 138KV | 254.3647 | -0.0012 | -0.08357 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00121 | -0.08356 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | SEMINOLE 138KV | 149.9142 | -0.00168 | -0.08309 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | SEMINOLE 345KV | 433.186 | -0.0017 | -0.08307 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | TURK 138KV | 643 | -0.00132 | -0.08345 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | WELSH 345KV | 1056 | -0.00125 | -0.08352 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | WILKES 138KV | 299.8593 | -0.00123 | -0.08354 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | WILKES 345KV | 348 | -0.00123 | -0.08354 | 103
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00201 | -0.08276 | 104
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.0021 | -0.08267 | 104
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00232 | -0.08245 | 104
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | REDBUD 345KV | 1224 | -0.00204 | -0.08273 | 104
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.002 | -0.08277 | 104
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | AES 161KV | 320 | -0.00327 | -0.0815 | 105
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.00458 | -0.08019 | 107
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00532 | -0.07945 | 108
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | COGENTRIX 345KV | 830 | -0.00569 | -0.07908 | 108
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | FLINT CREEK 161KV | 528 | -0.00615 | -0.07862 | 109
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | EMDE | LARUSSEL 161KV | 95.901 | -0.00623 | -0.07854 | 109
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | OEC 345KV | 1160 | -0.00609 | -0.07868 | 109
WERE | CITY OF WINFIELD 69KV | 36.8 | -0.08477 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00584 | -0.07893 | 109
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.03298 | 260
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.03268 | 262
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.03188 | 269
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.03158 | 271
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.03148 | 272
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.03123 | 274
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.03123 | 274
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.03122 | 274
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.03132 | 274
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.03109 | 276
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.03093 | 277
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.03093 | 277
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.03038 | 282
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.03042 | 282
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.03022 | 283
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.03013 | 284
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.03012 | 284
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.03012 | 284
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02999 | 286
EMDE | RIVERTON 161KV | 175 | -0.00773 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.03 | 286
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.02992 | 286
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02983 | 287
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.02983 | 287
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.02973 | 288
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02973 | 288
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.0297 | 288
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02219 | -0.02962 | 289
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.02957 | 290
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02957 | 290
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.02947 | 291
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02947 | 291
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.02934 | 292
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02934 | 292
AEPW | WELEETKA 138KV | 152.4 | -0.00379 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02904 | 295
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02892 | 296
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02107 | -0.0288 | 297
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02873 | 298
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02876 | 298
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.02863 | 299
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02866 | 299
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02853 | 300
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.0285 | 301
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.02847 | 301
AEPW | FITZHUGH 161KV | 168 | -0.00312 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02837 | 302
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.02837 | 302
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02834 | 302
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.0224 | -0.02824 | 303
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02824 | 303
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.02808 | 305
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02808 | 305
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02811 | 305
AEPW | WELEETKA 138KV | 152.4 | -0.00379 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02794 | 307
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.02775 | 309
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00232 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02757 | 311
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.02745 | 312
KCPL | LACYGNE UNIT 345KV | 148.6 | -0.0021 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02735 | 313
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.0274 | 313
EMDE | RIVERTON 161KV | 175 | -0.00773 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.02736 | 313
AEPW | FITZHUGH 161KV | 168 | -0.00312 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02727 | 314
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02727 | 314
AEPW | WELEETKA 138KV | 152.4 | -0.00379 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.02729 | 314
AEPW | WELEETKA 138KV | 152.4 | -0.00379 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02729 | 314
OKGE | HORSESHOE LAKE 138KV | 615 | -0.0019 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02715 | 316
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.0271 | 316
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | SUNC | RUBART 2 13.800 115KV | 108 | 0.01963 | -0.02706 | 317
EMDE | RIVERTON 161KV | 175 | -0.00773 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.02694 | 318
OKGE | SEMINOLE 138KV | 371.0858 | -0.00168 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02693 | 318
OKGE | SEMINOLE 345KV | 618.814 | -0.0017 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02695 | 318
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02685 | 319
EMDE | RIVERTON 161KV | 175 | -0.00773 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.02689 | 319
AEPW | FITZHUGH 161KV | 168 | -0.00312 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.0235 | -0.02662 | 322
AEPW | FITZHUGH 161KV | 168 | -0.00312 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02662 | 322
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.02664 | 322
EMDE | STATE LINE 161KV | 153.3061 | -0.00743 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.02659 | 322
AEPW | FULTON 115KV | 153.5 | -0.00129 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02654 | 323
AEPW | WELSH 345KV | 598.3 | -0.00125 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.0265 | 323
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00118 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02643 | 324
AEPW | EASTMAN 138KV | 335.01 | -0.00121 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02646 | 324
AEPW | KNOXLEE 138KV | 229.3353 | -0.0012 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02645 | 324
AEPW | LEBROCK 345KV | 559 | -0.0012 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02645 | 324
AEPW | LIEBERMAN 138KV | 251.4 | -0.00119 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02644 | 324
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00232 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02647 | 324
AEPW | WELEETKA 138KV | 152.4 | -0.00379 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02648 | 324
AEPW | WILKES 138KV | 254.3407 | -0.00123 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02648 | 324
KCPL | LACYGNE UNIT 345KV | 148.6 | -0.0021 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02625 | 326
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.02625 | 326
OKGE | MUSTANG 138KV | 169 | -0.00092 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02617 | 327
OKGE | MUSTANG 69KV | 110 | -0.00094 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02619 | 327
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.02609 | 328
OKGE | HORSESHOE LAKE 138KV | 615 | -0.0019 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02605 | 329
AEPW | WELEETKA 138KV | 152.4 | -0.00379 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02606 | 329
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.02599 | 330
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.0259 | 331
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.02586 | 331
OKGE | SEMINOLE 345KV | 618.814 | -0.0017 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02585 | 331
AEPW | FITZHUGH 161KV | 168 | -0.00312 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02581 | 332
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00232 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02582 | 332
OKGE | SEMINOLE 138KV | 371.0858 | -0.00168 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02583 | 332
OKGE | GRNTWDG2 0.6900 34KV | 148 | -0.00048 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02525 | -0.02573 | 333
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.02574 | 333
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.02564 | 334
KCPL | LACYGNE UNIT 345KV | 148.6 | -0.0021 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.0256 | 335
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.02551 | 336
AEPW | FITZHUGH 161KV | 168 | -0.00312 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02539 | 337
AEPW | FULTON 115KV | 153.5 | -0.00129 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02544 | 337
OKGE | HORSESHOE LAKE 138KV | 615 | -0.0019 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.0254 | 337
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.02544 | 337
EMDE | LARUSSEL 161KV | 166.099 | -0.00623 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.02539 | 337
AEPW | WELSH 345KV | 598.3 | -0.00125 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.0254 | 337
AEPW | ARSENAL HILL 69KV | 114.7 | -0.00118 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02533 | 338
AEPW | EASTMAN 138KV | 335.01 | -0.00121 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02536 | 338
AEPW | KNOXLEE 138KV | 229.3353 | -0.0012 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02535 | 338
AEPW | LEBROCK 345KV | 559 | -0.0012 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02535 | 338
AEPW | LIEBERMAN 138KV | 251.4 | -0.00119 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02534 | 338
AEPW | WILKES 138KV | 254.3407 | -0.00123 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02538 | 338
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.02528 | 339
OKGE | SEMINOLE 138KV | 371.0858 | -0.00168 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02518 | 340
OKGE | SEMINOLE 345KV | 618.814 | -0.0017 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.0252 | 340
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.02518 | 340
AEPW | TULSA POWER STATION 138KV | 340.3 | -0.00607 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.02523 | 340
AEPW | TONTITOWN 161KV | 304.5 | -0.00597 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.02513 | 341
OKGE | MUSTANG 138KV | 169 | -0.00092 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02507 | 342
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.01921 | -0.02505 | 342
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00232 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02501 | 343
AEPW | RIVERSIDE STATION 138KV | 185.5999 | -0.00584 | MIDW | SMOKEY HILLS 34KV | 191 | 0.01916 | -0.025 | 343
AEPW | FULTON 115KV | 153.5 | -0.00129 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02479 | 346
KCPL | LACYGNE UNIT 345KV | 148.6 | -0.0021 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02479 | 346
AEPW | WELSH 345KV | 598.3 | -0.00125 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02475 | 346
AEPW | WILKES 138KV | 254.3407 | -0.00123 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02473 | 346
AEPW | EASTMAN 138KV | 335.01 | -0.00121 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02471 | 347
AEPW | KNOXLEE 138KV | 229.3353 | -0.0012 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.0247 | 347
AEPW | LEBROCK 345KV | 559 | -0.0012 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.0247 | 347
AEPW | LIEBERMAN 138KV | 251.4 | -0.00119 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02469 | 347
OKGE | GRNTWDG2 0.6900 34KV | 148 | -0.00048 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02415 | -0.02463 | 348
OKGE | HORSESHOE LAKE 138KV | 615 | -0.0019 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02459 | 348
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | SUNC | HOLCOMB 115KV | 360 | 0.02002 | -0.0246 | 348
AEPW | NORTHEASTERN STATION 345KV | 532.8 | -0.00232 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02459 | 348
OKGE | MUSTANG 138KV | 169 | -0.00092 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.0235 | -0.02442 | 351
OKGE | SEMINOLE 345KV | 618.814 | -0.0017 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02439 | 351
KCPL | LACYGNE UNIT 345KV | 148.6 | -0.0021 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02227 | -0.02437 | 352
OKGE | SEMINOLE 138KV | 371.0858 | -0.00168 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02269 | -0.02437 | 352
OKGE | MUSKOGEE 345KV | 132.5 | -0.00458 | SUNC | MRWYP16 230KV | 196 | 0.01967 | -0.02425 | 353
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1
Limiting Facility: | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1
Direction: | FROM->TO
Line Outage: | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1
Flowgate: | 2017AG1AFS11T10255518SP
Date Redispatch Needed: | Starting 2018 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2018 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
84877548 | 23.8 | 36.2
84877556 | 12.4 | 36.2
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.02514 | -0.49296 | 73
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02701 | -0.49483 | 73
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.02513 | -0.49295 | 73
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02583 | -0.49365 | 73
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.02514 | -0.49296 | 73
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02701 | -0.49483 | 73
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.02513 | -0.49295 | 73
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02583 | -0.49365 | 73
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01919 | -0.48701 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.02082 | -0.48864 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.02082 | -0.48864 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02427 | -0.49209 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.02049 | -0.48831 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02382 | -0.49164 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02373 | -0.49155 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02253 | -0.49035 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.02131 | -0.48913 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | HOLCOMB 115KV | 360 | 0.02141 | -0.48923 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | MRWYP16 230KV | 196 | 0.02104 | -0.48886 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | RUBART 2 13.800 115KV | 108 | 0.02099 | -0.48881 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.02054 | -0.48836 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | MIDW | SMOKEY HILLS 34KV | 191 | 0.02049 | -0.48831 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.02395 | -0.49177 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01919 | -0.48701 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | MIDW | BUCKE_WTG 0.6900 34KV | 50.1 | 0.02082 | -0.48864 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | MIDW | BUCKW_WTG 0.6900 34KV | 50.1 | 0.02082 | -0.48864 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02427 | -0.49209 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.02049 | -0.48831 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02382 | -0.49164 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02373 | -0.49155 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02253 | -0.49035 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | GARDEN CITY 115KV | 42.9475 | 0.02131 | -0.48913 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | HOLCOMB 115KV | 360 | 0.02141 | -0.48923 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | MRWYP16 230KV | 196 | 0.02104 | -0.48886 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | RUBART 2 13.800 115KV | 108 | 0.02099 | -0.48881 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.02054 | -0.48836 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | MIDW | SMOKEY HILLS 34KV | 191 | 0.02049 | -0.48831 | 74
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.02395 | -0.49177 | 74
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01703 | -0.48485 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | CENT 21 34.500 138KV | 120 | 0.01322 | -0.48104 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01359 | -0.48141 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01377 | -0.48159 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.0166 | -0.48442 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01662 | -0.48444 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01214 | -0.47996 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01293 | -0.48075 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | OU SPIRIT 138KV | 102 | 0.01489 | -0.48271 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01703 | -0.48485 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01355 | -0.48137 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01328 | -0.4811 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01489 | -0.48271 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01703 | -0.48485 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | CENT 21 34.500 138KV | 120 | 0.01322 | -0.48104 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01359 | -0.48141 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01377 | -0.48159 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.0166 | -0.48442 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01662 | -0.48444 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01214 | -0.47996 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | MARSHGEN1 0.6900 34KV | 50 | 0.01293 | -0.48075 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | OU SPIRIT 138KV | 102 | 0.01489 | -0.48271 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01703 | -0.48485 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01355 | -0.48137 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01328 | -0.4811 | 75
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01489 | -0.48271 | 75
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | AINSWORTH WIND 34KV | 60 | 0.01013 | -0.47795 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01161 | -0.47943 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.00781 | -0.47563 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00886 | -0.47668 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00797 | -0.47579 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00956 | -0.47738 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00848 | -0.4763 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00797 | -0.47579 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | ENERGY CENTER 115KV | 77 | 0.01134 | -0.47916 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.01134 | -0.47916 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00796 | -0.47578 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | FREMONT 8 69KV | 88.21 | 0.00814 | -0.47596 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00682 | -0.47464 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00583 | -0.47365 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | IATAN 345KV | 1606 | 0.00769 | -0.47551 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00722 | -0.47504 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.01123 | -0.47905 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00779 | -0.47561 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00779 | -0.47561 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00774 | -0.47556 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00774 | -0.47556 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00895 | -0.47677 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | PLATTE 115KV | 90 | 0.01106 | -0.47888 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.0115 | -0.47932 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00777 | -0.47559 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00777 | -0.47559 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.01033 | -0.47815 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00916 | -0.47698 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00956 | -0.47738 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00956 | -0.47738 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00895 | -0.47677 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01154 | -0.47936 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | AINSWORTH WIND 34KV | 60 | 0.01013 | -0.47795 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01161 | -0.47943 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.00781 | -0.47563 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00886 | -0.47668 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | CROFTON HILLS WIND 34KV | 42.3 | 0.00797 | -0.47579 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00956 | -0.47738 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00848 | -0.4763 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00797 | -0.47579 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | ENERGY CENTER 115KV | 77 | 0.01134 | -0.47916 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.01134 | -0.47916 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00796 | -0.47578 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | FREMONT 8 69KV | 88.21 | 0.00814 | -0.47596 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00682 | -0.47464 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00583 | -0.47365 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | IATAN 345KV | 1606 | 0.00769 | -0.47551 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00722 | -0.47504 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.01123 | -0.47905 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00779 | -0.47561 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00779 | -0.47561 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00774 | -0.47556 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00774 | -0.47556 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00895 | -0.47677 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | PLATTE 115KV | 90 | 0.01106 | -0.47888 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.0115 | -0.47932 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00777 | -0.47559 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00777 | -0.47559 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.01033 | -0.47815 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00916 | -0.47698 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00956 | -0.47738 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00956 | -0.47738 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OPPD | TPWPBG1W 0.6900 34KV | 40.5 | 0.00895 | -0.47677 | 76
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01154 | -0.47936 | 76
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | ARIES 161KV | 402 | 0.00369 | -0.47151 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00508 | -0.4729 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | CANDN12 34.500 345KV | 298.2 | -0.0001 | -0.46772 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | COMANCHE 138KV | 164.7 | 0.00138 | -0.4692 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | COMANCHE 69KV | 64 | 0.00127 | -0.46909 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | GRADY CO SUB 345KV | 99 | 0.00053 | -0.46835 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00531 | -0.47313 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | MNCWND31 34.500 345KV | 100 | 0.00053 | -0.46835 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | MONTROSE 161KV | 335 | 0.00259 | -0.47041 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KACY | NEARMAN 20KV | 235 | 0.0057 | -0.47352 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KACY | QUINDARO 161KV | 117.9024 | 0.00568 | -0.4735 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KACY | QUINDARO 69KV | 36.1403 | 0.00567 | -0.47349 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00252 | -0.47034 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | SIBLEY 161KV | 354 | 0.00472 | -0.47254 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | SIBLEY 69KV | 97 | 0.00481 | -0.47263 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | SOUTH OTTAWA 161KV | 26.7 | 0.00289 | -0.47071 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00102 | -0.46884 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00232 | -0.47014 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | ARIES 161KV | 402 | 0.00369 | -0.47151 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00508 | -0.4729 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | CANDN12 34.500 345KV | 298.2 | -0.0001 | -0.46772 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | COMANCHE 138KV | 164.7 | 0.00138 | -0.4692 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | COMANCHE 69KV | 64 | 0.00127 | -0.46909 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00509 | -0.47291 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | GRADY CO SUB 345KV | 99 | 0.00053 | -0.46835 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00531 | -0.47313 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | MNCWND31 34.500 345KV | 100 | 0.00053 | -0.46835 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | MONTROSE 161KV | 335 | 0.00259 | -0.47041 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KACY | NEARMAN 20KV | 235 | 0.0057 | -0.47352 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KACY | QUINDARO 161KV | 117.9024 | 0.00568 | -0.4735 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KACY | QUINDARO 69KV | 36.1403 | 0.00567 | -0.47349 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00252 | -0.47034 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | SIBLEY 161KV | 354 | 0.00472 | -0.47254 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | SIBLEY 69KV | 97 | 0.00481 | -0.47263 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | SOUTH OTTAWA 161KV | 26.7 | 0.00289 | -0.47071 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00102 | -0.46884 | 77
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00232 | -0.47014 | 77
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00101 | -0.46681 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00101 | -0.46681 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | AES 161KV | 320 | -0.00349 | -0.46433 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00112 | -0.4667 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | ARSENAL HILL 138KV | 509 | -0.00126 | -0.46656 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00568 | -0.46214 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00215 | -0.46567 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | COGENTRIX 345KV | 830 | -0.00609 | -0.46173 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | EASTMAN 138KV | 150 | -0.00129 | -0.46653 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00051 | -0.46731 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.00203 | -0.46579 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | KNOXLEE 138KV | 254.3647 | -0.00129 | -0.46653 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.00225 | -0.46557 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00095 | -0.46687 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.0049 | -0.46292 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | MUSTANG 138KV | 221 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00248 | -0.46534 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00087 | -0.46695 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00129 | -0.46653 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | REDBUD 345KV | 1224 | -0.00218 | -0.46564 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00624 | -0.46158 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SEMINOLE 138KV | 149.9142 | -0.0018 | -0.46602 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SEMINOLE 345KV | 433.186 | -0.00181 | -0.46601 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SMITH COGEN 138KV | 107 | -0.00103 | -0.46679 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.00213 | -0.46569 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | TURK 138KV | 643 | -0.00141 | -0.46641 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | WELSH 345KV | 1056 | -0.00134 | -0.46648 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | WILKES 138KV | 299.8593 | -0.00132 | -0.4665 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | WILKES 345KV | 348 | -0.00131 | -0.46651 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00101 | -0.46681 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00101 | -0.46681 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | AES 161KV | 320 | -0.00349 | -0.46433 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00112 | -0.4667 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | ARSENAL HILL 138KV | 509 | -0.00126 | -0.46656 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00568 | -0.46214 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00215 | -0.46567 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | COGENTRIX 345KV | 830 | -0.00609 | -0.46173 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | EASTMAN 138KV | 150 | -0.00129 | -0.46653 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00051 | -0.46731 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.00203 | -0.46579 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | KNOXLEE 138KV | 254.3647 | -0.00129 | -0.46653 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.00225 | -0.46557 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00095 | -0.46687 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.0049 | -0.46292 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | MUSTANG 138KV | 221 | -0.00099 | -0.46683 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00248 | -0.46534 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00087 | -0.46695 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00129 | -0.46653 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | REDBUD 345KV | 1224 | -0.00218 | -0.46564 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00624 | -0.46158 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SEMINOLE 138KV | 149.9142 | -0.0018 | -0.46602 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SEMINOLE 345KV | 433.186 | -0.00181 | -0.46601 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SMITH COGEN 138KV | 107 | -0.00103 | -0.46679 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.00213 | -0.46569 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | TURK 138KV | 643 | -0.00141 | -0.46641 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | WELSH 345KV | 1056 | -0.00134 | -0.46648 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | WILKES 138KV | 299.8593 | -0.00132 | -0.4665 | 78
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | WILKES 345KV | 348 | -0.00131 | -0.46651 | 78
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | EMDE | ASBURY 161KV | 189 | -0.00865 | -0.45917 | 79
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | FLINT CREEK 161KV | 528 | -0.00658 | -0.46124 | 79
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | EMDE | LARUSSEL 161KV | 95.901 | -0.00667 | -0.46115 | 79
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.0084 | -0.45942 | 79
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | AEPW | OEC 345KV | 1160 | -0.00651 | -0.46131 | 79
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SOONER 345KV | 537 | -0.01103 | -0.45679 | 79
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | EMDE | STATE LINE 161KV | 440.6939 | -0.00795 | -0.45987 | 79
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | EMDE | ASBURY 161KV | 189 | -0.00865 | -0.45917 | 79
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | FLINT CREEK 161KV | 528 | -0.00658 | -0.46124 | 79
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | EMDE | LARUSSEL 161KV | 95.901 | -0.00667 | -0.46115 | 79
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.0084 | -0.45942 | 79
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | AEPW | OEC 345KV | 1160 | -0.00651 | -0.46131 | 79
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SOONER 345KV | 537 | -0.01103 | -0.45679 | 79
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | EMDE | STATE LINE 161KV | 440.6939 | -0.00795 | -0.45987 | 79
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | SOONER 138KV | 535 | -0.01351 | -0.45431 | 80
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01526 | -0.45256 | 80
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | SOONER 138KV | 535 | -0.01351 | -0.45431 | 80
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01526 | -0.45256 | 80
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | -0.0197 | -0.44812 | 81
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | BLKWLWD1 34.500 69KV | 59.8 | -0.0197 | -0.44812 | 81
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02415 | -0.44367 | 82
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02415 | -0.44367 | 82
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.03038 | -0.43744 | 83
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | ELK RIVER 345KV | 150 | -0.03233 | -0.43549 | 83
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.03038 | -0.43744 | 83
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | ELK RIVER 345KV | 150 | -0.03233 | -0.43549 | 83
WERE | EVANS ENERGY CENTER 138KV | 696 | -0.46782 | WERE | SLATEGEN1 0.6900 34KV | 150 | -0.0766 | -0.39122 | 93
WERE | EVANS ENERGY CENTER 4KV | 148 | -0.46782 | WERE | SLATEGEN1 0.6900 34KV | 150 | -0.0766 | -0.39122 | 93
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.02701 | -0.24578 | 147
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | SPEARVILLE 230KV | 247.6 | 0.02583 | -0.2446 | 148
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.02427 | -0.24304 | 149
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | EMPORIA ENERGY CENTER 345KV | 173.3818 | 0.02382 | -0.24259 | 149
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | ENSNGW 1 34.500 115KV | 99 | 0.02373 | -0.2425 | 149
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.02514 | -0.24391 | 149
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | JUDSON LARGE 115KV | 131.7433 | 0.02513 | -0.2439 | 149
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.02395 | -0.24272 | 149
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | FLAT RIDGE WIND 138KV | 100 | 0.02253 | -0.2413 | 150
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | COMMANCHE COUNTY 115KV | 99 | 0.02049 | -0.23926 | 151
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | HOLCOMB 115KV | 360 | 0.02141 | -0.24018 | 151
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | MRWYP16 230KV | 196 | 0.02104 | -0.23981 | 151
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | RUBART 2 13.800 115KV | 108 | 0.02099 | -0.23976 | 151
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | MIDW | SHAYS_GEN 0.6900 34KV | 198.69 | 0.02054 | -0.23931 | 151
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | MIDW | SMOKEY HILLS 34KV | 191 | 0.02049 | -0.23926 | 151
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | 0.01919 | -0.23796 | 152
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | BALKOWG2 0.6900 34KV | 200 | 0.01703 | -0.2358 | 154
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.0166 | -0.23537 | 154
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.01662 | -0.23539 | 154
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | PALDRW21 34.500 345KV | 249 | 0.01703 | -0.2358 | 154
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | OU SPIRIT 138KV | 102 | 0.01489 | -0.23366 | 155
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | WOODWARD CO SUB 2 138KV | 151.8 | 0.01489 | -0.23366 | 155
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | CENT 21 34.500 138KV | 120 | 0.01322 | -0.23199 | 156
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | GERALD GENTLEMAN STATION UNIT 1 230KV | 622.425 | 0.01359 | -0.23236 | 156
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | GERALD GENTLEMAN STATION UNIT 2 345KV | 626 | 0.01377 | -0.23254 | 156
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | MIDW | PRWINDG1 0.6900 34KV | 201 | 0.01355 | -0.23232 | 156
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | TECUMSEH ENERGY CENTER 115KV | 70 | 0.01328 | -0.23205 | 156
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | BRKNBW.GEN2W0.6900 34KV | 154.8 | 0.01161 | -0.23038 | 157
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | ENERGY CENTER 115KV | 77 | 0.01134 | -0.23011 | 157
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | ENERGY CENTER 2 115KV | 220 | 0.01134 | -0.23011 | 157
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | LAWRENCE ENERGY CENTER 230KV | 372.8263 | 0.01214 | -0.23091 | 157
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | S.FLATS.GENW0.6900 34KV | 74.8 | 0.0115 | -0.23027 | 157
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | WEBSTER CO SUB 34KV | 82 | 0.01154 | -0.23031 | 157
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | AINSWORTH WIND 34KV | 60 | 0.01013 | -0.2289 | 158
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | LAWRENCE ENERGY CENTER 115KV | 105 | 0.01123 | -0.23 | 158
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | PLATTE 115KV | 90 | 0.01106 | -0.22983 | 158
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | SCOTT CO SUB 2 34KV | 60 | 0.01033 | -0.2291 | 158
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | COLUMCOGENERATION 115KV | 70 | 0.00886 | -0.22763 | 159
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | CRSRDW21 34.500 345KV | 197.8 | 0.00956 | -0.22833 | 159
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00848 | -0.22725 | 159
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | PETERSBURG WIND 34KV | 80 | 0.00895 | -0.22772 | 159
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | SHELDON STATION UNIT 2 115KV | 148.1065 | 0.00916 | -0.22793 | 159
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SILNGW21 34.500 345KV | 100 | 0.00956 | -0.22833 | 159
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SLINGW11 34.500 345KV | 199 | 0.00956 | -0.22833 | 159
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | CASS COUNTY 2 345KV | 251.558 | 0.00781 | -0.22658 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | NPPD | ELKHORN RIDGE WIND 34KV | 81 | 0.00797 | -0.22674 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00796 | -0.22673 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | FREMONT 8 69KV | 88.21 | 0.00814 | -0.22691 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | IATAN 345KV | 1606 | 0.00769 | -0.22646 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | LAKERD#4 13.800 161KV | 96 | 0.00722 | -0.22599 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | NEBRASKA CITY 1 4KV | 655.9 | 0.00779 | -0.22656 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | NEBRASKA CITY 2 345KV | 676 | 0.00779 | -0.22656 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | NORTH OMAHA 4 2KV | 96.9 | 0.00774 | -0.22651 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | NORTH OMAHA 5 4KV | 168.4908 | 0.00774 | -0.22651 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | SARPY COUNTY 3 4KV | 107.7 | 0.00777 | -0.22654 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OPPD | SARPY COUNTY 5 161KV | 97.1 | 0.00777 | -0.22654 | 160
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | ATCHISON20.6900 34KV | 300 | 0.00682 | -0.22559 | 161
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | DEKALB CO_3 0.6900 34KV | 374 | 0.00583 | -0.2246 | 161
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KACY | NEARMAN 20KV | 235 | 0.0057 | -0.22447 | 161
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KACY | QUINDARO 161KV | 117.9024 | 0.00568 | -0.22445 | 161
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00508 | -0.22385 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | FR2E1WF1 0.6900 34KV | 113 | 0.00509 | -0.22386 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | FR2E2WF1 0.6900 34KV | 113 | 0.00509 | -0.22386 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | FR2W1WF1 0.6900 34KV | 117 | 0.00509 | -0.22386 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | FR2W2WF1 0.6900 34KV | 117 | 0.00509 | -0.22386 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | HAWTHORN 161KV | 675.2889 | 0.00531 | -0.22408 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | SIBLEY 161KV | 354 | 0.00472 | -0.22349 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | SIBLEY 69KV | 97 | 0.00481 | -0.22358 | 162
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | ARIES 161KV | 402 | 0.00369 | -0.22246 | 163
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | MONTROSE 161KV | 335 | 0.00259 | -0.22136 | 164
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00252 | -0.22129 | 164
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00232 | -0.22109 | 164
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | COMANCHE 138KV | 164.7 | 0.00138 | -0.22015 | 165
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | COMANCHE 69KV | 64 | 0.00127 | -0.22004 | 165
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | GRADY CO SUB 345KV | 99 | 0.00053 | -0.2193 | 165
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | MNCWND31 34.500 345KV | 100 | 0.00053 | -0.2193 | 165
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | SOUTHWESTERN STATION 138KV | 311 | 0.00102 | -0.21979 | 165
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | 10OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.21778 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | 11OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.21778 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | 12OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.21778 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | 6OKLAHOMACITY13.800 69KV | 57 | -0.00101 | -0.21776 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | 7OKLAHOMACITY13.800 69KV | 57 | -0.00101 | -0.21776 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | 8OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.21778 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | 9OKLAHOMACITY13.800 138KV | 57 | -0.00099 | -0.21778 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | ARBWND11 34.500 138KV | 100 | -0.00112 | -0.21765 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | CANDN12 34.500 345KV | 298.2 | -0.0001 | -0.21867 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | GRNTWDG2 0.6900 34KV | 152 | -0.00051 | -0.21826 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | MCCLAIN 138KV | 481.5977 | -0.00095 | -0.21782 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | MUSTANG 138KV | 221 | -0.00099 | -0.21778 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | ORIGIN21 34.500 138KV | 150 | -0.00087 | -0.2179 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SMITH COGEN 138KV | 107 | -0.00103 | -0.21774 | 166
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | ARSENAL HILL 138KV | 509 | -0.00126 | -0.21751 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | CHSHMVW1 34.500 345KV | 202 | -0.00215 | -0.21662 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | EASTMAN 138KV | 150 | -0.00129 | -0.21748 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | HORSESHOE LAKE 138KV | 294 | -0.00203 | -0.21674 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | KNOXLEE 138KV | 254.3647 | -0.00129 | -0.21748 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | KCPL | LACYGNE UNIT 345KV | 1380 | -0.00225 | -0.21652 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00248 | -0.21629 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00129 | -0.21748 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | REDBUD 345KV | 1224 | -0.00218 | -0.21659 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SEMINOLE 138KV | 149.9142 | -0.0018 | -0.21697 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SEMINOLE 345KV | 433.186 | -0.00181 | -0.21696 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | -0.00213 | -0.21664 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | TURK 138KV | 643 | -0.00141 | -0.21736 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | WELSH 345KV | 1056 | -0.00134 | -0.21743 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | WILKES 138KV | 299.8593 | -0.00132 | -0.21745 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | WILKES 345KV | 348 | -0.00131 | -0.21746 | 167
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | AES 161KV | 320 | -0.00349 | -0.21528 | 168
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | MUSKOGEE 345KV | 1542.5 | -0.0049 | -0.21387 | 169
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | BRKWND11 34.500 138KV | 70 | -0.00568 | -0.21309 | 170
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | COGENTRIX 345KV | 830 | -0.00609 | -0.21268 | 170
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | -0.00624 | -0.21253 | 170
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | FLINT CREEK 161KV | 528 | -0.00658 | -0.21219 | 171
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | EMDE | LARUSSEL 161KV | 95.901 | -0.00667 | -0.2121 | 171
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | OEC 345KV | 1160 | -0.00651 | -0.21226 | 171
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | EMDE | ASBURY 161KV | 189 | -0.00865 | -0.21012 | 172
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | AEPW | NORTHEASTERN STATION 138KV | 841 | -0.0084 | -0.21037 | 172
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | EMDE | STATE LINE 161KV | 440.6939 | -0.00795 | -0.21082 | 172
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SOONER 345KV | 537 | -0.01103 | -0.20774 | 174
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | SOONER 138KV | 535 | -0.01351 | -0.20526 | 176
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | WAVERGEN1 0.6900 34KV | 190.5 | -0.01526 | -0.20351 | 178
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | OKGE | KAYWNDG2 0.6900 34KV | 280 | -0.02415 | -0.19462 | 186
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | CANEYWF1 0.6900 34KV | 199.8 | -0.03038 | -0.18839 | 192
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | ELK RIVER 345KV | 150 | -0.03233 | -0.18644 | 194
WERE | GILL ENERGY CENTER 138KV | 192 | -0.21877 | WERE | SLATEGEN1 0.6900 34KV | 150 | -0.0766 | -0.14217 | 255
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor

## Table7
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
52ND & DELAWARE WEST TAP - RIVERSIDE STATION 138KV CKT 1 | AEPM | AG1-2017-017 | 84904909 | 100% | 25000000
|  |  |  | Total: | 25000000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
52ND & DELAWARE WEST TAP - TULSA POWER STATION 138KV CKT 1 | AEPM | AG1-2017-017 | 84904909 | 100% | 16111111
|  |  |  | Total: | 16111111
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
ARSENAL HILL - RAINES 138KV CKT 1 | AEPM | AG1-2017-011 | 84903862 | 14.65% | 1464935.5259
ARSENAL HILL - RAINES 138KV CKT 1 | AEPM | AG1-2017-012 | 84904082 | 23.6% | 2359506.1489
ARSENAL HILL - RAINES 138KV CKT 1 | AEPM | AG1-2017-013 | 84904145 | 22.5% | 2249998.9916
ARSENAL HILL - RAINES 138KV CKT 1 | AEPM | AG1-2017-014 | 84904230 | 17.88% | 1787810.2199
ARSENAL HILL - RAINES 138KV CKT 1 | AEPM | AG1-2017-015 | 84904264 | 15.89% | 1588720.9645
ARSENAL HILL - RAINES 138KV CKT 1 | AEPM | AG1-2017-017 | 84904909 | 5.49% | 549028.1492
|  |  |  | Total: | 10000000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
DENISON - J6BOYER8 69.000 69KV CKT 1 | BEPM | AG1-2017-018 | 84885588 | 100% | 80000
|  |  |  | Total: | 80000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
EASTRUTH-CP7115.00 - MALLARD 115KV CKT 1 | BEPM | AG1-2017-018 | 84885588 | 75.84% | 379205.6359
EASTRUTH-CP7115.00 - MALLARD 115KV CKT 1 | BEPM | AG1-2017-020 | 84885635 | 24.16% | 120794.3641
|  |  |  | Total: | 500000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
GLASSES - RUSSETT 138KV CKT 1 | PEC | AG1-2017-043 | 84885681 | 100% | 8000000
|  |  |  | Total: | 8000000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
HUGO POWER PLANT - VALLIANT 138KV CKT 1 | AEPM | AG1-2017-011 | 84903862 | 13.07% | 19607.461
HUGO POWER PLANT - VALLIANT 138KV CKT 1 | AEPM | AG1-2017-013 | 84904145 | 24.02% | 36023.3496
HUGO POWER PLANT - VALLIANT 138KV CKT 1 | AEPM | AG1-2017-014 | 84904230 | 41.72% | 62579.1802
HUGO POWER PLANT - VALLIANT 138KV CKT 1 | AEPM | AG1-2017-015 | 84904264 | 14.46% | 21683.2011
HUGO POWER PLANT - VALLIANT 138KV CKT 1 | AEPM | AG1-2017-017 | 84904909 | 6.738% | 10106.808
|  |  |  | Total: | 150000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
MUSTANG - SW 5TH 138KV CKT 1 | AEPM | AG1-2017-017 | 84904909 | 78.06% | 390299.0913
MUSTANG - SW 5TH 138KV CKT 1 | PEC | AG1-2017-043 | 84885681 | 21.94% | 109700.9087
|  |  |  | Total: | 500000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
THOMAS TAP - WEATHERFORD 69KV CKT 1 | AEPM | AG1-2017-017 | 84904909 | 100% | 2000000
|  |  |  | Total: | 2000000
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | KMEA | AG1-2017-028 | 84885203 | 0.3487% | 20920.0291
WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | WRGS | AG1-2017-048 | 84877548 | 65.01% | 3900515.0524
WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | WRGS | AG1-2017-049 | 84877556 | 33.8% | 2028267.8272
WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | KMEA | AG1-2017-027 | 84884608 | 0.8383% | 50297.0913
|  |  |  | Total: | 6000000