## Executive Summary
Executive Summary: DISIS-2017-001-2 Restudy of Stability and Short Circuit Analysis
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2017. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2017-001-2 includes study requests in the following cluster group: 04 - Northwest Kansas. Please note that Group 16 results from DISIS-2017-001-2 will be updated at a later date. These groups were included for informational purposes only: 01 - Woodward, 02 - Hitchland, 03 - Spearville, 06 - South Texas Panhandle/New Mexico, 07 - Southwestern Oklahoma, 08 - North Oklahoma/South Central Kansas, 09 - Nebraska, 10 - Southeast Oklahoma/Northeast Texas, 12 - Northwest Arkansas, 13 - Northeast Kansas/Northwest Missouri, 14 - South Central Oklahoma, and 15 - Eastern South Dakota, 16 - Western North Dakota and 17 - Western South Dakota)
DISIS Manual Version 1.4
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
5633 MW
The minimum cost, including both power flow and stability, of interconnecting all requests included in this DISIS is estimated at:
374756319.5
Models Used in Study
2018 MDWG
Winter: 2019
Summer: 2021, 2028
Light: 2021
By: SPP Generator Interconnection Department
Published: June 16, 2022

## Revision History
Date | Author | Change Description
2021-04-07 | SPP | Posting of DISIS-2017-001 Phase 2 Results
2021-04-27 | SPP | Phase Two Report Workbook has been updated for dynamics model corrections.
2021-05-05 | SPP | Corrected LOIS & MW Amounts
2021-10-08 | SPP | Posting of DISIS-2017-001-1 Restudy Draft Results
2021-10-22 | SPP | Corrected LOIS & MW Amounts, Event Description and Primary Mitigation text
2021-11-03 | SPP | Updated report as final restudy results
2022-03-16 | SPP | DISIS-2017-001-2: Restudy of Group 4 Final Posting; Group 16 results to be posted at a later date
2022-06-16 | SPP | DISIS-2017-001-2: Group 16 results

## Requests
Gen Number | Gen Model | Region | Group | Queue | Fuel Type | MW Amount | LOIS Amount | Area | POI | Status | Reactive Compensation Requirements (MVAR)
GEN-2017-011 | REGCAU1 | Central | 01 - Woodward | DIS-17-1 | Solar | 151.8 | 151.8 | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE | -4.8
GEN-2017-047 | GEWTG2 | South | 02 - Hitchland | DIS-17-1 | Wind | 102 | 77 | SPS | Cole 115kV | FACILITY STUDY STAGE | 1.67
GEN-2017-100 | GEPVG | South | 02 - Hitchland | DIS-17-1 | Solar | 102.6 | 102.6 | SPS | Texas County 115kV | FACILITY STUDY STAGE | 1.64
GEN-2017-018 | SMASC126/REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Solar | 189 | 189 | SUNC | Thistle 345kV sub | FACILITY STUDY STAGE | -3.7
GEN-2017-021 | REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Wind | 200 | 200 | SUNC | Post Rock - Spearville 345kV | FACILITY STUDY STAGE | -9.5
GEN-2017-032 | REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Wind | 200 | 200 | SPS | Finney - Lamar 345kV | FACILITY STUDY STAGE | 0
GEN-2017-099 | REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Wind | 150 | 150 | SUNC | Post Rock - Spearville 345kV | FACILITY STUDY STAGE | -10.5
GEN-2017-004 | CP17093300 | North | 04 - Northwest Kansas | DIS-17-1 | Wind | 201.6 | 201.6 | WERE | Elm Creek - Summit 345kV | FACILITY STUDY STAGE | 10.61
GEN-2017-033 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 200 | 200 | AEPW | Oklaunion 345kV sub | FACILITY STUDY STAGE | 9.8
GEN-2016-037 | REGCAU1 | South | 07 - Southwestern Oklahoma | DIS-17-1 | Wind | 300 | 300 | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE | 32.1
GEN-2017-036 | REGCAU1 | South | 07 - Southwestern Oklahoma | DIS-17-1 | Solar | 100 | 100 | AEPW | Snyder - Cache 138kV | FACILITY STUDY STAGE | 1.7
GEN-2017-005 | GEWTG2 | Central | 12 - Northwest Arkansas | DIS-17-1 | Wind | 190 | 190 | WERE | Marmaton - Litchfield 161kV | FACILITY STUDY STAGE | -7.6
GEN-2017-009 | VC18084901 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Wind | 302 | 301 | WERE | Neosho - Caney River 345kV | FACILITY STUDY STAGE | -29.1
GEN-2017-022 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 65 | 65 | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE | -0.9
GEN-2017-040 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 200.1 | 200.1 | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE | -5.5
GEN-2017-061 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 101.5 | 101.5 | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE | -1.1
GEN-2017-068 | SMASC126 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 103.5 | 103.5 | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE | -3.1
GEN-2017-071 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 124.7 | 124.7 | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE | -1.2
GEN-2017-072 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 52.2 | 52.2 | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE | -0.5
GEN-2017-073 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 72.5 | 72.5 | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE | -0.7
GEN-2017-074 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 72.5 | 72.5 | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE | -0.7
GEN-2017-077 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 124.7 | 124.7 | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE | -1.2
GEN-2017-086 | VWCOR8 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Wind | 150 | 150 | WERE | Viola 345kV | FACILITY STUDY STAGE | -13.8
GEN-2017-092 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 200 | 200 | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE | -8.5
GEN-2017-085 | VWCOR8 | North | 09 - Nebraska | DIS-17-1 | Wind | 0.6 | 0.6 | NPPD | Friend 115kV | FACILITY STUDY STAGE | 4.95
GEN-2017-057 | GEPVG | South | 10 - Southeast Oklahoma/Northeast Texas | DIS-17-1 | Solar | 72.5 | 72.5 | AEPW | Hosston 69kV | FACILITY STUDY STAGE | 0.8
GEN-2017-060 | VC18084901/VC19024901 | Central | 12 - Northwest Arkansas | DIS-17-1 | Wind | 149.4 | 149.4 | EDE | LaRussell Energy Center 161kV | FACILITY STUDY STAGE | -8.2
GEN-2017-076 | GEPVG | Central | 12 - Northwest Arkansas | DIS-17-1 | Solar | 52.2 | 52.2 | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE | -0.6
GEN-2017-082 | VC18084901 | Central | 12 - Northwest Arkansas | DIS-17-1 | Wind | 149.4 | 149.4 | EDE | Asbury Plant 161kV | FACILITY STUDY STAGE | -6
GEN-2017-023 | REGCAU1 | South | 14 - South Central Oklahoma | DIS-17-1 | Solar | 85 | 85 | WFEC | Hugo Power Plant 138kV Sub | FACILITY STUDY STAGE | 1.03
GEN-2017-027 | CP20065709/VC20045709 | South | 14 - South Central Oklahoma | DIS-17-1 | Wind | 140 | 140 | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE | 5.05 (GEN1,2,3&4)
GEN-2017-075 | SWTGU2 | South | 14 - South Central Oklahoma | DIS-17-1 | Solar | 200 | 200 | OKGE | Hugo-Sunnyside 345kV | FACILITY STUDY STAGE | 8.95
GEN-2017-094 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-17-1 | Wind | 200 | 200 | WAPA | Fort Thompson-Huron 230kV | FACILITY STUDY STAGE | 9.3
GEN-2017-010 | SWTGU2 | North | 16 - Western North Dakota | DIS-17-1 | Wind | 200.1 | 200.1 | WAPA | Rhame 230kV Sub | FACILITY STUDY STAGE | 6.91
GEN-2017-048 | REGCAU1 | North | 16 - Western North Dakota | DIS-17-1 | Wind | 300 | 300 | WAPA | Neset 230kV | FACILITY STUDY STAGE | 30.78
GEN-2017-014 | VWCO81 | North | 17 - Western South Dakota | DIS-17-1 | Wind | 300 | 230 | WAPA | Philip Tap 230kV | FACILITY STUDY STAGE | 18.09
GEN-2017-097 | PE_GEN_700 | North | 17 - Western South Dakota | DIS-17-1 | Solar | 128 | 128 | WAPA | Underwood 115kV Sub | FACILITY STUDY STAGE | 1.29
SPSChanning | None | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1-PQ | Wind | 4.2 |  | SPS
SPSLeaCounty | None | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1-PQ | Solar | 5.5 |  | SPS
J748 | REGCAU1 | North | 09 - Nebraska | DIS-17-1-PQ | Wind | 100 |  | MEC
NPPDSpringview | GENCLS | North | 09 - Nebraska | DIS-17-1-PQ | Wind | 3 |  | NPPD
SWPANixaSolar | None | Central | 12 - Northwest Arkansas | DIS-17-1-PQ | Solar | 7.9 |  | SWPA
ASGI-2018-001GIA-61 | VWCOR6 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-17-1-PQ | Wind | 238 |  | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2018-001GIA-61 | VWCOR8 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-17-1-PQ | Wind | 230 |  | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
BEPCAyrshire | WT3G2 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 21 |  | BEPC-SPP | Ayershire 69kV
BEPCGerled | WT3G2 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 10.5 |  | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | WT3G2 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 10.5 |  | BEPC-SPP | Hummel 69kV
J718 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Solar | 49.98 |  | XEL
WAPATitanWind | REGCAU1 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 25 |  | WAPA
BEPCNDPW0 | WT3G2 | North | 16 - Western North Dakota | DIS-17-1-PQ | Wind | 7.5 |  | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | GEWTG2 | North | 16 - Western North Dakota | DIS-17-1-PQ | Wind | 5 |  | BEPC-SPP | ND Prairie Wind 115kV
GEN-2016-118 | VWCO81 | Central | 01 - Woodward | DIS-16-2 | Wind | 288 |  | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | GEWTG2 | Central | 01 - Woodward | DIS-16-2 | Wind | 202.5 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | GEWTG0501 | South | 02 - Hitchland | DIS-16-2 | Wind | 90 |  | SPS | Powell Corner 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-111 | GEWTG2 | North | 04 - Northwest Kansas | DIS-16-2 | Wind | 302 |  | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-160 | GEPVG | North | 04 - Northwest Kansas | DIS-16-2 | Battery | 20 |  | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | SMASC126 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Solar | 110 |  | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 150 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-123 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 148 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 150 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 74 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Gas | 20 |  | SPS | XTO-Cornell 115kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | SWTGU1 | South | 07 - Southwestern Oklahoma | DIS-16-2 | Wind | 303.6 |  | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | VWCO81 | South | 07 - Southwestern Oklahoma | DIS-16-2 | Wind | 200 |  | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | VWCO81 | South | 07 - Southwestern Oklahoma | DIS-16-2 | Wind | 100 |  | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-119 | VWCO81 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 600 |  | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 176 |  | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-134 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-137 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-138 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-139 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 100 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-141 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 350 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-142 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 350 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-145 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 175 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-146 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 175 |  | AEPW | Riverside 345kV | IA PENDING
GEN-2016-153 | VWCO81 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 134 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-162 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 252 |  | WERE | Benton 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-163 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 252 |  | WERE | Benton 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-074 | VWCO81 | North | 09 - Nebraska | DIS-16-2 | Wind | 200 |  | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-147 | GEPVG | North | 09 - Nebraska | DIS-16-2 | Solar | 40 |  | NPPD | Sidney 115kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | GEPVG | South | 10 - Southeast Oklahoma/Northeast Texas | DIS-16-2 | Solar | 73.5 |  | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | VWCO81 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 300 |  | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 252 |  | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 252 |  | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-2 | Wind | 132.5 |  | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-126 | GSCOR1 | South | 14 - South Central Oklahoma | DIS-16-2 | Wind | 172.5 |  | OKGE | Arbuckle 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-036 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-16-2 | Wind | 44.6 |  | WAPA | Granite Falls 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-16-2 | Wind | 98.9 |  | WAPA | Bismark-Glenham 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | GEWTG2 | North | 16 - Western North Dakota | DIS-16-2 | Wind | 202 |  | WAPA | Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | WT3G2 | North | 16 - Western North Dakota | DIS-16-2 | Wind | 202 |  | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-094 | GEWTG2 | North | 17 - Western South Dakota | DIS-16-2 | Wind | 200 |  | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
J555 | VWCOR6 | North | 09 - Nebraska | DIS-16-2-PQ | Wind | 140 |  | MEC
J583 | REGCAU1 | North | 09 - Nebraska | DIS-16-2-PQ | Wind | 200 |  | MEC | Fallow Avenue 345kV . Zip Code 50002
J476 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2-PQ | Wind | 246 |  | AMMO | Atchison County to Booneville 345kV Line Tap
J541 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2-PQ | Wind | 400 |  | AMMO | Zachary-Ottumwa 345kV line
J611 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2-PQ | Wind | 110 |  | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-011 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 7.4 |  | SWPA | Allen 138kV
ASGI-2016-012 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 32.1 |  | SWPA | Tupelo 138kV
ASGI-2016-012 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 29.63 |  | SWPA | Tupelo 138kV
ASGI-2016-013 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 2.46 |  | WFEC | Ashland 138kV
ASGI-2016-013 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 2.46 |  | WFEC | Ashland 138kV
J512 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 20 |  | MP | Nobles - Fenton 115kV line
J512 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 230 |  | MP | Nobles - Fenton 115kV line
J569 | SWTGU2 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 100 |  | XEL | NSP Rock County
J587 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 100 |  | XEL | J460 on the Brookings-H081 345kV line
J587 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 100 |  | XEL | J460 on the Brookings-H081 345kV line
J590 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 45 |  | MEC | Obrien - Kossuth 345kV line
J590 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 45 |  | MEC | Obrien - Kossuth 345kV line
GEN-2015-095 | VWCOR6 | Central | 01 - Woodward | DIS-16-1 | Wind | 176 |  | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | GSCOR1 | Central | 01 - Woodward | DIS-16-1 | Wind | 248.4 |  | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | GEWTG2 | Central | 01 - Woodward | DIS-16-1 | WIND | 148.4 |  | WFEC | Moreland 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | GEWTG2 | Central | 01 - Woodward | DIS-16-1 | WIND | 148.4 |  | WFEC | Moreland 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 478.7 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 478.7 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 478.7 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 519.46 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 519.46 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 519.46 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-082 | GEWTG2 | South | 02 - Hitchland | DIS-16-1 | Wind | 200 |  | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | GEWTG2 | Central | 03 - Spearville | DIS-16-1 | Wind | 78.2 |  | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | GEWTG2 | Central | 03 - Spearville | DIS-16-1 | Wind | 299 |  | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | SWTGU1 | North | 04 - Northwest Kansas | DIS-16-1 | Wind | 73.6 |  | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-004 | ECODFG | South | 06 - South Texas Panhandle/New Mexico | DIS-16-1 | Wind | 0.4 |  | SPS | Palo Duro 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-1 | Wind | 9.6 |  | SPS | Palo Duro 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | GENROE | South | 06 - South Texas Panhandle/New Mexico | DIS-16-1 | CT | 196 |  | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Steam Turbine | 29 |  | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Steam Turbine | 29 |  | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 151.8 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 202.8 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 200 |  | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 248.16 |  | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 250 |  | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 250 |  | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 198.2 |  | OKGE | Middleton Tap 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-071 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 198.2 |  | OKGE | Middleton Tap 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-073 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | WIND | 220 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-089 | GEWTG2 | North | 09 - Nebraska | DIS-16-1 | Wind | 7.5 |  | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | GEWTG2 | North | 09 - Nebraska | DIS-16-1 | Wind | 192.5 |  | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | VWCOR6 | North | 09 - Nebraska | DIS-16-1 | Wind | 300 |  | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | GSCOR1 | North | 09 - Nebraska | DIS-16-1 | Wind | 230 |  | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | GEWTG2 | North | 09 - Nebraska | DIS-16-1 | Wind | 250.7 |  | NPPD | Axtell - Post Rock 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | VWCOR6 | North | 09 - Nebraska | DIS-16-1 | Wind | 50 |  | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | GENROU | Central | 12 - Northwest Arkansas | DIS-16-1 | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | GENROU | Central | 12 - Northwest Arkansas | DIS-16-1 | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-003 | GENSAL | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-1 | Diesel | 12 |  | KCPL | Paola 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 151.8 |  | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 137.5 |  | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 23 |  | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | GSCOR1 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 100 |  | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | GEPVG | South | 14 - South Central Oklahoma | DIS-16-1 | Solar | 100 |  | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 100 |  | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 100 |  | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-017 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-16-1 | Wind | 250.24 |  | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | VWCOR6 | North | 16 - Western North Dakota | DIS-16-1 | Wind | 202 |  | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SUSPENSION
J475 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 168 |  | MEC
J475 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 32 |  | MEC
J495 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 100 |  | ALTW | Ledyard-Colby 345kV line
J495 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 100 |  | ALTW | Ledyard-Colby 345kV line
J498 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J498 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J499 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 168 |  | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J500 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 166 |  | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J500 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 166 |  | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 99.1 |  | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J506 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 100.9 |  | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J524 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Solar | 100 |  | MEC | Webster 161kV bus
J527 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Booneville Cooper 345kV line
J527 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Booneville Cooper 345kV line
J530 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Montezuma - Hills 345kV Line
J530 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Montezuma - Hills 345kV Line
J534 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | ALTW | Kossuth - Webster 345kV Line
J534 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | ALTW | Kossuth - Webster 345kV Line
J535 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 210 |  | ALTW | J411 - Lehigh 345kV Line
J432 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 98 |  | XEL | Brookings 345kV
J460 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 100 |  | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J460 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 100 |  | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J488 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 151.8 |  | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 150 |  | OTP | Big Stone - Brookings 345kV
J510 | GENTPJU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Gas | 284.5 |  | OTP | Scandinavia Township 113N, Range 48W
J526 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 150 |  | OTP | Brooking County to Big Stone South 345kV line
J526 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 150 |  | OTP | Brooking County to Big Stone South 345kV line
J529 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 125 |  | MEC | Obrien - Kossuth 345kV line
J529 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 125 |  | MEC | Obrien - Kossuth 345kV line
GEN-2015-048 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 199.4 |  | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 100.65 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-057 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 100.65 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-057 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 100.65 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-093 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 250 |  | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 250 |  | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | SWTGU2 | North | 04 - Northwest Kansas | DIS-15-2 | Wind | 197.8 |  | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | SWTGU2 | North | 04 - Northwest Kansas | DIS-15-2 | Wind | 202.4 |  | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-055 | AEINX | South | 07 - Southwestern Oklahoma | DIS-15-2 | Solar | 40 |  | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-034 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 200 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 297.8 |  | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 297.8 |  | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 297.8 |  | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 300 |  | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 107.06 |  | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | A1530U1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 299.25 |  | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | A1530U1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 299.25 |  | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 248.4 |  | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | A1530U1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 299.25 |  | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | GMD0352 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 166.32 |  | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 218.5 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 218.5 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | VWCOR6 | North | 09 - Nebraska | DIS-15-2 | Wind | 300 |  | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | PVGU1 | South | 14 - South Central Oklahoma | DIS-15-2 | Battery | 20 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-15-2 | Wind | 140 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-15-2 | Wind | 110 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | REGCAU1 | North | 16 - Western North Dakota | DIS-15-2 | Wind | 300 |  | WAPA | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2 | Wind | 150 |  | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G612 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 150 |  | ALTW | ITC Midwest Fernald 115kV
GEN-2007-017IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-017IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 66 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 34 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | OPPD | Ft Thompson-Grand Island 345kV
H096 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 50 |  | ALTW | Grand Junction - Perry 161kV
J191 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 101.2 |  | MEC | Rolling Hills 345kV
J274 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | Winterset. - Creston 161kV
J279 | GENROU | North | 09 - Nebraska | DIS-15-2-PQ | Coal | 30 |  | MEC | Raun 345kV
J279NEAL | GENROU | North | 09 - Nebraska | DIS-15-2-PQ | Coal | 680 |  | MEC
J285 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 125 |  | MEC | Proposed O'Brien County 345kV
J285 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 125 |  | MEC | Proposed O'Brien County 345kV
J289 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 20 |  | MEC | 161kV substation on Winterset Junction to Creston 161kV Line
J343 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 150 |  | MEC | 161kV on Creston-Clarinda line
J411 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 150 |  | MEC | LeHigh - Raun 345kV Line
J411 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 25 |  | MEC | LeHigh - Raun 345kV Line
J411 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 125 |  | MEC | LeHigh - Raun 345kV Line
J412 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | LeHigh - Raun 345kV line
J412 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | LeHigh - Raun 345kV line
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 11.5 |  | ALTW
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 11 |  | ALTW
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 90 |  | ALTW
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 87.5 |  | ALTW
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 29.9 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 2.6 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 117.5 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 2.6 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 29.9 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 117.5 |  | ALTW | Kossuth - Obrien 345kV line
R15 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 80 |  | MEC | Pomeroy 161kV
R22 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 102.5 |  | MEC
R22 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 97.5 |  | MEC
R23 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | Monona - Carroll 161kV
R34 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 170.2 |  | MEC | Council Bluffs - Madison County 345kV
R34 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 79.8 |  | MEC | Council Bluffs - Madison County 345kV
R35 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 27.5 |  | MEC | Pomeroy Wind Farm site
R35 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 52.5 |  | MEC | Pomeroy Wind Farm site
R42 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 136 |  | MEC
R42 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 114 |  | MEC
R49 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 12 |  | MEC | Pomeroy Generating station
R65 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 92 |  | MEC | R34 Expansion
R26 | WT3E1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-2-PQ | Wind | 146 |  | MEC | MEC Cooper - Booneville 345kV
ASGI-2016-005NWE205 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.2 |  | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-005NWE205 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 19.8 |  | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.2 |  | WAPA | Kimball 69kV
ASGI-2016-007NWE208 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 19.8 |  | WAPA | Kimball 69kV
G255 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 50 |  | XEL | Yankee
G255 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 50 |  | XEL | Yankee
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 183.48 |  | XEL
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 116.62 |  | XEL
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 188.5 |  | XEL
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 188.5 |  | XEL
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 49 |  | XEL | Nobles County
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 51 |  | XEL | Nobles County
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 49 |  | XEL | Nobles County
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 51 |  | XEL | Nobles County
G349 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Brookings County
G349 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Brookings County
G362 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | GRE | Pleasant Valley
G362 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | GRE | Pleasant Valley
G370 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Gas | 148 |  | XEL | Anson 4
G370 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Gas | 57 |  | XEL | Anson 4
G389 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Gas | 200 |  | GRE | Elk River 230kV
G514 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 148.8 |  | XEL | Lakefield Station via Trimont G263 Interconnect
G514 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 1.2 |  | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 80 |  | ALTW | Adams - Lime Creek 161kV
G548 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 80 |  | ALTW | Barton 161kV
G586 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 15 |  | XEL | Xcel New Yankee Sub 34.5kV
G586 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 15 |  | XEL | Xcel New Yankee Sub 34.5kV
G595 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 150 |  | ALTW | Lime Creek 161kV
G602 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 16.4 |  | XEL | Nobles County 115kV
G602 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 1.25 |  | XEL | Nobles County 115kV
G602 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 14.35 |  | XEL | Nobles County 115kV
G604 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 44 |  | ALTW | Owatonna - County Line 69kV
G621 | WT1G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 20 |  | XEL | Golf - Wookstock 34.5kV
G685 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 20 |  | XEL | Lake Lillian - Atwater 69kV
G735 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 200 |  | ALTW | Lime Creek
G736 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 200 |  | OTP | Big Stone South 230kV
G741 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Waste Heat Recovery | 1.85 |  | ALTW | Near Alliant 69kV line
G741 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Waste Heat Recovery | 6.15 |  | ALTW | Near Alliant 69kV line
G826 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G826 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G870 | WT1G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100.5 |  | ALTW | Hayward - Winnebago 161kV
G870 | WT1G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100.5 |  | ALTW | Hayward - Winnebago 161kV
G930 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 20 |  | XEL | Sherco
G930 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 20 |  | XEL | Sherco
G930 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 20 |  | XEL | Sherco
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 730 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 40.5 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 730 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 40.5 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 910 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 40.5 |  | XEL
G971 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 20 |  | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2002-009IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 40.5 |  | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 50 |  | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Wessington Springs 230kV
GEN-2009-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | GENROE | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 99.5 |  | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-018IS | GENROE | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.5 |  | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 99 |  | BEPC-SPP | Bismarck-Glenham 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 34 |  | BEPC-SPP | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 19.5 |  | WAPA | Redfield NW 115kV
GEN-2014-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 103.24 |  | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 201 |  | XEL | Brookings County - Lyon County 345kV
J091 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 66 |  | ALTW
J183 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100.8 |  | XEL | Split Rock
J183 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.1 |  | XEL | Split Rock
J183 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 99.1 |  | XEL | Split Rock
J278 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | 161kV bus at the Pleasant Valley Station
J278 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | 161kV bus at the Pleasant Valley Station
J299 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 36.5 |  | XEL | Wilmarth
J299 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 36.5 |  | XEL | Wilmarth
J385 | PVGU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Solar | 100 |  | XEL | Chisago 115kV
J400 | PVGU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Solar | 62 |  | XEL | Lyon County 115kV
J400 | PVGU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Solar | 0.5 |  | XEL | Lyon County 115kV
J407 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Glenworth 161kV
J407 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Glenworth 161kV
J426 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Chanarambie 35.4kV
J436 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 150 |  | OTP | Big Stone South - Ellendale 345kV line
J437 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 150 |  | OTP | Big Stone South - Ellendale 345kV line
J442 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 200 |  | OTP | Big Stone via a radial 230kV line
R39 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 166.66 |  | MEC | Raun - Lakefield Junction
R39 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 166.66 |  | MEC | Raun - Lakefield Junction
R39 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 166.66 |  | MEC | Raun - Lakefield Junction
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.8 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 67.2 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 29.4 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 12.6 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 40 |  | OTP | Rugby 115kV
G752 | WT3G2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 42.5 |  | MDU | Bison - Hettinger 230kV
G752 | WT3G2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 107.5 |  | MDU | Bison - Hettinger 230kV
G830 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 99 |  | GRE | GRE McHenry
GEN-2005-008IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 49.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 49.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-015IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2009-026IS | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 106.5 |  | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2009-026IS | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 3.5 |  | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 5.86 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 5.86 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-010IS | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | BEPC-SPP | Neset 115kV
GEN-2014-014IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | BEPC-SPP | Belfield-Rhame 230kV
J262 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 100 |  | OTP | OTP Jamestown 345/115kV
J263 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 100 |  | OTP | OTP Jamestown 345/115kV
J290 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | XEL | 230kV Rugby to Glenboro
J316 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | MDU | MDU 230kV Tatanka-Ellendale line
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 10.4 |  | MDU | MDUs existing Lewis & Clark Jct
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.6 |  | MDU | MDUs existing Lewis & Clark Jct
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.6 |  | MDU | MDUs existing Lewis & Clark Jct
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 10.4 |  | MDU | MDUs existing Lewis & Clark Jct
MPC01300 | GENROU | North | 16 - Western North Dakota | DIS-15-2-PQ | Coal | 493 |  | OTP | Square Butte 230kV
MPC02100 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 8.95 |  | OTP | Center - Mandan 230kV
MPC02100 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 90.3 |  | OTP | Center - Mandan 230kV
MPC02100 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.75 |  | OTP | Center - Mandan 230kV
Young1 | GENROU | North | 16 - Western North Dakota | DIS-15-2-PQ | Coal | 274 |  | OTP
GEN-2006-002IS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 51 |  | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 2 |  | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 79.6 |  | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 0.4 |  | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | GENSAL | Central | 03 - Spearville | DIS-15-1 | Thermal | 6.132 |  | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | GEPVG_LV5 | Central | 03 - Spearville | DIS-15-1 | Solar | 20 |  | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-15-1 | Wind | 10.29 |  | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-15-1 | Wind | 4 |  | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-15-1 | Wind | 135.7 |  | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | SMAXINV | South | 07 - Southwestern Oklahoma | DIS-15-1 | Solar | 120 |  | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2015-004 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Thermal | 109.364 |  | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-004 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Thermal | 109.364 |  | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-004 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Thermal | 109.364 |  | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 202.8 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 154.575 |  | OKGE | Tap Medford Tap - Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 154.575 |  | OKGE | Tap Medford Tap - Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | GMD0352 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 199.275 |  | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | GMD0352 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 199.275 |  | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 217.8 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 215.95 |  | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 215.95 |  | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 215.95 |  | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | GEWTG2 | North | 09 - Nebraska | DIS-15-1 | Wind | 160 |  | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | GEWTG2 | North | 09 - Nebraska | DIS-15-1 | Wind | 150.36 |  | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | GEWTG2 | North | 09 - Nebraska | DIS-15-1 | Wind | 150.36 |  | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-005 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-1 | Wind | 200.11 |  | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-1 | Wind | 200.11 |  | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-1 | Wind | 200.11 |  | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | GD0810 | Central | 01 - Woodward | DIS-14-2 | Wind | 99.1 |  | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | GD0810 | Central | 01 - Woodward | DIS-14-2 | Wind | 99.1 |  | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | GEWTG2 | Central | 01 - Woodward | DIS-14-2 | Wind | 248.94 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | GEWTG2 | Central | 01 - Woodward | DIS-14-2 | Wind | 248.94 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | GEWTG2 | Central | 01 - Woodward | DIS-14-2 | Wind | 248.94 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | SWTGU2 | North | 04 - Northwest Kansas | DIS-14-2 | Wind | 2.42 |  | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | GSCOR1 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Wind | 148.35 |  | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | GEPVG_LV5 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 66.8 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | XCPVIN | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 3.2 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | REGCAU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 70 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | GEPVG_LV5 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 30 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Wind | 167.9 |  | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Wind | 151.8 |  | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2014-014 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | Thermal | 54.3 |  | GRDA | Ferguson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CT/ST | 259 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CT/ST | 259 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CC | 0 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CC | 0 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | Wind | 248.4 |  | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | GEWTG2 | North | 09 - Nebraska | DIS-14-2 | Wind | 35.8 |  | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | GEWTG2 | North | 09 - Nebraska | DIS-14-2 | Wind | 5.11 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | GEWTG2 | North | 09 - Nebraska | DIS-14-2 | Wind | 5.11 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-039 | REGCAU1 | North | 09 - Nebraska | DIS-14-2 | Wind | 73.4 |  | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-021 | VWCOR6 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-14-2 | Wind | 300 |  | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | VWCOR6 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-14-2 | Wind | 300 |  | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-14-2 | Wind | 249.9 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | GEWTG2 | Central | 01 - Woodward | DIS-14-1 | Wind | 209.43 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | GEWTG2 | Central | 01 - Woodward | DIS-14-1 | Wind | 106.47 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-1 | Wind | 199.5 |  | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-1 | Wind | 199.5 |  | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-004 | GEWTG2 | North | 09 - Nebraska | DIS-14-1 | Wind | 3.96 |  | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | GEWTG2 | North | 09 - Nebraska | DIS-14-1 | Wind | 73.39 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | GEWTG2 | North | 09 - Nebraska | DIS-14-1 | Wind | 0.11 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.2 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 3 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.2 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 3 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.2 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 3 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.12 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.27 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.29 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.35 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 1.15 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.18 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.34 |  | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.34 |  | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.34 |  | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-2 | Wind | 19.8 |  | SPS | Clovis Intg. 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | SMASC139 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-2 | Solar | 28.6 |  | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Gas | 516.4 |  | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Gas | 516.4 |  | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Wind | 299 |  | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Wind | 299 |  | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | SWTGU1 | North | 09 - Nebraska | DIS-13-2 | Wind | 73.6 |  | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | GEWTG2 | North | 09 - Nebraska | DIS-13-2 | Wind | 202.5 |  | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | SWTGU2 | South | 02 - Hitchland | DIS-13-1 | Wind | 11.5 |  | SPS | PanTex South 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | SWTGU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-1 | Wind | 18.4 |  | SPS | FE Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-003 | SWTGU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-1 | Wind | 18.4 |  | SPS | Clovis Intg. 115kV
GEN-2013-016 | GENROE | South | 06 - South Texas Panhandle/New Mexico | DIS-13-1 | CT | 195.4 |  | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | SWTGU1 | North | 09 - Nebraska | DIS-13-1 | Wind | 50.6 |  | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | GEWTG2 | North | 09 - Nebraska | DIS-13-1 | Wind | 1.2 |  | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-010 | GENROU | Central | 12 - Northwest Arkansas | DIS-13-1 | Coal | 681 |  | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | GENROU | Central | 12 - Northwest Arkansas | DIS-13-1 | Coal | 681 |  | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-13-1 | Wind | 100 |  | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | GSCORE | Central | 03 - Spearville | DIS-12-2 | Wind | 178.2 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | Wind | 19.8 |  | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | VC18084500 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | Wind | 48.72 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | VC18084500 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | Wind | 430.08 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 157 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 157 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 172 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | GENROE | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 196 |  | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | VWCOR6 | South | 07 - Southwestern Oklahoma | DIS-12-2 | Wind | 74 |  | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 299 |  | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 299 |  | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 107.06 |  | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 107.06 |  | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | CT | 103 |  | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | GENSAE | North | 09 - Nebraska | DIS-12-2 | Gas | 4.8 |  | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | GNESAL | Central | 03 - Spearville | DIS-12-1 | Steam | 21.21 |  | SUNC | ABBK 2 69kV
GEN-2012-007 | GENTPJU1 | Central | 03 - Spearville | DIS-12-1 | Gas | 120 |  | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | GENTPJU1 | Central | 03 - Spearville | DIS-12-1 | Gas | 120 |  | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | WT4G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-1 | Wind | 61.2 |  | SPS | Tap Grassland - Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | VWCOR6 | Central | 01 - Woodward | DIS-11-2 | Wind | 300 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | VWCOR6 | Central | 01 - Woodward | DIS-11-2 | Wind | 300 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | Wind | 9 |  | SPS | Pleasant Hill 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | Wind | 10.8 |  | SPS | Pleasant Hill 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | NG CT | 180 |  | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | Diesel CT | 23 |  | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | CT | 172 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-11-2 | Wind | 150 |  | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 3.6 |  | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 3.6 |  | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 18 |  | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 4.5 |  | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 18 |  | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056PQ | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 18 |  | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-11-2 | Wind | 76 |  | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-11-2 | Wind | 74 |  | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-11-2 | Wind | 108 |  | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | GEWTG2 | Central | 01 - Woodward | DIS-11-1 | Wind | 106.47 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | VWCOR6 | Central | 01 - Woodward | DIS-11-1 | Wind | 174 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | VWCOR6 | Central | 01 - Woodward | DIS-11-1 | Wind | 174 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | GEWTG2 | Central | 01 - Woodward | DIS-11-1 | Wind | 165.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | GEWTG2 | Central | 01 - Woodward | DIS-11-1 | Wind | 165.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-002 | GENSAL | South | 02 - Hitchland | DIS-11-1 | Wind | 10 |  | SPS | Herring 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | GENSAL | South | 02 - Hitchland | DIS-11-1 | Wind | 10 |  | SPS | Herring 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | GSCORE | South | 02 - Hitchland | DIS-11-1 | Wind | 99 |  | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | GSCORE | South | 02 - Hitchland | DIS-11-1 | Wind | 99 |  | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | SWTGU2 | South | 02 - Hitchland | DIS-11-1 | Wind | 149.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | SWTGU2 | South | 02 - Hitchland | DIS-11-1 | Wind | 149.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-008 | VWCOR6 | Central | 03 - Spearville | DIS-11-1 | Wind | 600 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | VWCOR6 | Central | 03 - Spearville | DIS-11-1 | Wind | 600 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | VWCOR6 | Central | 03 - Spearville | DIS-11-1 | Wind | 600 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | GEWTG2 | North | 04 - Northwest Kansas | DIS-11-1 | Wind | 201 |  | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-003 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 10 |  | SPS | Hendricks 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 6.86 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 2 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 2.1 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 69 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-11-1 | Gas | 4.8 |  | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | GEWTG2 | North | 09 - Nebraska | DIS-11-1 | Wind | 73.6 |  | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | GEWTG2 | North | 09 - Nebraska | DIS-11-1 | Wind | 120 |  | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-008 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-11-1 | Coal | 904.5 |  | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-11-1 | Coal | 0 |  | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | M24G1 | Central | 01 - Woodward | DIS-10-2 | Wind | 298.45 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | WT3G2 | Central | 01 - Woodward | DIS-10-2 | Wind | 298.45 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | GEWTG2 | South | 02 - Hitchland | DIS-10-2 | Wind | 149.85 |  | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | GEWTG2 | South | 02 - Hitchland | DIS-10-2 | Wind | 149.85 |  | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 29.9 |  | SPS | Tap LE-Tatum - LE-Crossroads 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-021 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 10 |  | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-021 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 4.95 |  | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-001 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 27.3 |  | SPS | Lovington 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | GEWTG2 | North | 09 - Nebraska | DIS-10-2 | Wind | 200 |  | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | GEWTG2 | South | 02 - Hitchland | DIS-10-1 | Wind | 249.9 |  | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | SWTGU1 | South | 02 - Hitchland | DIS-10-1 | Wind | 177.1 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | SWTGU1 | South | 02 - Hitchland | DIS-10-1 | Wind | 181.7 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | SWTGU2 | Central | 03 - Spearville | DIS-10-1 | Wind | 165.6 |  | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | GEWTG2 | North | 04 - Northwest Kansas | DIS-10-1 | Wind | 198.69 |  | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | SWTGU2 | North | 04 - Northwest Kansas | DIS-10-1 | Wind | 48.3 |  | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Gas | 42.196 |  | SPS | Lovington 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Wind | 50 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Wind | 124 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Wind | 126 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Gas | 180 |  | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | VWCOR4 | South | 07 - Southwestern Oklahoma | DIS-10-1 | Wind | 99.83 |  | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | GXX048 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 100.3 |  | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | GXX048 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 100.3 |  | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | GXX048 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 98.7 |  | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | GEWTG2 | North | 09 - Nebraska | DIS-10-1 | Wind | 89.66 |  | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | VWCOR6 | North | 09 - Nebraska | DIS-10-1 | Wind | 72 |  | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | SWTGU2 | South | 02 - Hitchland | DIS-09-1 | Wind | 161 |  | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | SWTGU2 | South | 02 - Hitchland | DIS-09-1 | Wind | 161 |  | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | WT4G2 | Central | 03 - Spearville | DIS-09-1 | Wind | 131.1 |  | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | SWTGU2 | Central | 03 - Spearville | DIS-09-1 | Wind | 98.9 |  | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | SWTGU1 | Central | 03 - Spearville | DIS-09-1 | Wind | 200.1 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | SWTGU1 | Central | 03 - Spearville | DIS-09-1 | Wind | 200.1 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | GEWTG2 | North | 04 - Northwest Kansas | DIS-09-1 | Wind | 100.24 |  | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | GEWTG2 | North | 04 - Northwest Kansas | DIS-09-1 | Wind | 100.24 |  | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | GEWTG2 | South | 07 - Southwestern Oklahoma | DIS-09-1 | Wind | 73.6 |  | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | GEWTG2 | South | 07 - Southwestern Oklahoma | DIS-09-1 | Wind | 75.2 |  | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-09-1 | Wind | 59.8 |  | OKGE | TAP Deer Creek - Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 75 |  | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 40.5 |  | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 0.2 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 0.2 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 100.3 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 100.3 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-09-1 | CT | 675 |  | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-09-1 | CT | 675 |  | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-09-1 | CT | 675 |  | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 209.43 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 202.5 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 299.2 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 299.2 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | SWTGU2 | Central | 01 - Woodward | ICS1 | Wind | 170.2 |  | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | GSCORE | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | GSCORE | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | VWCOR6 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | VWCOR6 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | SWTGU2 | Central | 01 - Woodward | ICS1 | Wind | 101.2 |  | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | VWCOR6 | South | 02 - Hitchland | ICS1 | Wind | 102 |  | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | VWCOR6 | South | 02 - Hitchland | ICS1 | Wind | 20 |  | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | VWCOR6 | South | 02 - Hitchland | ICS1 | Wind | 78 |  | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | GEWTG2 | Central | 03 - Spearville | ICS1 | Wind | 249.75 |  | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | GENROU | South | 07 - Southwestern Oklahoma | ICS1 | Gas | 48.5 |  | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | GENROU | South | 07 - Southwestern Oklahoma | ICS1 | Gas | 49.1 |  | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | GENROU | South | 07 - Southwestern Oklahoma | ICS1 | Gas | 49.84 |  | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-014 | WT2G1 | Central | 01 - Woodward | PQ | Wind | 94.5 |  | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | GEWTG2 | Central | 01 - Woodward | PQ | Wind | 102 |  | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | GEWTG2 | Central | 01 - Woodward | PQ | Wind | 120 |  | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | WT2G1 | Central | 01 - Woodward | PQ | Wind | 18.9 |  | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | M24G1 | Central | 01 - Woodward | PQ | Wind | 132 |  | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 79.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 82.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 78 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | WT2G1 | South | 02 - Hitchland | PQ | Wind | 79.8 |  | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | SWTEU1 | South | 02 - Hitchland | PQ | Wind | 78.2 |  | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | SWTGU2 | South | 02 - Hitchland | PQ | Wind | 161 |  | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 30 |  | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 49.6 |  | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 79.5 |  | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | GENSAL | South | 02 - Hitchland | PQ | Wind | 20 |  | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 80 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 134 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 80 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 76 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
LlanoEstacadoWhiteDeer | WT1G1 | South | 02 - Hitchland | PQ | Wind | 80 |  | SPS | Llano Wind 115kV
SPSCarson | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
SPSDumas19thSt | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Dumas 19th Street 115kV
SPSDumas19thSt | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Dumas 19th Street 115kV
SPSEtter | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Etter 115kV
SPSEtter | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Etter 115kV
SPSMooreE | None | South | 02 - Hitchland | PQ | Wind | 7.5 |  | SPS | Moore East 115kV
SPSMooreE | None | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Moore East 115kV
SPSSherman | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Sherman 115kV
SPSSherman | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Sherman 115kV
GEN-2001-039A | GEWTG2 | Central | 03 - Spearville | PQ | Wind | 105 |  | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | GEWTG2 | Central | 03 - Spearville | PQ | Wind | 148.5 |  | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | GEWTG2 | Central | 03 - Spearville | PQ | Wind | 155.2 |  | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | SWTGU2 | Central | 03 - Spearville | PQ | Wind | 248.4 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | WT4E2 | Central | 03 - Spearville | PQ | Wind | 248.4 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | VWCOR6 | Central | 03 - Spearville | PQ | Wind | 94 |  | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | WT4G1 | Central | 03 - Spearville | PQ | Wind | 94 |  | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | REGCAU1 | Central | 03 - Spearville | PQ | Wind | 112.2 |  | SUNC | Gray County Tap 115kV
GEN-2001-039M | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 99 |  | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 1 |  | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 101 |  | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 1 |  | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 99 |  | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | WT2G1 | North | 04 - Northwest Kansas | PQ | Wind | 100.8 |  | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | WT2G1 | North | 04 - Northwest Kansas | PQ | Wind | 148.5 |  | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 120 |  | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 60 |  | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 80 |  | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | GENROU | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 150 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | GENROU | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 150 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 55.122 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 55.122 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 55.122 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | GENROE | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 156.476 |  | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | GENROE | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 156.9 |  | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | GENROE | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 235.582 |  | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
SPSHopi | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | Hopi 115kV
SPSJal | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | S Jal 115kV
SPSLeaRoad | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | Lea Road 115kV
SPSMonument | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | Monument 115kV
SPSOcotillo | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | S_Jal 115kV
Sunray | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 49.5 |  | SPS | Valero 115kV
GEN-2001-026 | WT1G1 | South | 07 - Southwestern Oklahoma | PQ | Wind | 74.25 |  | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | A1530U1 | South | 07 - Southwestern Oklahoma | PQ | Wind | 123 |  | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | WT2G1 | South | 07 - Southwestern Oklahoma | PQ | Wind | 151.2 |  | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 105.6 |  | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 156.8 |  | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 77.76 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 29.16 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | GXX048 | South | 07 - Southwestern Oklahoma | PQ | Wind | 132 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | SWTGU2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 98.9 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 150 |  | AECI | Remington 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 199.5 |  | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 199.5 |  | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | VWCOR4 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 300.6 |  | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | VWCOR4 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 300.6 |  | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | WT1G1 | North | 09 - Nebraska | PQ | Wind | 15 |  | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | WT1G1 | North | 09 - Nebraska | PQ | Wind | 60 |  | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | GENROU | North | 09 - Nebraska | PQ | Coal | 75 |  | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | VWCOR4 | North | 09 - Nebraska | PQ | Wind | 42 |  | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | GEWTG2 | North | 09 - Nebraska | PQ | Wind | 80 |  | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | GEWTG2 | North | 09 - Nebraska | PQ | Wind | 80 |  | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | VWCOR4 | North | 09 - Nebraska | PQ | Wind | 81 |  | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | GEWTG2 | North | 09 - Nebraska | PQ | Wind | 60 |  | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBrokenBow | GENCLS | North | 09 - Nebraska | PQ | Heat | 7.3 |  | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | None | North | 09 - Nebraska | PQ | Solar | 10 |  | NPPD | Kearney Northeast
NPPDBurtCountyWind | None | North | 09 - Nebraska | PQ | Wind | 10 |  | NPPD | Tekamah & Oakland 115kV
NPPDBurtCountyWind | None | North | 09 - Nebraska | PQ | Wind | 10 |  | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | GENCLS | North | 09 - Nebraska | PQ | Heat | 3.3 |  | NPPD | Ord 115kV
NPPDColumbusHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 15 |  | NPPD | Columbus 115kV
NPPDColumbusHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 15 |  | NPPD | Columbus 115kV
NPPDColumbusHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 15 |  | NPPD | Columbus 115kV
NPPDOrd | GENCLS | North | 09 - Nebraska | PQ | Heat | 10.8 |  | NPPD | Ord 115kV
NPPDStuart | GENCLS | North | 09 - Nebraska | PQ | Heat | 1.8 |  | NPPD | Ainsworth 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 34 |  | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPointHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 34 |  | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPointHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 34 |  | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | GENROU | North | 09 - Nebraska | PQ | Heat | 60 |  | BEPC-SPP | Spirit Mound (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | GENROU | North | 09 - Nebraska | PQ | Heat | 60 |  | BEPC-SPP | Spirit Mound (WAPA) 115kV
GEN-2001-030 | GENROU | Central | 12 - Northwest Arkansas | PQ | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | GENROU | Central | 12 - Northwest Arkansas | PQ | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-008 | None | Central | 13 - Northeast Kansas/Northwest Missouri | PQ | Gas | 3.55 |  | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-008 | None | Central | 13 - Northeast Kansas/Northwest Missouri | PQ | Gas | 3.55 |  | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Stability Analysis
Region | Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational) | Notes
Central | 01 - Woodward | 19W | Normal | G1_FLT1-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT2-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT3-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT4-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT5-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT6-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT7-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT8-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT9-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT10-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT12-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT13-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT14-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT15-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT16-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT17-3PH | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT18-3PH | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.3. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT19-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT20-3PH | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT21-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT22-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT23-3PH | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT26-3PH | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 (520893) 138.0 kV to EL RENO2 (520892) 69.0 kV to ELRNTERT (521167) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT43-3PH | 3 Phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT44-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT46-3PH | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT47-3PH | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT48-3PH | 3 Phase fault on JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.4. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT49-3PH | 3 Phase fault on REDROCKRD4 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.2. HINTON 4 (511433) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT2-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT3-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT4-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT5-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT6-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT7-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT8-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT9-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT10-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT11-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT12-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT13-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT14-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT15-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT16-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT17-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT18-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT38-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT39-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT40-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT41-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT42-PO | Prior Outage: WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit 3 Phase Fault on WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit b.2. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT43-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT45-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT46-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT47-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT48-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 19W | Normal | G1_FLT49-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT50-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT51-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT52-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT53-PO | Prior Outage: MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT55-PO | Prior Outage: CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT5-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT6-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT7-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT10-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT14-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT15-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT16-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT17-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT18-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT19-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT20-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT21-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT22-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT23-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT28-SB | Single Phase Fault with Stuck Breaker on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT33-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT45-SB | Single Phase Fault with Stuck Breaker on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT46-SB | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 19W | Normal | G1_FLT50-SB | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT1-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT2-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT3-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT4-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT5-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT6-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT7-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT8-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT9-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT10-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT12-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT13-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT14-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT15-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT16-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT17-3PH | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT18-3PH | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.3. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT19-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT20-3PH | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT21-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT22-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT23-3PH | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT26-3PH | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 (520893) 138.0 kV to EL RENO2 (520892) 69.0 kV to ELRNTERT (521167) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT43-3PH | 3 Phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT44-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.116 pu
Central | 01 - Woodward | 21L | Normal | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT46-3PH | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT47-3PH | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT48-3PH | 3 Phase fault on JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.4. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT49-3PH | 3 Phase fault on REDROCKRD4 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.2. HINTON 4 (511433) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21L | Normal | G1_FLT2-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT3-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT4-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT5-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT6-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT7-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT8-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT9-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT10-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT11-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT12-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT13-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT14-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT15-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT16-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT17-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT18-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT38-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT39-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT40-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT41-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT42-PO | Prior Outage: WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit 3 Phase Fault on WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit b.2. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT43-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT45-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT46-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT47-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT48-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT49-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT50-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.118 pu
Central | 01 - Woodward | 21L | Normal | G1_FLT51-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.118 pu
Central | 01 - Woodward | 21L | Normal | G1_FLT52-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.116 pu
Central | 01 - Woodward | 21L | Normal | G1_FLT53-PO | Prior Outage: MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT55-PO | Prior Outage: CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT5-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT6-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT7-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT10-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT14-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT15-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT16-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT17-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT18-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT19-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT20-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT21-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT22-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT23-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT28-SB | Single Phase Fault with Stuck Breaker on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT33-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT45-SB | Single Phase Fault with Stuck Breaker on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT46-SB | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21L | Normal | G1_FLT50-SB | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT1-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT2-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT3-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT4-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT5-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT6-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT7-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT8-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT9-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT10-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT12-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 01 - Woodward | 21S | Normal | G1_FLT13-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 01 - Woodward | 21S | Normal | G1_FLT14-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 01 - Woodward | 21S | Normal | G1_FLT15-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT16-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT17-3PH | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT18-3PH | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.3. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT19-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT20-3PH | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT21-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT22-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT23-3PH | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT26-3PH | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 (520893) 138.0 kV to EL RENO2 (520892) 69.0 kV to ELRNTERT (521167) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT43-3PH | 3 Phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT44-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT46-3PH | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT47-3PH | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT48-3PH | 3 Phase fault on JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.4. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT49-3PH | 3 Phase fault on REDROCKRD4 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.2. HINTON 4 (511433) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 523160: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT2-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT3-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT4-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT5-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT6-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT7-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT8-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT9-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT10-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT11-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT12-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT13-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT14-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT15-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT16-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT17-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT18-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT38-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT39-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT40-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT41-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT42-PO | Prior Outage: WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit 3 Phase Fault on WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit b.2. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT43-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT45-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT46-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT47-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT48-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 21S | Normal | G1_FLT49-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT50-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT51-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT52-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT53-PO | Prior Outage: MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT55-PO | Prior Outage: CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT5-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT6-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT7-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT10-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT14-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT15-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT16-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT17-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT18-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT19-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT20-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT21-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT22-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT23-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT28-SB | Single Phase Fault with Stuck Breaker on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT33-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT45-SB | Single Phase Fault with Stuck Breaker on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT46-SB | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 21S | Normal | G1_FLT50-SB | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT1-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT2-3PH | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT3-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT4-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT5-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT6-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT7-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT8-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT9-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT10-3PH | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT12-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 01 - Woodward | 28S | Normal | G1_FLT13-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 01 - Woodward | 28S | Normal | G1_FLT14-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 01 - Woodward | 28S | Normal | G1_FLT15-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT16-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT17-3PH | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT18-3PH | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit b.3. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT19-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT20-3PH | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT21-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT22-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT23-3PH | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT26-3PH | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 (520893) 138.0 kV to EL RENO2 (520892) 69.0 kV to ELRNTERT (521167) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT43-3PH | 3 Phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT44-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.111 pu
Central | 01 - Woodward | 28S | Normal | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT46-3PH | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT47-3PH | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT48-3PH | 3 Phase fault on JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.4. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT49-3PH | 3 Phase fault on REDROCKRD4 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.2. HINTON 4 (511433) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT2-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT3-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT4-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT5-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT6-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT7-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT8-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT9-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT10-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT11-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT12-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT13-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT14-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT15-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT16-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT17-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT18-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT38-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT39-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT40-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT41-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT42-PO | Prior Outage: WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit 3 Phase Fault on WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit b.2. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT43-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT45-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT46-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT47-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT48-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 01 - Woodward | 28S | Normal | G1_FLT49-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT50-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.111 pu
Central | 01 - Woodward | 28S | Normal | G1_FLT51-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.111 pu
Central | 01 - Woodward | 28S | Normal | G1_FLT52-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.111 pu
Central | 01 - Woodward | 28S | Normal | G1_FLT53-PO | Prior Outage: MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT55-PO | Prior Outage: CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT5-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT6-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT7-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT10-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT14-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT15-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT16-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT17-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT18-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT19-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT20-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT21-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT22-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT23-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT28-SB | Single Phase Fault with Stuck Breaker on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT33-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT45-SB | Single Phase Fault with Stuck Breaker on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT46-SB | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 01 - Woodward | 28S | Normal | G1_FLT50-SB | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
South | 02 - Hitchland | 21L | Base | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - GOODWELL_1 1[1] GOODWELL_2 1[1] GOODWELL_1 1[2] |  |  |  |  | GOODWELL_1 1[1] GOODWELL_2 1[1] GOODWELL_1 1[2] tripped on over voltage protection and FRISCO_WND 3[1] became Unstable. The voltage protection for GOODWELL units was disabled and the simulations were run. No further issues were observed.
South | 02 - Hitchland | 19W | Base | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 19W | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. OCEG units [#511939,511940,511942,511943] showed abnormal responses in post-fault period which is attributed to a modeling issue. Since this issue is observed in multiple contingencies in BC, SC and TC cases, it is reported once.
South | 02 - Hitchland | 21L | Base | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Sensitivity | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Base | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Sensitivity | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Base | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Sensitivity | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Base | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 19W | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Base | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Sensitivity | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Base | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Sensitivity | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Base | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Sensitivity | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Base | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Base | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Sensitivity | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated. GOODWELL_1 1[1] GOODWELL_1 1[2] GOODWELL_2 1[1] tripped on over voltage protection in the GNETed case. Voltage protection were disabled for these units and the simulation was repeated once again, no further issues were observed with the protection disabled. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Base | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Sensitivity | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Base | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Sensitivity | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Sensitivity | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. No mitigation action was performed in the sensitivity scenario for this contingency. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 02 - Hitchland | 19W | Transfer | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Unstable | NO | NO | NO | NO | NO | NO |  | Reduce output of GEN-2017-047 to 77MW |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. The dispatch of this unit is reduced to 77 MW (75% dispatch) and the simulation is repeated. No further issue is observed. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 02 - Hitchland | 21L | Sensitivity | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. No mitigation action was performed in the sensitivity scenario for this contingency. Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 02 - Hitchland | 21L | Transfer | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Unstable | NO | NO | NO | NO | NO | NO |  | Reduce output of GEN-2017-047 to 77MW |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. The dispatch of this unit is reduced to 77 MW (75% dispatch) and the simulation is repeated. No further issue is observed. Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 02 - Hitchland | 28S | Sensitivity | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. No mitigation action was performed in the sensitivity scenario for this contingency. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 02 - Hitchland | 28S | Transfer | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Unstable | NO | NO | NO | NO | NO | NO |  | Reduce output of GEN-2017-047 to 77MW |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. The dispatch of this unit is reduced to 77 MW (75% dispatch) and the simulation is repeated. No further issue is observed. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 02 - Hitchland | 19W | Base | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 19W | Transfer | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed.
South | 02 - Hitchland | 21L | Base | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Sensitivity | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Transfer | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Base | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Sensitivity | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Transfer | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Base | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Sensitivity | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Transfer | FLT_121_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Base | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Sensitivity | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Transfer | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - NOVUS_WND 1[1] LANOGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Base | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Sensitivity | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21L | Transfer | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Base | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Sensitivity | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 21S | Transfer | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Base | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Sensitivity | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 28S | Transfer | FLT_122_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO - LANOGSU10.60[W1] NOVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1] |  |  |  |  | NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disabled and the simulations were repeated, these generators went Unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC, SC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. No further simulation is done.
South | 02 - Hitchland | 19W | Sensitivity | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. No mitigation action was performed in the sensitivity scenario for this contingency. Voltage Spike: 1.21pu, MaxDur: 0.04s
South | 02 - Hitchland | 19W | Transfer | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | Reduce output of GEN-2017-047 to 77MW |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. The dispatch of this unit is reduced to 77 MW (75% dispatch) and the simulation is repeated. No further issue is observed. Voltage Spike: 1.21pu, MaxDur: 0.04s
South | 02 - Hitchland | 21L | Sensitivity | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 02 - Hitchland | 21L | Transfer | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | Reduce output of GEN-2017-047 to 77MW |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. The dispatch of this unit is reduced to 77 MW (75% dispatch) and the simulation is repeated. No further issue is observed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. No mitigation action was performed in the sensitivity scenario for this contingency. Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 02 - Hitchland | 28S | Transfer | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | Reduce output of GEN-2017-047 to 77MW |  |  | The studied contingency cuts the two 115kV lines at the project POI, leaving the GEN-2017-047 project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. The dispatch of this unit is reduced to 77 MW (75% dispatch) and the simulation is repeated. No further issue is observed. Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 02 - Hitchland | 19W | Base | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 523941[MAJSTC-WTG110.6900]1 and 523942[MAJSTC-WTG210.6900]1: These generating units showed sustained oscillatory responses under several contingencies in the BCs, TCs, and SCs. Since this issue is observed in the BC and does not impact the overall stability of the system, no further action was taken.
South | 02 - Hitchland | 19W | Sensitivity | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV transmission line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV transmission line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV transmission line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPEARMAN to HANSFORD 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Base | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Base | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Base | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV transmission line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - FRISCO_WND 3[1] |  |  |  |  | G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Base | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV transmission line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV transmission line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV transmission line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV transmission line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_32_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_33_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_34_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_35_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_36_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV transmission line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_37_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_38_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_39_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_40_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV transmission line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_41_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV transmission line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_42_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_43_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV transmission line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_44_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_45_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_46_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - ROOSWND-GEN2[2] G08-022-GEN3[1] |  |  |  |  | ROOSWND-GEN2[2] G08-022-GEN3[1] tripped on over voltage protection. The voltage protection were disabled and simulation was run. No further issues were observed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - ROOSWND-GEN2[2] G08-022-GEN3[1] |  |  |  |  | ROOSWND-GEN2[2] G08-022-GEN3[1] tripped on over voltage protection. The voltage protection were disabled and simulation was run. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - ROOSWND-GEN2[2] G08-022-GEN3[1] |  |  |  |  | ROOSWND-GEN2[2] G08-022-GEN3[1] tripped on over voltage protection. The voltage protection were disabled and simulation was run. No further issues were observed.
South | 02 - Hitchland | 21L | Base | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_47_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_48_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_49_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV transmission line CKT 1, near E-LIBER3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NLIB 3 to NATBEEF3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NLIB 3 to NATBEEF3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_50_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV transmission line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_51_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_52_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_54_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_55_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_56_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_57_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_58_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_59_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_60_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GOODWELL_1 1[1] GOODWELL_2 1[1] GOODWELL_1 1[2] |  |  |  |  | GOODWELL_1 1[1] GOODWELL_2 1[1] GOODWELL_1 1[2] tripped on over voltage. The voltage protection is disabled and the simulations were run. No further issues were observed. Voltage Spike: 3.87pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Base | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_61_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_62_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_63_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_64_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_65_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_66_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_67_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_68_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_69_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 21L | Base | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.22pu, MaxDur: 18.33s | Yes | NO - Max: 1.21pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.22pu, MaxDur: 18.33s | Yes | NO - Max: 1.21pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.24pu, MaxDur: 1.06s | Yes | NO - Max: 1.20pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.24pu, MaxDur: 1.07s | Yes | NO - Max: 1.20pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 28S | Base | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_70_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] tripped on over voltage protection. The protections were disabled and simulations were repeated. No further issues were observed.
South | 02 - Hitchland | 19W | Base | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.21pu, MaxDur: 18.48s | Yes | NO - Max: 1.21pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.21pu, MaxDur: 18.48s | Yes | NO - Max: 1.21pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.21pu, MaxDur: 1.56s | Yes | NO - Max: 1.20pu | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.21pu, MaxDur: 1.56s | Yes | NO - Max: 1.20pu | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_71_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_72_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_73_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_74_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_75_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_76_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_77_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_78_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_79_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_80_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_81_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_82_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_83_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_84_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_85_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_86_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_87_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_88_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_89_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.16pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_90_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_91_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.14pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_92_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open TXPHSF to E-LIBER3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_93_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open HITCHLAND to FRISCO_WND 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_94_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1.Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_95_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_96_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_97_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | NO - MaxV: 1.27pu, MaxDur: 18.74s | Yes | NO - Max: 1.23pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.78pu | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_98_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.78pu | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_99_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open COLE to OCHILTREE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_100_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_101_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_102_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Transmission Circuit. Simultaneously open TXFARMS to OCHILTREE 115kV transmission line CKT 1.Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_103_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV transmission line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted Transmission Circuit. Simultaneously open SPEARMAN to HANSFORD 115kV transmission line CKT 1.Simultaneously open OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding. Simultaneously open HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Sensitivity | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Transfer | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Base | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21L | Transfer | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Base | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Sensitivity | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 21S | Transfer | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Base | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_105_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted Transmission Circuit. Simultaneously open POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_106_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV transmission line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Transmission Circuit. Simultaneously open BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1.Simultaneously open BUSHLAND to DEAFSMITH 230kV transmission line CKT 1.Simultaneously open DS-#25+ to DEAFSMITH 115kV transmission line CKT 1.Simultaneously open RANDALL to CANYON_E_TP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_107_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted Transmission Circuit. Simultaneously open DS-#20 to CURRY 115kV transmission line CKT 1.Simultaneously open HEREFORD to DS-#6 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - CANEYWF12[1] |  |  |  |  | CANEYWF12[1]: Frequency protection at CANEYWF12[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Sensitivity | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - CANEYWF12[1] |  |  |  |  | CANEYWF12[1]: Frequency protection at CANEYWF12[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - CANEYWF12[1] |  |  |  |  | CANEYWF12[1]: Frequency protection at CANEYWF12[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Base | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_108_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV transmission line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open CASTRO_CNTY3 to BC-KELLEY +3 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to PLANT_X 115kV transmission line CKT 1.Simultaneously open MULSHVLY_TP3 to BAILEYCO 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_109_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV transmission line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted Transmission Circuit. Simultaneously open DEAFSMITH to PLANT_X 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.15pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_110_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_111_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_112_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_113_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_114_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_115_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_116_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV transmission line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_117_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV transmission line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_118_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_119_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV transmission line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_120_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_123_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_124_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_125_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COLE to TC-AGGIE 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COLE to TC-AGGIE 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_126_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | NO - Min: 0.78pu | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 02 - Hitchland | 21S | Transfer | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | NO - MaxV: 1.20pu, MaxDur: 0.60s | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_127_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV transmission line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV transmission line CKT 1, near COLE 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | NO - Min: 0.78pu | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Base | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Sensitivity | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 28S | Transfer | FLT_128_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV transmission line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV transmission line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV transmission line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 02 - Hitchland | 19W | Base | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Sensitivity | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21L | Base | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 02 - Hitchland | 21L | Sensitivity | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 02 - Hitchland | 21S | Base | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Sensitivity | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Base | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Sensitivity | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_129_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV transmission line CKT 1Prior Outage of HEREFORD to DS-#6 115kV transmission line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV transmission line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Normal | G3_FLT1-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT2-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT3-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT4-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT5-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT6-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT11-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT12-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT14-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT15-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT16-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT17-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT18-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT19-3PH | 3 Phase fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT20-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT21-3PH | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT22-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT23-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT24-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT25-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT36-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT37-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT38-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT40-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT41-3PH | 3 Phase fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT42-3PH | 3 Phase fault on PIONEER3 (531391) 115 kV Bus a. Apply fault at the PIONEER3 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT43-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT44-3PH | 3 Phase fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT45-3PH | 3 Phase fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT46-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT47-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT48-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 19W | Normal | G3_FLT50-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT52-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT53-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT54-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT55-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT57-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT58-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT59-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT60-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT61-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT62-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT63-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT64-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT65-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT66-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT67-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT68-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT69-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT70-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT71-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT72-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT73-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT74-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT75-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT76-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT77-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT78-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT79-3PH | 3 Phase fault on CLDWELL4 (539003) 138 kV Bus a. Apply fault at the CLDWELL4 (539003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLDWELL4 (539003) 138.0 kV Trip Bus b.2. MILAN_GOAB (539008) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT80-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT81-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT82-3PH | 3 Phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT83-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT84-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT85-3PH | 3 Phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT86-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT87-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT89-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT1-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT2-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 15 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.868 pu
Central | 03 - Spearville | 19W | Normal | G3_FLT4-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT5-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT6-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT7-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT8-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT9-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT10-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT11-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 19W | Normal | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 19W | Normal | G3_FLT14-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT15-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT16-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT17-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT18-PO | Prior Outage: SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT19-PO | Prior Outage: SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT20-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT21-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT22-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT23-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT24-PO | Prior Outage: KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT25-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT26-PO | Prior Outage: CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT27-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT28-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT29-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT30-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT31-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT32-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT33-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT34-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT35-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT36-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT37-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT39-PO | Prior Outage: PIONEER1 (531251) 13.8 kV to Trip Bus 3 Phase Fault on G17-052-TAP (588914) 115 kV Bus a. Apply fault at the G17-052-TAP (588914) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCRK3 (531473) 115.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT40-PO | Prior Outage: SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT41-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT42-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT43-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT44-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT46-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT47-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT51-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT52-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT53-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT54-PO | Prior Outage: ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | NO | NO | NO | NO | YES | NO |  |  |  |  | UNSOLVABLE IN BASE CASE AND TRANSFER CASE
Central | 03 - Spearville | 19W | Normal | G3_FLT56-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on ELMCREK6 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT57-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT58-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT59-PO | Prior Outage: MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit b.2. SETAB 7 (531465) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT61-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT65-PO | Prior Outage: HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit 3 Phase Fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT66-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT67-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT68-PO | Prior Outage: DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit 3 Phase Fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT69-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT70-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT71-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT72-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT73-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT1-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT2-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT3-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT4-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 19W | Normal | G3_FLT5-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT6-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT7-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT8-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT11-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.125 pu
Central | 03 - Spearville | 19W | Normal | G3_FLT13-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT20-SB | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT21-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 4 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.899 pu
Central | 03 - Spearville | 19W | Normal | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 21 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.852 pu
Central | 03 - Spearville | 19W | Normal | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT30-SB | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT31-SB | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT32-SB | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT34-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT35-SB | Single Phase Fault with Stuck Breaker on HARPER 4 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT36-SB | Single Phase Fault with Stuck Breaker on BARBER 3 (539760) 115 kV Bus a. Apply Fault at the BARBER 3 (539760) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT37-SB | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT42-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT43-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT44-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT45-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT47-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT48-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 19W | Normal | G3_FLT49-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT1-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT2-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT3-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT4-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT5-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT6-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT11-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT12-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT14-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT15-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT16-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT17-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT18-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT19-3PH | 3 Phase fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT20-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT21-3PH | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT22-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT23-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT24-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT25-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT36-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT37-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT38-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT40-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT41-3PH | 3 Phase fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT42-3PH | 3 Phase fault on PIONEER3 (531391) 115 kV Bus a. Apply fault at the PIONEER3 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT43-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT44-3PH | 3 Phase fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT45-3PH | 3 Phase fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT46-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21L | Normal | G3_FLT47-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT48-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21L | Normal | G3_FLT50-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT52-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT53-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT54-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT55-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT57-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT58-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT59-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT60-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT61-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT62-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT63-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT64-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT65-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT66-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT67-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT68-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21L | Normal | G3_FLT69-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT70-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT71-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT72-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT73-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT74-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT75-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT76-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT77-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT78-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT79-3PH | 3 Phase fault on CLDWELL4 (539003) 138 kV Bus a. Apply fault at the CLDWELL4 (539003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLDWELL4 (539003) 138.0 kV Trip Bus b.2. MILAN_GOAB (539008) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT80-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT81-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT82-3PH | 3 Phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT83-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT84-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT85-3PH | 3 Phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT86-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT87-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT89-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT1-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT2-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION |  |  |  |  | 16 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.878 pu
Central | 03 - Spearville | 21L | Normal | G3_FLT4-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT5-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT6-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT7-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT8-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT9-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT10-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT11-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21L | Normal | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21L | Normal | G3_FLT14-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT15-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT16-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.898 pu
Central | 03 - Spearville | 21L | Normal | G3_FLT17-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT18-PO | Prior Outage: SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT19-PO | Prior Outage: SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT20-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT21-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT22-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT23-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT24-PO | Prior Outage: KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT25-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT26-PO | Prior Outage: CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT27-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT28-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT29-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT30-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT31-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT32-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT33-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT34-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT35-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT36-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT37-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT39-PO | Prior Outage: PIONEER1 (531251) 13.8 kV to Trip Bus 3 Phase Fault on G17-052-TAP (588914) 115 kV Bus a. Apply fault at the G17-052-TAP (588914) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCRK3 (531473) 115.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT40-PO | Prior Outage: SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT41-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT42-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT43-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT44-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT46-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT47-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT51-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT52-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT53-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT54-PO | Prior Outage: ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | NO | NO | NO | NO | YES | NO |  |  |  |  | UNSOLVABLE IN BASE CASE AND TRANSFER CASE
Central | 03 - Spearville | 21L | Normal | G3_FLT56-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on ELMCREK6 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT57-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT58-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT59-PO | Prior Outage: MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit b.2. SETAB 7 (531465) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT61-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT65-PO | Prior Outage: HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit 3 Phase Fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT66-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT67-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT68-PO | Prior Outage: DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit 3 Phase Fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT69-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT70-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT71-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT72-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT73-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT1-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT2-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT3-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT4-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT5-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT6-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT7-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT8-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT11-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | NO 588633: MACHINE TRIPPED DUE TO UNKNOWN
Central | 03 - Spearville | 21L | Normal | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | NO | YES | NO 588633: MACHINE TRIPPED DUE TO UNKNOWN |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.102 pu
Central | 03 - Spearville | 21L | Normal | G3_FLT13-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT20-SB | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT21-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 8 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.885 pu
Central | 03 - Spearville | 21L | Normal | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT30-SB | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT31-SB | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT32-SB | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT34-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT35-SB | Single Phase Fault with Stuck Breaker on HARPER 4 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT36-SB | Single Phase Fault with Stuck Breaker on BARBER 3 (539760) 115 kV Bus a. Apply Fault at the BARBER 3 (539760) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT37-SB | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT42-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT43-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT44-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT45-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT47-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT48-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21L | Normal | G3_FLT49-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT1-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT2-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT3-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT4-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT5-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT6-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT11-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT12-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT14-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT15-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT16-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT17-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT18-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT19-3PH | 3 Phase fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT20-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT21-3PH | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT22-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT23-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT24-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT25-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT36-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT37-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT38-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT40-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT41-3PH | 3 Phase fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT42-3PH | 3 Phase fault on PIONEER3 (531391) 115 kV Bus a. Apply fault at the PIONEER3 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT43-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT44-3PH | 3 Phase fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT45-3PH | 3 Phase fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT46-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT47-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT48-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21S | Normal | G3_FLT50-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT52-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT53-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT54-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT55-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT57-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT58-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT59-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT60-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT61-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT62-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT63-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT64-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT65-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT66-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT67-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT68-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT69-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT70-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT71-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT72-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT73-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT74-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT75-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT76-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT77-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT78-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT79-3PH | 3 Phase fault on CLDWELL4 (539003) 138 kV Bus a. Apply fault at the CLDWELL4 (539003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLDWELL4 (539003) 138.0 kV Trip Bus b.2. MILAN_GOAB (539008) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT80-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT81-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT82-3PH | 3 Phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT83-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT84-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT85-3PH | 3 Phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT86-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT87-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT89-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT1-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT2-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.885 pu
Central | 03 - Spearville | 21S | Normal | G3_FLT4-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT5-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT6-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT7-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT8-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT9-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT10-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT11-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21S | Normal | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 21S | Normal | G3_FLT14-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT15-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT16-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT17-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT18-PO | Prior Outage: SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT19-PO | Prior Outage: SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT20-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT21-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT22-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT23-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT24-PO | Prior Outage: KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT25-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT26-PO | Prior Outage: CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT27-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT28-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT29-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT30-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT31-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT32-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT33-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT34-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT35-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT36-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT37-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT39-PO | Prior Outage: PIONEER1 (531251) 13.8 kV to Trip Bus 3 Phase Fault on G17-052-TAP (588914) 115 kV Bus a. Apply fault at the G17-052-TAP (588914) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCRK3 (531473) 115.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT40-PO | Prior Outage: SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT41-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT42-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT43-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT44-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT46-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT47-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT51-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT52-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT53-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT54-PO | Prior Outage: ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | NO | NO | NO | NO | YES | NO |  |  |  |  | UNSOLVABLE IN BASE CASE AND TRANSFER CASE
Central | 03 - Spearville | 21S | Normal | G3_FLT56-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on ELMCREK6 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT57-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT58-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT59-PO | Prior Outage: MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit b.2. SETAB 7 (531465) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT61-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT65-PO | Prior Outage: HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit 3 Phase Fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT66-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT67-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT68-PO | Prior Outage: DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit 3 Phase Fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT69-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT70-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT71-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT72-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT73-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT1-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT2-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT3-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT4-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT5-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT6-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT7-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT8-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT11-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.127 pu
Central | 03 - Spearville | 21S | Normal | G3_FLT13-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT20-SB | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT21-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.879 pu
Central | 03 - Spearville | 21S | Normal | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT30-SB | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT31-SB | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT32-SB | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT34-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT35-SB | Single Phase Fault with Stuck Breaker on HARPER 4 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT36-SB | Single Phase Fault with Stuck Breaker on BARBER 3 (539760) 115 kV Bus a. Apply Fault at the BARBER 3 (539760) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT37-SB | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT42-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT43-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT44-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT45-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT47-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT48-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 21S | Normal | G3_FLT49-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT1-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT2-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT3-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT4-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT5-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT6-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT11-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT12-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | 4 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.783 pu
Central | 03 - Spearville | 28S | Normal | G3_FLT14-3PH | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT15-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT16-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT17-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT18-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT19-3PH | 3 Phase fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT20-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT21-3PH | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT22-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT23-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT24-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT25-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT36-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT37-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT38-3PH | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT40-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT41-3PH | 3 Phase fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT42-3PH | 3 Phase fault on PIONEER3 (531391) 115 kV Bus a. Apply fault at the PIONEER3 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT43-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT44-3PH | 3 Phase fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT45-3PH | 3 Phase fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT46-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT47-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT48-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 28S | Normal | G3_FLT50-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT52-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT53-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT54-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT55-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT57-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT58-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT59-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT60-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT61-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT62-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT63-3PH | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT64-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT65-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT66-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT67-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT68-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT69-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT70-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT71-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT72-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT73-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT74-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT75-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT76-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT77-3PH | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT78-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT79-3PH | 3 Phase fault on CLDWELL4 (539003) 138 kV Bus a. Apply fault at the CLDWELL4 (539003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLDWELL4 (539003) 138.0 kV Trip Bus b.2. MILAN_GOAB (539008) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT80-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT81-3PH | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT82-3PH | 3 Phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT83-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT84-3PH | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT85-3PH | 3 Phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT86-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT87-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT89-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT1-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT2-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 03 - Spearville | 28S | Normal | G3_FLT4-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 03 - Spearville | 28S | Normal | G3_FLT5-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT6-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT7-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT8-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT9-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT10-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT11-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 28S | Normal | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 03 - Spearville | 28S | Normal | G3_FLT14-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT15-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT16-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT17-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT18-PO | Prior Outage: SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT19-PO | Prior Outage: SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV ThreeWinding 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT20-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT21-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT22-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT23-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT24-PO | Prior Outage: KEYSTON3 (640252) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT25-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT26-PO | Prior Outage: CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT27-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT28-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT29-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT30-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT31-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT32-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT33-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT34-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT35-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT36-PO | Prior Outage: HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT37-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT39-PO | Prior Outage: PIONEER1 (531251) 13.8 kV to Trip Bus 3 Phase Fault on G17-052-TAP (588914) 115 kV Bus a. Apply fault at the G17-052-TAP (588914) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCRK3 (531473) 115.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT40-PO | Prior Outage: SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT41-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT42-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on JOHNCR 3 (531424) 115 kV Bus a. Apply fault at the JOHNCR 3 (531424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCR 3 (531424) 115.0 kV to G17-052-TAP (588914) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT43-PO | Prior Outage: FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT44-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on SYRACUS3 (531437) 115 kV Bus a. Apply fault at the SYRACUS3 (531437) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SYRACUS3 (531437) 115.0 kV to TRIBUNE3 (531439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT46-PO | Prior Outage: PK_GOAB3 (531400) 115.0 kV to Trip Bus 3 Phase Fault on PIONEER2 (531390) 69 kV Bus a. Apply fault at the PIONEER2 (531390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER1 (531251) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT47-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT51-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT52-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT53-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT54-PO | Prior Outage: ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | NO | NO | NO | NO | YES | NO |  |  |  |  | UNSOLVABLE IN BASE CASE AND TRANSFER CASE
Central | 03 - Spearville | 28S | Normal | G3_FLT56-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on ELMCREK6 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT57-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT58-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT59-PO | Prior Outage: MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit b.2. SETAB 7 (531465) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT61-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT65-PO | Prior Outage: HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit 3 Phase Fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT66-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT67-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT68-PO | Prior Outage: DGRASSE4 (515853) 138.0 kV to RSVLYSW4 (520529) 138.0 kV Transmission Circuit 3 Phase Fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT69-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT70-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT71-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT72-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT73-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT1-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT2-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV ThreeWinding b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT3-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT4-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT5-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT6-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT7-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT8-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT11-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | NO | YES | YES |  |  |  |  | 1 BUS/BUSES ABOVE 1.1 pu. HIGHEST VOLTAGE 1.123 pu
Central | 03 - Spearville | 28S | Normal | G3_FLT13-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT20-SB | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT21-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 7 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 03 - Spearville | 28S | Normal | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 4 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.889 pu
Central | 03 - Spearville | 28S | Normal | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT30-SB | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT31-SB | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT32-SB | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT34-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT35-SB | Single Phase Fault with Stuck Breaker on HARPER 4 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT36-SB | Single Phase Fault with Stuck Breaker on BARBER 3 (539760) 115 kV Bus a. Apply Fault at the BARBER 3 (539760) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT37-SB | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT42-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT43-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT44-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT45-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT47-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT48-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 03 - Spearville | 28S | Normal | G3_FLT49-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21L | Normal | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | Yes | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Normal | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 533761 [GIRARD 2 69.000] '6' tripped at 1.45s , (first swing) | remove high speed reclose
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 533761 [GIRARD 2 69.000] '7' tripped at 1.45s, (first swing) | remove high speed reclose
North | 04 - Northwest Kansas | 21S | Normal | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 640010 [GENTLM1G 23.000] '1' tripped at 1.93s (first swing) | remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 640010 [GENTLM1G 23.000] '1' tripped at 1.93s (first swing) | remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 530675 [GMECG2 1 13.800] '10' tripped at 1.61s , 530675 [GMECG2 1 13.800] '7' tripped at 1.62s (first swing) | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 533761 [GIRARD 2 69.000] '6' tripped at 1.45s , (first swing) | remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | Yes | 533761 [GIRARD 2 69.000] '7' tripped at 1.45s, (first swing) | remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Normal | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 19W | Normal | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 are tripped. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 19W | Normal | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-065, G16-067 are tripped. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 19W | Normal | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | Yes | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 19W | Normal | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21L | Normal | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21L | Normal | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-065, G16-067 are tripped. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21L | Normal | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Normal | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle Unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Normal | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21S | Normal | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21S | Normal | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 21S | Normal | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle Unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Normal | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 28S | Normal | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle Unstable (first swing) and get tripped | Remove high speed reclose. Set breaker trip to 3.75 cycles.
North | 04 - Northwest Kansas | 28S | Normal | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post prior outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 28S | Normal | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | Curtail Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post prior outage in anticipation of contingencies in the system.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed in the G6 region. Since, the issue was observed in the BC, it is considered pre-existing issue and no mitigation solution was evaluated for this contingency for this case.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed in the G6 region. Since, the issue was observed in the BC, it is considered pre-existing issue and no mitigation solution was evaluated for this contingency for this case.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed in the G6 region. Since, the issue was observed in the BC, it is considered pre-existing issue and no mitigation solution was evaluated for this contingency for this case.
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed in the G6 region. Since, the issue was observed in the BC, it is considered pre-existing issue and no mitigation solution was evaluated for this contingency for this case.
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed in the G6 region. Since, the issue was observed in the BC, it is considered pre-existing issue and no mitigation solution was evaluated for this contingency for this case.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed in the G6 region. Since, the issue was observed in the BC, it is considered pre-existing issue and no mitigation solution was evaluated for this contingency for this case.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.15pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.15pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.15pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.17pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_9_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_10_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_11_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_12_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_13_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_14_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_15_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_16_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_17_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV transmission line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_18_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G08-022-GEN3[1] |  |  |  |  | G08-022-GEN3[1] tripped on over-voltage protection setting. The protection setting was disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G08-022-GEN3[1] |  |  |  |  | G08-022-GEN3[1] tripped on over-voltage protection setting. The protection setting was disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_19_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_20_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_21_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_22_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_23_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.53pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.53pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.51pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.52pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.52pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.52pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.51pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.52pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_24_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.52pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | OCEG units [#511939,511940,511942,511943] showed abnormal responses in the post-fault period which is attributed to a modeling issue. Since this issue is observed in multiple contingencies in BCs, TCs and SCs, it is reported once.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | ROOSWND-GEN and G08-022-GEN3 with Vestas user models showed sustained oscillatory responses in the system. This issue was observed in the BC, TC and SC. Hence, it was not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | ROOSWND-GEN and G08-022-GEN3 with Vestas user models showed sustained oscillatory responses in the system. This issue was observed in the BC, TC and SC. Hence, it was not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | ROOSWND-GEN and G08-022-GEN3 with Vestas user models showed sustained oscillatory responses in the system. This issue was observed in the BC, TC and SC. Hence, it was not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | ROOSWND-GEN and G08-022-GEN3 with Vestas user models showed sustained oscillatory responses in the system. This issue was observed in the BC, TC and SC. Hence, it was not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | G08-022-GEN3 with Vestas user models showed sustained oscillatory responses in the system. This issue was observed in the BC, TC and SC. Hence, it was not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_25_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | G08-022-GEN3 with Vestas user models showed sustained oscillatory responses in the system. This issue was observed in the BC, TC and SC. Hence, it was not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_26_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_27_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_28_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_29_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_30_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_31_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_32_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-045-GEN1[1] |  |  |  |  | G16-045-GEN1[1] tripped on voltage protection setting. Since this trip happened only in the BC, no further action was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_33_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_34_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_35_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_36_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-045-GEN1[1] |  |  |  |  | G16-045-GEN1[1] tripped on voltage protection setting. Since this trip happened only in the BC, no further action was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_37_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_38_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_39_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_40_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_41_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_42_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_43_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_44_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_45_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_46_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_47_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_48_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_49_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_50_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator. Simultaneously open SWISHER to TUCO_INT 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_51_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to JONES 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_52_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV transmission line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Transmission Circuit. Simultaneously open TUCO_INT to CARLISLE 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_53_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_54_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_55_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_56_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_57_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding. Simultaneously open TOLK to CROSSROADS 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_58_P4_CRAWFISH_DR | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open CRAWFISH_DR 345kV/765kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_59_P4_CRAWFISH_DR | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 1, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Two Winding. Simultaneously open TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_60_P4_CRAWFISH765 | Apply single-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH765 765kV for 16 cycles with stuck breaker at CRAWFISH765 . Open the faulted Two Winding. Simultaneously open CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_61_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit. Simultaneously open BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_62_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device Prior Outage of DC line SPP_44_OKLUNApply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_63_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_64_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_65_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_66_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_67_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_68_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_69_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_70_P6_OKU-7 | Prior Outage of BORDER shunt device Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_71_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_72_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV transmission line CKT 1Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV transmission line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_73_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_74_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_75_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_76_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV transmission line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_77_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 06 - South Texas Panhandle/New Mexico | 19W | Base | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Sensitivity | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Base | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Sensitivity | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Base | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Sensitivity | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Base | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Sensitivity | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_78_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV transmission line CKT 1Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: Abnormal oscillations were observed for these units under numerous contingencies across all cases. This issue was observed also in the original Study and was identified as a potential modeling issue. Since this issue is observed in many contingencies it's reported once.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.87pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.87pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.85pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.84pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.85pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV transmission line CKT 1, near HOB-JCT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOB-JCT2 to HOBART-2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOB-JCT2 to HOBART-2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV transmission line CKT 1, near SNYDER-2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VRNMTAP2 to VERNON 2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VRNMTAP2 to VERNON 2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 511939[OECGT1-1],511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These have shown abnormal fluctuations in the post-contingency period in BC, SC and TC for several contingencies across all cases. This observation is consistent with the original DSIS and was identified as a modeling issue.
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.28pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.85pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.84pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG], 520522[BCVI_WTG1], 511939[OECGT1-1], 511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These units have shown abnormal fluctuations and caused oscillations in the system in the post-fault period under several contingencies across all the cases. This observation is consistent with the original DSIS and is identified as a modeling issue.
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.90pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG], 520522[BCVI_WTG1], 511939[OECGT1-1], 511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These units have shown abnormal fluctuations and caused oscillations in the system in the post-contingency period under several contingencies across all the cases. This observation is consistent with the original DSIS and is identified as a modeling issue.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.87pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG], 520522[BCVI_WTG1], 511939[OECGT1-1], 511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These units have shown abnormal fluctuations and caused oscillations in the system in the post-contingency period under several contingencies across all the cases. This observation is consistent with the original DSIS and is identified as a modeling issue.
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV transmission line CKT 1, near ANADARK4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-close CORNVIL4 to CORN TP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open NAPLSTP4 to CORN TP4 138kV transmission line CKT 1.Simultaneously re-open CORNVIL4 to CORN TP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_38_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV transmission line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_39_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_40_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_41_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_42_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_43_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_44_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_45_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_46_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV transmission line CKT 1, near CACHEJ4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.54pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.50pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.52pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.51pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.49pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.50pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.49pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_47_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.49pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_48_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_49_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV transmission line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.36pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.37pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.39pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_50_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_51_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_52_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_53_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_54_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_55_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line.Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_56_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_57_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_58_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_59_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_60_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_61_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_62_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_63_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_64_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.85pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | NO - 032204201651[1 ] |  |  |  |  | 032204201651[1 ]: The generation unit at bus 511975 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No stability issues was observed. However, 520519[BCI WTG, 520520[BCII WTG], 520522[BCVI_WTG1], 511939[OECGT1-1], 511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2] showed abnormal fluctuations and caused oscillations in the system in the post-contingency period under several contingencies across all the cases. When BC units (#520519, 520520, 520521, 520522) are GNETed and the simulation is repeated no further issue is observed. Post fault ss voltage: Min: 0.81pu
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.90pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | NO - Min: 0.90pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_65_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_66_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | NO - MaxV: 1.66pu, MaxDur: 0.33s | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_67_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_68_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1] |  |  |  |  | GW_WTG11[1] GW_WTG21[1] CB_WTG1[1] CB_WTG2[1]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_69_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_70_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_71_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_72_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_73_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_74_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_75_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_76_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_77_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_78_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_79_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_80_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_81_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_82_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_83_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_84_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_85_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_86_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding. Simultaneously open SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_87_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_88_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Transmission Circuit. Simultaneously open SNYDER-4 to SNYDER 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_89_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV transmission line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_90_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV transmission line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Transmission Circuit. Simultaneously open ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1.Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_91_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding. Simultaneously open HEADRIK2 to SNYDER-2 69kV transmission line CKT 1.Simultaneously open ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1.Simultaneously open HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_92_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding. Simultaneously open LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_93_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_94_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_95_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted Transmission Circuit. Simultaneously open LWS-NTP4 to 112GORE4 138kV transmission line CKT 1.Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_96_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted Transmission Circuit. Simultaneously open ELKCITY6 to CHISHOLM6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_97_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open NORTWST7 to CIMARON7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_98_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding. Simultaneously open CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_99_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV transmission line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Transmission Circuit. Simultaneously open CIMARON7 to MATHWSN7 345kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.87pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_100_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted Transmission Circuit. Simultaneously open GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_101_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV transmission line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted Transmission Circuit. Simultaneously open GRACMNT4 to WASHITA4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_102_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted Transmission Circuit. Simultaneously open NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_103_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV transmission line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted Transmission Circuit. Simultaneously open FREDRIK2 to HOLLSTR2 69kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_104_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV transmission line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted Transmission Circuit. Simultaneously open SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_105_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV transmission line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_106_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_107_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV transmission line CKT 1, near COMANC-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-close DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open COMANC-4 to COMMTAP4 138kV transmission line CKT 1.Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_108_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_109_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV transmission line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_110_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV transmission line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV transmission line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_111_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV transmission line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV transmission line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV transmission line CKT 1, near 112GORE4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close L.E.S.-4 to SHERID4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open L.E.S.-4 to SHERID4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.40pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.40pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.44pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.40pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. LANOGSU10.60[W1] tripped on undervoltage protection. Due to size and location of the unit no further simulation was performed. Voltage Spike: 1.40pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_112_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | NO - Min: 0.79pu | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.07s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.39pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_113_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.38pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_114_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | NO - Min: 0.90pu | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.40pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.39pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | NO - MaxV: 1.42pu, MaxDur: 0.20s | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.40pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.40pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_115_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | NO - MaxV: 1.42pu, MaxDur: 0.33s | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.05s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_116_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | NO - MaxV: 1.38pu, MaxDur: 0.21s | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | NO - MaxV: 1.42pu, MaxDur: 0.34s | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | NO - MaxV: 1.37pu, MaxDur: 0.27s | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed.
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. Voltage Spike: 1.39pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_117_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.84pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated.
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.90pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated. Voltage Spike: 1.41pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.78pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.76pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1] and OECG (511939): These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated.
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.78pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1] and OECG (511939):These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated. Voltage Spike: 1.39pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.87pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]:These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated. Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.87pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_118_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.80pu | Yes | Yes | Yes |  |  |  |  | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated.
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_119_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV transmission line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_120_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV transmission line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV transmission line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.87pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_121_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV transmission line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV transmission line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.88pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.76pu | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. However, 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: These units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated. Voltage Spike: 1.33pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.76pu | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. However, 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1] units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated. Voltage Spike: 1.34pu, MaxDur: 0.04s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.37pu, MaxDur: 0.09s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. However, 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1] units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated.
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.89pu | Yes | Yes | Yes |  |  |  |  | The N-1 power flow case could not be solved. The sensitivity Case was redispatched for less MW in the area to achieve a power flow solution under the N-1 condition (sensitivity units SWS were switched off - total 660.6 MW). No stability issues were observed. However, 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1] units have caused abnormal oscillations in the system during the post fault period. To confirm this, these units were GNETed and the simulation was repeated. It was observed that the system oscillations were mitigated.
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_122_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV transmission line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.90pu | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.46pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.45pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.45pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_123_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.39pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.38pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_124_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.38pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 19W | Base | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 19W | Sensitivity | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 19W | Transfer | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Base | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21L | Sensitivity | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.42pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21L | Transfer | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.45pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Base | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 21S | Sensitivity | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 21S | Transfer | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.40pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 28S | Base | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 07 - Sotuhwestern Oklahoma | 28S | Sensitivity | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.41pu, MaxDur: 0.03s
South | 07 - Sotuhwestern Oklahoma | 28S | Transfer | FLT_125_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV transmission line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV transmission line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV transmission line CKT 1, near TAP_G17-036 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close 112GORE4 to LAIRGST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open 112GORE4 to LAIRGST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.03s
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT1-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT2-3PH | 3 Phase fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT3-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT4-3PH | 3 Phase fault on LITCH 5 (532932) 161 kV Bus a. Apply fault at the LITCH 5 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.886 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT7-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT9-3PH | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT10-3PH | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT11-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT13-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT15-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT17-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT18-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT19-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT20-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT22-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT23-3PH | 3 Phase fault on MARMATN2 (533639) 69 kV Bus a. Apply fault at the MARMATN2 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN1 (532955) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT24-3PH | 3 Phase fault on FRANKLIN2 (533876) 69 kV Bus a. Apply fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN1 (533122) 12.5 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 7 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.887 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT26-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT27-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT28-3PH | 3 Phase fault on G17-022-TAP (588664) 138 kV Bus a. Apply fault at the G17-022-TAP (588664) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT29-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT30-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT31-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT33-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT34-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT35-3PH | 3 Phase fault on MONTGOM4 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT36-3PH | 3 Phase fault on ALTOO W2 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO1 1 (533086) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT37-3PH | 3 Phase fault on ALTOO E2 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO3 1 (533087) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT38-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT39-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT40-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT41-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT42-3PH | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT43-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT44-3PH | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT45-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT46-3PH | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT48-3PH | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT50-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT51-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT52-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT53-3PH | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT55-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT56-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT57-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT59-3PH | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT60-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT61-3PH | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to 5ANO% (337912) 161.0 kV to 1ANO AUX (337913) 22.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT62-3PH | 3 Phase fault on FTSMITH8 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT63-3PH | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT64-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT65-3PH | 3 Phase fault on GERALDGAY5 (512760) 161 kV Bus a. Apply fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT66-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT67-3PH | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT68-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT69-3PH | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT70-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT71-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT72-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT73-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT74-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT75-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT76-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT77-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT78-3PH | 3 Phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT79-3PH | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT80-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT90-3PH | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-112-TAP (587894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT92-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT94-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT99-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT100-3PH | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT101-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT102-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT103-3PH | 3 Phase fault on CUSHING2 (515032) 69 kV Bus a. Apply fault at the CUSHING2 (515032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING2 (515032) 69.0 kV to CUSHING4 (515033) 138.0 kV to CUSHING1 (515718) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT104-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV2 (515021) 69.0 kV to GRNWOOD2 (515416) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT105-3PH | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 (515514) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit b.2. KNIPE 4 (515514) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT106-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to PAYNESB4 (515039) 138.0 kV Transmission Circuit b.2. PAYNESB4 (515039) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT107-3PH | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 (515047) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT108-3PH | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 (509758) 138.0 kV to BLUEBEL4 (515242) 138.0 kV Transmission Circuit b.2. PRATTV-4 (509758) 138.0 kV to S.S.---4 (509815) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT109-3PH | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 (515237) 138.0 kV to BEELINE4 (515247) 138.0 kV Transmission Circuit b.2. POLECTP4 (515218) 138.0 kV to TIBBENS4 (515237) 138.0 kV Transmission Circuit b.3. POLECTP4 (515218) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit b.4. BLUEBEL4 (515242) 138.0 kV to BOWDEN 4 (515243) 138.0 kV Transmission Circuit b.5. POLECTP4 (515218) 138.0 kV to POLECAT4 (515219) 138.0 kV Transmission Circuit b.6. BOWDEN 4 (515243) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT110-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 (515233) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit b.2. BRISTOW4 (515035) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT111-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to KEYWEST4 (515048) 138.0 kV Transmission Circuit b.2. KEYWEST4 (515048) 138.0 kV to BELLCOW4 (515369) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT116-3PH | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT117-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT118-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT119-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT120-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT122-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit b.2. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT123-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT124-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT125-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT126-3PH | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT127-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT128-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE1-1 (510368) 13.8 kV to GROVE 4 (510402) 138.0 kV to GROVE 5 (510411) 161.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT129-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to COWSKIN 4 (512719) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT130-3PH | 3 Phase fault on KERR GR3 (512634) 115 kV Bus a. Apply fault at the KERR GR3 (512634) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit b.2. LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit b.3. LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT131-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 (510387) 69.0 kV to VINITA-2 (510404) 69.0 kV Transmission Circuit b.2. ADAIR--2 (510387) 69.0 kV to PRY-JCT2 (510400) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT132-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 (510400) 69.0 kV to PRYORC12 (512810) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT133-3PH | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT134-3PH | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.3. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit b.4. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.5. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.6. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit b.7. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT135-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 (509779) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.2. MINGO-N4 (509760) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit b.3. LLAN ET4 (509771) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.4. LLAN ET4 (509771) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit b.5. MINGO-N4 (509760) 138.0 kV to MAYO--N4 (509779) 138.0 kV Transmission Circuit b.6. T.S.E.-4 (509811) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT136-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT137-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to 141PINE4 (509892) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT138-3PH | 3 Phase fault on PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit b.2. CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit b.3. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT139-3PH | 3 Phase fault on TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 (509835) 138.0 kV to VERDIGS4 (509854) 138.0 kV Transmission Circuit b.2. CLARTOK4 (509864) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit b.3. VERDIGS4 (509854) 138.0 kV to CLARTOK4 (509864) 138.0 kV Transmission Circuit b.4. CATOOSA4 (509790) 138.0 kV to TERNITP4 (509835) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT140-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT141-3PH | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT142-3PH | 3 Phase fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT151-3PH | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT162-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT165-3PH | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT168-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT170-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT171-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT172-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT174-3PH | 3 Phase fault on MILANTP4 (539675) 138 kV Bus a. Apply fault at the MILANTP4 (539675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILANTP4 (539675) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT1-PO | Prior Outage: N345 1 1 (532824) 13.8 kV to Trip Bus 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT2-PO | Prior Outage: FRANKLIN1 (533122) 12.5 kV to Trip Bus 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 3 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.828 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT4-PO | Prior Outage: MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT5-PO | Prior Outage: MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT11-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT12-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT14-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT15-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT16-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT17-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT18-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT19-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT21-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT22-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT23-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT24-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT25-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT26-PO | Prior Outage: BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT27-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT28-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT29-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT30-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT31-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 7 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT33-PO | Prior Outage: C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT34-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT35-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT36-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT37-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT38-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT39-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT40-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT42-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT43-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT44-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT45-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT46-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT47-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT48-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT49-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT50-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT51-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT52-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT53-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT54-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT55-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT56-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT57-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT58-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT59-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT60-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT61-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT62-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT63-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT64-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT65-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT66-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT67-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT68-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT69-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT70-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT72-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT73-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT74-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT75-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT76-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT77-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 578533: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT81-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT83-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT85-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT89-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT90-PO | Prior Outage: GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT91-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT92-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT93-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT94-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT95-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT96-PO | Prior Outage: 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT97-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT98-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT99-PO | Prior Outage: MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT100-PO | Prior Outage: 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT101-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT102-PO | Prior Outage: PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT103-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT104-PO | Prior Outage: PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT105-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT106-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT107-PO | Prior Outage: MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT108-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT109-PO | Prior Outage: L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT110-PO | Prior Outage: INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT112-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT113-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT114-PO | Prior Outage: CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT115-PO | Prior Outage: PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 585303: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 587463: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 587466: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 588193: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 18 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.828 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515900: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515900: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION 584173: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 587483: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 587486: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515900: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT125-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT126-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT127-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT128-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.9 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT134-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.898 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT135-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT136-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 7 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.889 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT138-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 7 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.883 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT143-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT147-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT160-PO | Prior Outage: PECANCK7 (515235) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit 3 Phase Fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT161-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT162-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.874 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT163-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.898 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT164-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT165-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT166-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT170-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT179-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT180-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT182-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT183-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT184-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT188-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.88 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT189-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.88 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT190-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.88 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT191-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.88 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT194-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW AND WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.89 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT195-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW AND WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.89 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT196-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT197-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT198-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.89 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT199-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.887 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT200-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT201-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT202-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.89 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT203-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.886 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT204-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT205-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT206-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT207-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT208-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT1-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT2-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT5-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT6-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT7-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT8-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT9-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT10-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT11-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV ThreeWinding b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT12-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT13-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV ThreeWinding b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT14-SB | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT15-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT16-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT17-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV TwoWinding b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT19-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT20-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT21-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT22-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT23-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT24-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT25-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT26-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT27-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT28-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT29-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT30-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT31-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT32-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT42-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT43-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT45-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT46-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV ThreeWinding b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT47-SB | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit b.2. CHAMSPR1 (506919) 13.8 kV to CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT48-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT49-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT50-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT51-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT52-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT53-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT54-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT55-SB | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT56-SB | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT58-SB | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT59-SB | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT60-SB | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT61-SB | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT62-SB | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT63-SB | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT64-SB | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.86 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT76-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit b.2. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT77-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding b.2. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT78-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT79-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT85-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV ThreeWinding b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT86-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-061-TAP (560084) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT91-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT92-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT93-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT94-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT96-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 7 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.887 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT99-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT100-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT101-SB | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT102-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT103-SB | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT104-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT105-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT108-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 4 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.866 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT109-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 3 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.882 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT110-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.886 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT111-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.898 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT112-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT113-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 23 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.828 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT115-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT116-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT117-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT118-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT120-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT121-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT122-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT123-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT124-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT125-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT126-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT127-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 19W | Normal | G8_FLT128-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT1-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT2-3PH | 3 Phase fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT3-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT4-3PH | 3 Phase fault on LITCH 5 (532932) 161 kV Bus a. Apply fault at the LITCH 5 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT7-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT9-3PH | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT10-3PH | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT11-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT13-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT15-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT17-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT18-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT19-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT20-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT22-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT23-3PH | 3 Phase fault on MARMATN2 (533639) 69 kV Bus a. Apply fault at the MARMATN2 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN1 (532955) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT24-3PH | 3 Phase fault on FRANKLIN2 (533876) 69 kV Bus a. Apply fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN1 (533122) 12.5 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT26-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT27-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT28-3PH | 3 Phase fault on G17-022-TAP (588664) 138 kV Bus a. Apply fault at the G17-022-TAP (588664) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT29-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT30-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT31-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT33-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT34-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT35-3PH | 3 Phase fault on MONTGOM4 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT36-3PH | 3 Phase fault on ALTOO W2 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO1 1 (533086) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT37-3PH | 3 Phase fault on ALTOO E2 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO3 1 (533087) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT38-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT39-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT40-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT41-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT42-3PH | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT43-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT44-3PH | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT45-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT46-3PH | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT48-3PH | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT50-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT51-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT52-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT53-3PH | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT55-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT56-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT57-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT59-3PH | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT60-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT61-3PH | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to 5ANO% (337912) 161.0 kV to 1ANO AUX (337913) 22.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT62-3PH | 3 Phase fault on FTSMITH8 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT63-3PH | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT64-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT65-3PH | 3 Phase fault on GERALDGAY5 (512760) 161 kV Bus a. Apply fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT66-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT67-3PH | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT68-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT69-3PH | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT70-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT71-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT72-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT73-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT74-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT75-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT76-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT77-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT78-3PH | 3 Phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT79-3PH | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT80-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT90-3PH | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-112-TAP (587894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT92-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT94-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT99-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT100-3PH | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT101-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT102-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT103-3PH | 3 Phase fault on CUSHING2 (515032) 69 kV Bus a. Apply fault at the CUSHING2 (515032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING2 (515032) 69.0 kV to CUSHING4 (515033) 138.0 kV to CUSHING1 (515718) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT104-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV2 (515021) 69.0 kV to GRNWOOD2 (515416) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT105-3PH | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 (515514) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit b.2. KNIPE 4 (515514) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT106-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to PAYNESB4 (515039) 138.0 kV Transmission Circuit b.2. PAYNESB4 (515039) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT107-3PH | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 (515047) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT108-3PH | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 (509758) 138.0 kV to BLUEBEL4 (515242) 138.0 kV Transmission Circuit b.2. PRATTV-4 (509758) 138.0 kV to S.S.---4 (509815) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT109-3PH | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 (515237) 138.0 kV to BEELINE4 (515247) 138.0 kV Transmission Circuit b.2. POLECTP4 (515218) 138.0 kV to TIBBENS4 (515237) 138.0 kV Transmission Circuit b.3. POLECTP4 (515218) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit b.4. BLUEBEL4 (515242) 138.0 kV to BOWDEN 4 (515243) 138.0 kV Transmission Circuit b.5. POLECTP4 (515218) 138.0 kV to POLECAT4 (515219) 138.0 kV Transmission Circuit b.6. BOWDEN 4 (515243) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT110-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 (515233) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit b.2. BRISTOW4 (515035) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT111-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to KEYWEST4 (515048) 138.0 kV Transmission Circuit b.2. KEYWEST4 (515048) 138.0 kV to BELLCOW4 (515369) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT116-3PH | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT117-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT118-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT119-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT120-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT122-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit b.2. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT123-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT124-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT125-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT126-3PH | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT127-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT128-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE1-1 (510368) 13.8 kV to GROVE 4 (510402) 138.0 kV to GROVE 5 (510411) 161.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT129-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to COWSKIN 4 (512719) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT130-3PH | 3 Phase fault on KERR GR3 (512634) 115 kV Bus a. Apply fault at the KERR GR3 (512634) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit b.2. LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit b.3. LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT131-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 (510387) 69.0 kV to VINITA-2 (510404) 69.0 kV Transmission Circuit b.2. ADAIR--2 (510387) 69.0 kV to PRY-JCT2 (510400) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT132-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 (510400) 69.0 kV to PRYORC12 (512810) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT133-3PH | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT134-3PH | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.3. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit b.4. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.5. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.6. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit b.7. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT135-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 (509779) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.2. MINGO-N4 (509760) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit b.3. LLAN ET4 (509771) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.4. LLAN ET4 (509771) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit b.5. MINGO-N4 (509760) 138.0 kV to MAYO--N4 (509779) 138.0 kV Transmission Circuit b.6. T.S.E.-4 (509811) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT136-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT137-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to 141PINE4 (509892) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT138-3PH | 3 Phase fault on PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit b.2. CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit b.3. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT139-3PH | 3 Phase fault on TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 (509835) 138.0 kV to VERDIGS4 (509854) 138.0 kV Transmission Circuit b.2. CLARTOK4 (509864) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit b.3. VERDIGS4 (509854) 138.0 kV to CLARTOK4 (509864) 138.0 kV Transmission Circuit b.4. CATOOSA4 (509790) 138.0 kV to TERNITP4 (509835) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT140-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT141-3PH | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT142-3PH | 3 Phase fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT151-3PH | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT162-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT165-3PH | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT168-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT170-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT171-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT172-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT174-3PH | 3 Phase fault on MILANTP4 (539675) 138 kV Bus a. Apply fault at the MILANTP4 (539675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILANTP4 (539675) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT1-PO | Prior Outage: N345 1 1 (532824) 13.8 kV to Trip Bus 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT2-PO | Prior Outage: FRANKLIN1 (533122) 12.5 kV to Trip Bus 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 3 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.87 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT4-PO | Prior Outage: MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT5-PO | Prior Outage: MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT11-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT12-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT14-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT15-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT16-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT17-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT18-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT19-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT21-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT22-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT23-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT24-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT25-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT26-PO | Prior Outage: BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT27-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT28-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT29-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT30-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT31-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 10 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.838 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT33-PO | Prior Outage: C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT34-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT35-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT36-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT37-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT38-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT39-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT40-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT42-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT43-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT44-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT45-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT46-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT47-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT48-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT49-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT50-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT51-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT52-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT53-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT54-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT55-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT56-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT57-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT58-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT59-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT60-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT61-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT62-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT63-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT64-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT65-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT66-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT67-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT68-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT69-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT70-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT72-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT73-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT74-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT75-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT76-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT77-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT81-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT83-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT85-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT89-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT90-PO | Prior Outage: GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT91-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT92-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT93-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT94-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT95-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT96-PO | Prior Outage: 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT97-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT98-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT99-PO | Prior Outage: MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT100-PO | Prior Outage: 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT101-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT102-PO | Prior Outage: PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT103-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT104-PO | Prior Outage: PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT105-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT106-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT107-PO | Prior Outage: MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT108-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT109-PO | Prior Outage: L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT110-PO | Prior Outage: INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT112-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT113-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT114-PO | Prior Outage: CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT115-PO | Prior Outage: PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 578533: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515926: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 515927: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515926: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 515927: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 587213: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 587463: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 587466: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 587483: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT125-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT126-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT127-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT128-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.872 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.899 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT134-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT135-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT136-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.899 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT138-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT143-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT147-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT160-PO | Prior Outage: PECANCK7 (515235) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit 3 Phase Fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT161-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT162-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT163-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT164-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT165-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT166-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT170-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT179-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT180-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT182-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT183-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT184-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 578533: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT188-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT189-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT190-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT191-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT194-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT195-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT196-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT197-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT198-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT199-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT200-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT201-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT202-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT203-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT204-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT205-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT206-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT207-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT208-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT1-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT2-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.878 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.878 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT5-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT6-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT7-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT8-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT9-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT10-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT11-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV ThreeWinding b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT12-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT13-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV ThreeWinding b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT14-SB | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT15-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT16-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT17-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV TwoWinding b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT19-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT20-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT21-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT22-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT23-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT24-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT25-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT26-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT27-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT28-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT29-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT30-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT31-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT32-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT42-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT43-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT45-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT46-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV ThreeWinding b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT47-SB | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit b.2. CHAMSPR1 (506919) 13.8 kV to CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT48-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT49-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT50-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT51-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT52-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT53-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT54-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT55-SB | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT56-SB | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT58-SB | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT59-SB | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT60-SB | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT61-SB | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT62-SB | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT63-SB | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT64-SB | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT76-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit b.2. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT77-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding b.2. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT78-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT79-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT85-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV ThreeWinding b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT86-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-061-TAP (560084) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT91-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT92-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT93-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT94-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT96-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT99-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT100-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT101-SB | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT102-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT103-SB | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT104-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT105-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT108-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT109-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT110-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT111-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT112-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT113-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT115-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT116-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT117-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT118-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT120-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT121-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT122-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT123-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT124-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT125-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT126-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT127-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21L | Normal | G8_FLT128-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT1-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT2-3PH | 3 Phase fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT3-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT4-3PH | 3 Phase fault on LITCH 5 (532932) 161 kV Bus a. Apply fault at the LITCH 5 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT7-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT9-3PH | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT10-3PH | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT11-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT13-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT15-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT17-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT18-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT19-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT20-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT22-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT23-3PH | 3 Phase fault on MARMATN2 (533639) 69 kV Bus a. Apply fault at the MARMATN2 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN1 (532955) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT24-3PH | 3 Phase fault on FRANKLIN2 (533876) 69 kV Bus a. Apply fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN1 (533122) 12.5 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT26-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT27-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT28-3PH | 3 Phase fault on G17-022-TAP (588664) 138 kV Bus a. Apply fault at the G17-022-TAP (588664) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT29-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT30-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT31-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT33-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT34-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT35-3PH | 3 Phase fault on MONTGOM4 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT36-3PH | 3 Phase fault on ALTOO W2 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO1 1 (533086) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT37-3PH | 3 Phase fault on ALTOO E2 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO3 1 (533087) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT38-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT39-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT40-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT41-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT42-3PH | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT43-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT44-3PH | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT45-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT46-3PH | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT48-3PH | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT50-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT51-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT52-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT53-3PH | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT55-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT56-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT57-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT59-3PH | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT60-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT61-3PH | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to 5ANO% (337912) 161.0 kV to 1ANO AUX (337913) 22.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT62-3PH | 3 Phase fault on FTSMITH8 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT63-3PH | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT64-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT65-3PH | 3 Phase fault on GERALDGAY5 (512760) 161 kV Bus a. Apply fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT66-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT67-3PH | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT68-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT69-3PH | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT70-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT71-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT72-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT73-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT74-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT75-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT76-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT77-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT78-3PH | 3 Phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT79-3PH | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT80-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT90-3PH | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-112-TAP (587894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT92-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT94-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT99-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT100-3PH | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT101-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT102-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT103-3PH | 3 Phase fault on CUSHING2 (515032) 69 kV Bus a. Apply fault at the CUSHING2 (515032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING2 (515032) 69.0 kV to CUSHING4 (515033) 138.0 kV to CUSHING1 (515718) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT104-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV2 (515021) 69.0 kV to GRNWOOD2 (515416) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT105-3PH | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 (515514) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit b.2. KNIPE 4 (515514) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT106-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to PAYNESB4 (515039) 138.0 kV Transmission Circuit b.2. PAYNESB4 (515039) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT107-3PH | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 (515047) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT108-3PH | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 (509758) 138.0 kV to BLUEBEL4 (515242) 138.0 kV Transmission Circuit b.2. PRATTV-4 (509758) 138.0 kV to S.S.---4 (509815) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT109-3PH | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 (515237) 138.0 kV to BEELINE4 (515247) 138.0 kV Transmission Circuit b.2. POLECTP4 (515218) 138.0 kV to TIBBENS4 (515237) 138.0 kV Transmission Circuit b.3. POLECTP4 (515218) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit b.4. BLUEBEL4 (515242) 138.0 kV to BOWDEN 4 (515243) 138.0 kV Transmission Circuit b.5. POLECTP4 (515218) 138.0 kV to POLECAT4 (515219) 138.0 kV Transmission Circuit b.6. BOWDEN 4 (515243) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT110-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 (515233) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit b.2. BRISTOW4 (515035) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT111-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to KEYWEST4 (515048) 138.0 kV Transmission Circuit b.2. KEYWEST4 (515048) 138.0 kV to BELLCOW4 (515369) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT116-3PH | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT117-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT118-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT119-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT120-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT122-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit b.2. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT123-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT124-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT125-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT126-3PH | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT127-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT128-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE1-1 (510368) 13.8 kV to GROVE 4 (510402) 138.0 kV to GROVE 5 (510411) 161.0 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT129-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to COWSKIN 4 (512719) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT130-3PH | 3 Phase fault on KERR GR3 (512634) 115 kV Bus a. Apply fault at the KERR GR3 (512634) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit b.2. LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit b.3. LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT131-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 (510387) 69.0 kV to VINITA-2 (510404) 69.0 kV Transmission Circuit b.2. ADAIR--2 (510387) 69.0 kV to PRY-JCT2 (510400) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT132-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 (510400) 69.0 kV to PRYORC12 (512810) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT133-3PH | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT134-3PH | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.3. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit b.4. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.5. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.6. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit b.7. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT135-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 (509779) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.2. MINGO-N4 (509760) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit b.3. LLAN ET4 (509771) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.4. LLAN ET4 (509771) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit b.5. MINGO-N4 (509760) 138.0 kV to MAYO--N4 (509779) 138.0 kV Transmission Circuit b.6. T.S.E.-4 (509811) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT136-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT137-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to 141PINE4 (509892) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT138-3PH | 3 Phase fault on PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit b.2. CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit b.3. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT139-3PH | 3 Phase fault on TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 (509835) 138.0 kV to VERDIGS4 (509854) 138.0 kV Transmission Circuit b.2. CLARTOK4 (509864) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit b.3. VERDIGS4 (509854) 138.0 kV to CLARTOK4 (509864) 138.0 kV Transmission Circuit b.4. CATOOSA4 (509790) 138.0 kV to TERNITP4 (509835) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT140-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT141-3PH | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT142-3PH | 3 Phase fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT151-3PH | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT162-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT165-3PH | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT168-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT170-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT171-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT172-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT174-3PH | 3 Phase fault on MILANTP4 (539675) 138 kV Bus a. Apply fault at the MILANTP4 (539675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILANTP4 (539675) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT1-PO | Prior Outage: N345 1 1 (532824) 13.8 kV to Trip Bus 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT2-PO | Prior Outage: FRANKLIN1 (533122) 12.5 kV to Trip Bus 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 3 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.858 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT4-PO | Prior Outage: MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT5-PO | Prior Outage: MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT11-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT12-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT14-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT15-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT16-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT17-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT18-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT19-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT21-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT22-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT23-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT24-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT25-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT26-PO | Prior Outage: BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT27-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT28-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT29-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT30-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT31-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 9 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.853 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT33-PO | Prior Outage: C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT34-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT35-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT36-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT37-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT38-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT39-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT40-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT42-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT43-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT44-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT45-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT46-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT47-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT48-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT49-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT50-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT51-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT52-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT53-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT54-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT55-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT56-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT57-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT58-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT59-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT60-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT61-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT62-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT63-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT64-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT65-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT66-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT67-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT68-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT69-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT70-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT72-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT73-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT74-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT75-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT76-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT77-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT81-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT83-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT85-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT89-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT90-PO | Prior Outage: GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT91-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT92-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT93-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT94-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT95-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT96-PO | Prior Outage: 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT97-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT98-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT99-PO | Prior Outage: MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT100-PO | Prior Outage: 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT101-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT102-PO | Prior Outage: PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT103-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT104-PO | Prior Outage: PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT105-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT106-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT107-PO | Prior Outage: MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT108-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT109-PO | Prior Outage: L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT110-PO | Prior Outage: INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT112-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT113-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT114-PO | Prior Outage: CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT115-PO | Prior Outage: PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515900: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION 515926: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 515927: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION |  |  |  |  | 10 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.875 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515926: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT125-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT126-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT127-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT128-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.898 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.881 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.899 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT134-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT135-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT136-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT138-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT143-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT147-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT160-PO | Prior Outage: PECANCK7 (515235) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit 3 Phase Fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.9 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT161-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT162-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT163-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT164-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT165-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT166-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT170-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.9 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT179-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT180-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT182-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT183-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT184-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 7 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.883 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 515926: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT188-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT189-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT190-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT191-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT194-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT195-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT196-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT197-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT198-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT199-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT200-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT201-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT202-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT203-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT204-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT205-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT206-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT207-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT208-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT1-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT2-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.885 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.885 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT5-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.9 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT6-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT7-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT8-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT9-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT10-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT11-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV ThreeWinding b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT12-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT13-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV ThreeWinding b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT14-SB | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT15-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT16-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT17-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV TwoWinding b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT19-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT20-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT21-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.9 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT22-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT23-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.9 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT24-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT25-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT26-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT27-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT28-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT29-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT30-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT31-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT32-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT42-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT43-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT45-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT46-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV ThreeWinding b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT47-SB | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit b.2. CHAMSPR1 (506919) 13.8 kV to CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT48-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT49-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT50-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT51-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT52-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT53-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT54-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT55-SB | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT56-SB | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT58-SB | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT59-SB | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT60-SB | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT61-SB | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT62-SB | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT63-SB | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT64-SB | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.899 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT76-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit b.2. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT77-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding b.2. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT78-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT79-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT85-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV ThreeWinding b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT86-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-061-TAP (560084) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT91-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT92-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT93-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT94-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT96-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT99-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT100-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT101-SB | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT102-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT103-SB | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT104-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT105-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT108-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT109-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT110-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT111-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT112-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT113-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.875 pu
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT115-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT116-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT117-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT118-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT120-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT121-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT122-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT123-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT124-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT125-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT126-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT127-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 21S | Normal | G8_FLT128-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT1-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT2-3PH | 3 Phase fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT3-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT4-3PH | 3 Phase fault on LITCH 5 (532932) 161 kV Bus a. Apply fault at the LITCH 5 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT7-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT9-3PH | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT10-3PH | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT11-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT13-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT15-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT17-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT18-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT19-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT20-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT22-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT23-3PH | 3 Phase fault on MARMATN2 (533639) 69 kV Bus a. Apply fault at the MARMATN2 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN1 (532955) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT24-3PH | 3 Phase fault on FRANKLIN2 (533876) 69 kV Bus a. Apply fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN1 (533122) 12.5 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT26-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT27-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT28-3PH | 3 Phase fault on G17-022-TAP (588664) 138 kV Bus a. Apply fault at the G17-022-TAP (588664) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT29-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT30-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT31-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT33-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT34-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT35-3PH | 3 Phase fault on MONTGOM4 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT36-3PH | 3 Phase fault on ALTOO W2 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO1 1 (533086) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT37-3PH | 3 Phase fault on ALTOO E2 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO3 1 (533087) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT38-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT39-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT40-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT41-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT42-3PH | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT43-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT44-3PH | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT45-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT46-3PH | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT48-3PH | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT50-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT51-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT52-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT53-3PH | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.892 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT55-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT56-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT57-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.892 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT59-3PH | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT60-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT61-3PH | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to 5ANO% (337912) 161.0 kV to 1ANO AUX (337913) 22.0 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT62-3PH | 3 Phase fault on FTSMITH8 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT63-3PH | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT64-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT65-3PH | 3 Phase fault on GERALDGAY5 (512760) 161 kV Bus a. Apply fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT66-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT67-3PH | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT68-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT69-3PH | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT70-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT71-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT72-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT73-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT74-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT75-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT76-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT77-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT78-3PH | 3 Phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT79-3PH | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT80-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT90-3PH | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-112-TAP (587894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT92-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT94-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT99-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT100-3PH | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT101-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT102-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT103-3PH | 3 Phase fault on CUSHING2 (515032) 69 kV Bus a. Apply fault at the CUSHING2 (515032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING2 (515032) 69.0 kV to CUSHING4 (515033) 138.0 kV to CUSHING1 (515718) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT104-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV2 (515021) 69.0 kV to GRNWOOD2 (515416) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT105-3PH | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 (515514) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit b.2. KNIPE 4 (515514) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT106-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to PAYNESB4 (515039) 138.0 kV Transmission Circuit b.2. PAYNESB4 (515039) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT107-3PH | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 (515047) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT108-3PH | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 (509758) 138.0 kV to BLUEBEL4 (515242) 138.0 kV Transmission Circuit b.2. PRATTV-4 (509758) 138.0 kV to S.S.---4 (509815) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT109-3PH | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 (515237) 138.0 kV to BEELINE4 (515247) 138.0 kV Transmission Circuit b.2. POLECTP4 (515218) 138.0 kV to TIBBENS4 (515237) 138.0 kV Transmission Circuit b.3. POLECTP4 (515218) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit b.4. BLUEBEL4 (515242) 138.0 kV to BOWDEN 4 (515243) 138.0 kV Transmission Circuit b.5. POLECTP4 (515218) 138.0 kV to POLECAT4 (515219) 138.0 kV Transmission Circuit b.6. BOWDEN 4 (515243) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT110-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 (515233) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit b.2. BRISTOW4 (515035) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT111-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to KEYWEST4 (515048) 138.0 kV Transmission Circuit b.2. KEYWEST4 (515048) 138.0 kV to BELLCOW4 (515369) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT116-3PH | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT117-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT118-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT119-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT120-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT122-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit b.2. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT123-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT124-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT125-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT126-3PH | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT127-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT128-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE1-1 (510368) 13.8 kV to GROVE 4 (510402) 138.0 kV to GROVE 5 (510411) 161.0 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT129-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to COWSKIN 4 (512719) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT130-3PH | 3 Phase fault on KERR GR3 (512634) 115 kV Bus a. Apply fault at the KERR GR3 (512634) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit b.2. LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit b.3. LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT131-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 (510387) 69.0 kV to VINITA-2 (510404) 69.0 kV Transmission Circuit b.2. ADAIR--2 (510387) 69.0 kV to PRY-JCT2 (510400) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT132-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 (510400) 69.0 kV to PRYORC12 (512810) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT133-3PH | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT134-3PH | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.3. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit b.4. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.5. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.6. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit b.7. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT135-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 (509779) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.2. MINGO-N4 (509760) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit b.3. LLAN ET4 (509771) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.4. LLAN ET4 (509771) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit b.5. MINGO-N4 (509760) 138.0 kV to MAYO--N4 (509779) 138.0 kV Transmission Circuit b.6. T.S.E.-4 (509811) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT136-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT137-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to 141PINE4 (509892) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT138-3PH | 3 Phase fault on PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit b.2. CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit b.3. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT139-3PH | 3 Phase fault on TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 (509835) 138.0 kV to VERDIGS4 (509854) 138.0 kV Transmission Circuit b.2. CLARTOK4 (509864) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit b.3. VERDIGS4 (509854) 138.0 kV to CLARTOK4 (509864) 138.0 kV Transmission Circuit b.4. CATOOSA4 (509790) 138.0 kV to TERNITP4 (509835) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT140-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT141-3PH | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT142-3PH | 3 Phase fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT151-3PH | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT162-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.892 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT165-3PH | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT168-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT170-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT171-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT172-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT174-3PH | 3 Phase fault on MILANTP4 (539675) 138 kV Bus a. Apply fault at the MILANTP4 (539675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILANTP4 (539675) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT1-PO | Prior Outage: N345 1 1 (532824) 13.8 kV to Trip Bus 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT2-PO | Prior Outage: FRANKLIN1 (533122) 12.5 kV to Trip Bus 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 4 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.822 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT4-PO | Prior Outage: MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT5-PO | Prior Outage: MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT11-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT12-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT14-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT15-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT16-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT17-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT18-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT19-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT21-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT22-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT23-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT24-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT25-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT26-PO | Prior Outage: BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT27-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT28-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT29-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT30-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT31-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT33-PO | Prior Outage: C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT34-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT35-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT36-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT37-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT38-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT39-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT40-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.892 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT42-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT43-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.892 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT44-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT45-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT46-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT47-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT48-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT49-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT50-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT51-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT52-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT53-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT54-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT55-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT56-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT57-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT58-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT59-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT60-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT61-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT62-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT63-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT64-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT65-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT66-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT67-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT68-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT69-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT70-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT72-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT73-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT74-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT75-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT76-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT77-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT81-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT83-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT85-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT89-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT90-PO | Prior Outage: GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT91-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT92-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT93-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT94-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT95-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT96-PO | Prior Outage: 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT97-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT98-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT99-PO | Prior Outage: MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT100-PO | Prior Outage: 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT101-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT102-PO | Prior Outage: PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT103-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT104-PO | Prior Outage: PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT105-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT106-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT107-PO | Prior Outage: MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT108-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT109-PO | Prior Outage: L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT110-PO | Prior Outage: INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT112-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT113-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT114-PO | Prior Outage: CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT115-PO | Prior Outage: PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 585303: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT125-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT126-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT127-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT128-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.889 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.89 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.887 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 2 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.88 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT134-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT135-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT136-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.898 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT138-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT143-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT147-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 588637: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT160-PO | Prior Outage: PECANCK7 (515235) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit 3 Phase Fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT161-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT162-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT163-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT164-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT165-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT166-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.898 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT170-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.892 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT179-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT180-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT182-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT183-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT184-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 515882: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 515900: MACHINE TRIPPED DUE TO FREQUENCY PROTECTION 533141: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVERVOLTAGE PROTECTION |  |  |  |  | RE-RUNS WITH PROTECTIONS DISABLED WERE PERFORMED TO VERIFY STABILITY VOLTAGE SPIKES EXIST DURING/CLEARING FAULT 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT188-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT189-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT190-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT191-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT194-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT195-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | NO | YES |  | REDUCE WAVERLY TO 0.0 MW |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT196-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT197-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT198-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT199-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT200-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT201-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT202-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT203-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT204-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT205-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT206-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT207-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT208-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT1-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT2-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT5-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT6-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT7-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT8-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT9-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT10-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT11-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV ThreeWinding b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT12-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT13-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV ThreeWinding b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT14-SB | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT15-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT16-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT17-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV TwoWinding b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT19-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT20-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT21-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT22-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT23-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.891 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT24-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT25-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT26-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT27-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT28-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT29-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT30-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT31-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT32-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT42-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT43-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT45-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT46-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV ThreeWinding b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT47-SB | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit b.2. CHAMSPR1 (506919) 13.8 kV to CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT48-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT49-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT50-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT51-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT52-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT53-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT54-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT55-SB | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT56-SB | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT58-SB | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT59-SB | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.894 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT60-SB | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT61-SB | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT62-SB | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT63-SB | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT64-SB | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT76-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit b.2. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.893 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT77-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding b.2. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT78-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT79-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT85-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV ThreeWinding b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT86-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-061-TAP (560084) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT91-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT92-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT93-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT94-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT96-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.897 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT99-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT100-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT101-SB | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT102-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT103-SB | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT104-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT105-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT108-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT109-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT110-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT111-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT112-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT113-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 5 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.874 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT115-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT116-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT117-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT118-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT120-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT121-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT122-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT123-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT124-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT125-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT126-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT127-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 08 - North Oklahoma/South Central Kansas | 28S | Normal | G8_FLT128-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WCGS U1 (532751) 25.0 kV Two Winding b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.896 pu
Central | 08 - North Oklahoma/South Central Kansas | 19W | Sensitivity | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | MITIGATION NOT REQUIRED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Sensitivity | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | MITIGATION NOT REQUIRED
Central | 08 - North Oklahoma/South Central Kansas | 21S | Sensitivity | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | MITIGATION NOT REQUIRED
Central | 08 - North Oklahoma/South Central Kansas | 28S | Sensitivity | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | MITIGATION NOT REQUIRED
Central | 08 - North Oklahoma/South Central Kansas | 19W | Sensitivity | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | MITIGATION NOT REQUIRED
Central | 08 - North Oklahoma/South Central Kansas | 21L | Sensitivity | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | MITIGATION NOT REQUIRED
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-01 | 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-02 | 3-ph fault on 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-03 | 3-ph fault on CRETE to SHELDON 115kV crt 1, near CRETE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-04 | 3-ph fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-05 | 3-ph fault on GENEVA to SUTTON 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-06 | 3-ph fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-07 | 3-ph fault on SHELDON to MONOLITH 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-08 | 3-ph fault on SHELDON to SW7&BENNET7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-09 | 3-ph fault on SHELDON to FOLSM&PHIL7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-10 | 3-ph fault on Moore 345/115/13.8kV TF T1, near SHELDON 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-11 | 3-ph fault on MCCOOL 345/115/13.8kV TF T2, near MCCOOL 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-12 | 3-ph fault on MCCOOL to YORK SW7 115kV crt 1, near MCCOOL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-13 | 3-ph fault on SUTTON to EGYCNTR7 115kV crt 1, near SUTTON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-14 | 3-ph fault on CARLJCT7 to HEBRN 115kV crt 1, near CARLJCT7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-15 | SLG fault on Friend to CRETE 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the Faulted crt, CRETE to SHELDON 115kV crt 1. and CRETE G Generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-16 | SLG fault on Friend to GENEVA 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the GENEVA 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-17 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to MONOLITH 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-18 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to SW7&BENNET7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-19 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to FOLSM&PHIL7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-20 | SLG fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping CARLJCT7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-21 | SLG fault on GENEVA to SUTTON 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping SUTTON 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-SLG-22 | SLG fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping MCCOOL 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-23 | Prior Outage of Friend to CRETE 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-24 | Prior Outage of Friend to GENEVA 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-25 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator, CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | G17-085-3ph-26 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-01 | 3-ph fault on S3456 to CBLUFFS3 345kV crt 1, near S3456. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-02 | 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-03 | 3-ph fault on COOPER to ATCHSN 3 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-04 | 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-05 | 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-06 | 3-ph fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-07 | 3-ph fault on G16-050-TAP to POSTROCK 345kV crt 1, near G16-050-TAP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-08 | 3-ph fault on REDWILO to POSTROCK 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-09 | 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-10 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-11 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-12 | 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-13 | 3-ph fault on THEDFRD3 to HOLT 345kV crt 1, near THEDFRD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-14 | 3-ph fault on ANTELOPE to HOLT 345kV crt 1, near ANTELOPE. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-15 | 3-ph fault on GR ISLD-LNX3 to HOLT 345kV crt 1, near GR ISLD-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-16 | 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-17 | 3-ph fault on MEADOWGROVE to FTRANDL4 230kV crt 1, near MEADOWGROVE. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-18 | SLG fault on S3456 to CBLUFFS3 345kV crt 1, near S3456 for 16 cycles. Clear fault by tripping the faulted crt and S3456 to S3458 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-19 | SLG fault on COOPER to ST JOE 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER to ATCHSN 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-20 | SLG fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER 345/161/13.8kV TF T5. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-21 | SLG fault on S3451 to RAUN 345kV crt 1, near S3451 for 16 cycles. Clear fault by tripping the faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-22 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-23 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-24 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the faulted crt, REDWILO3 to GENTLMN3 345kV crt 1 and REDWILO3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-25 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the faulted crt, KEYSTON3 to GENTLMN3 345kV crt 1 and KEYSTON3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-26 | SLG fault on S3458 to HOLT 345kV crt 1, near S3458 for 16 cycles. Clear fault by tripping the faulted crt and S3458 to COOPER 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-27 | SLG fault on ANTELOPE to HOLT.CO3 345kV crt 1, near ANTELOPE for 16 cycles. Clear fault by tripping ANTELOPE 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-28 | SLG fault on THEDFRD3 to HOLT.CO3 345kV crt 1, near THEDFRD3 for 16 cycles. Clear fault by tripping THEDFRD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-29 | SLG fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3 for 16 cycles. Clear fault by tripping the faulted crt, GR PRAIRIE 345kV bus, G16-075 Gen and GRPR11W/12W/21W/22W Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-SLG-30 | SLG fault on MEADOWGROVE to FTRANDL4 230kV crt 1, near MEADOWGROVE for 16 cycles. Clear fault by tripping MEADOWGROVE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-32 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-33 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-35 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-36 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-37 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-38 | Prior Outage of S3456 to CBLUFFS3 345kV crt 1. 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Normal | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 6 cycles. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-01 | 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-02 | 3-ph fault on 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-03 | 3-ph fault on CRETE to SHELDON 115kV crt 1, near CRETE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-04 | 3-ph fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-05 | 3-ph fault on GENEVA to SUTTON 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-06 | 3-ph fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-07 | 3-ph fault on SHELDON to MONOLITH 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-08 | 3-ph fault on SHELDON to SW7&BENNET7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-09 | 3-ph fault on SHELDON to FOLSM&PHIL7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-10 | 3-ph fault on Moore 345/115/13.8kV TF T1, near SHELDON 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-11 | 3-ph fault on MCCOOL 345/115/13.8kV TF T2, near MCCOOL 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-12 | 3-ph fault on MCCOOL to YORK SW7 115kV crt 1, near MCCOOL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-13 | 3-ph fault on SUTTON to EGYCNTR7 115kV crt 1, near SUTTON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-14 | 3-ph fault on CARLJCT7 to HEBRN 115kV crt 1, near CARLJCT7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-15 | SLG fault on Friend to CRETE 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the Faulted crt, CRETE to SHELDON 115kV crt 1. and CRETE G Generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-16 | SLG fault on Friend to GENEVA 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the GENEVA 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-17 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to MONOLITH 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-18 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to SW7&BENNET7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-19 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to FOLSM&PHIL7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-20 | SLG fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping CARLJCT7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-21 | SLG fault on GENEVA to SUTTON 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping SUTTON 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-SLG-22 | SLG fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping MCCOOL 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-23 | Prior Outage of Friend to CRETE 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-24 | Prior Outage of Friend to GENEVA 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-25 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator, CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | G17-085-3ph-26 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-01 | 3-ph fault on S3456 to CBLUFFS3 345kV crt 1, near S3456. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-02 | 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-03 | 3-ph fault on COOPER to ATCHSN 3 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-04 | 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-05 | 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-06 | 3-ph fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-07 | 3-ph fault on G16-050-TAP to POSTROCK 345kV crt 1, near G16-050-TAP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-08 | 3-ph fault on REDWILO to POSTROCK 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-09 | 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-10 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-11 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-12 | 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-13 | 3-ph fault on THEDFRD3 to HOLT 345kV crt 1, near THEDFRD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-14 | 3-ph fault on ANTELOPE to HOLT 345kV crt 1, near ANTELOPE. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-15 | 3-ph fault on GR ISLD-LNX3 to HOLT 345kV crt 1, near GR ISLD-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-16 | 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-17 | 3-ph fault on MEADOWGROVE to FTRANDL4 230kV crt 1, near MEADOWGROVE. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-18 | SLG fault on S3456 to CBLUFFS3 345kV crt 1, near S3456 for 16 cycles. Clear fault by tripping the faulted crt and S3456 to S3458 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-19 | SLG fault on COOPER to ST JOE 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER to ATCHSN 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-20 | SLG fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER 345/161/13.8kV TF T5. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-21 | SLG fault on S3451 to RAUN 345kV crt 1, near S3451 for 16 cycles. Clear fault by tripping the faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-22 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-23 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-24 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the faulted crt, REDWILO3 to GENTLMN3 345kV crt 1 and REDWILO3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-25 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the faulted crt, KEYSTON3 to GENTLMN3 345kV crt 1 and KEYSTON3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-26 | SLG fault on S3458 to HOLT 345kV crt 1, near S3458 for 16 cycles. Clear fault by tripping the faulted crt and S3458 to COOPER 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-27 | SLG fault on ANTELOPE to HOLT.CO3 345kV crt 1, near ANTELOPE for 16 cycles. Clear fault by tripping ANTELOPE 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-28 | SLG fault on THEDFRD3 to HOLT.CO3 345kV crt 1, near THEDFRD3 for 16 cycles. Clear fault by tripping THEDFRD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-29 | SLG fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3 for 16 cycles. Clear fault by tripping the faulted crt, GR PRAIRIE 345kV bus, G16-075 Gen and GRPR11W/12W/21W/22W Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-SLG-30 | SLG fault on MEADOWGROVE to FTRANDL4 230kV crt 1, near MEADOWGROVE for 16 cycles. Clear fault by tripping MEADOWGROVE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-32 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-33 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-35 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-36 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-37 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-38 | Prior Outage of S3456 to CBLUFFS3 345kV crt 1. 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Normal | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 6 cycles. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-01 | 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-02 | 3-ph fault on 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-03 | 3-ph fault on CRETE to SHELDON 115kV crt 1, near CRETE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-04 | 3-ph fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-05 | 3-ph fault on GENEVA to SUTTON 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-06 | 3-ph fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-07 | 3-ph fault on SHELDON to MONOLITH 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-08 | 3-ph fault on SHELDON to SW7&BENNET7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-09 | 3-ph fault on SHELDON to FOLSM&PHIL7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-10 | 3-ph fault on Moore 345/115/13.8kV TF T1, near SHELDON 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-11 | 3-ph fault on MCCOOL 345/115/13.8kV TF T2, near MCCOOL 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-12 | 3-ph fault on MCCOOL to YORK SW7 115kV crt 1, near MCCOOL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-13 | 3-ph fault on SUTTON to EGYCNTR7 115kV crt 1, near SUTTON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-14 | 3-ph fault on CARLJCT7 to HEBRN 115kV crt 1, near CARLJCT7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-15 | SLG fault on Friend to CRETE 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the Faulted crt, CRETE to SHELDON 115kV crt 1. and CRETE G Generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-16 | SLG fault on Friend to GENEVA 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the GENEVA 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-17 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to MONOLITH 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-18 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to SW7&BENNET7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-19 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to FOLSM&PHIL7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-20 | SLG fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping CARLJCT7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-21 | SLG fault on GENEVA to SUTTON 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping SUTTON 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-SLG-22 | SLG fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping MCCOOL 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-23 | Prior Outage of Friend to CRETE 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-24 | Prior Outage of Friend to GENEVA 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-25 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator, CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | G17-085-3ph-26 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-01 | 3-ph fault on S3456 to CBLUFFS3 345kV crt 1, near S3456. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-02 | 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-03 | 3-ph fault on COOPER to ATCHSN 3 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-04 | 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-05 | 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-06 | 3-ph fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-07 | 3-ph fault on G16-050-TAP to POSTROCK 345kV crt 1, near G16-050-TAP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-08 | 3-ph fault on REDWILO to POSTROCK 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-09 | 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-10 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-11 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-12 | 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-13 | 3-ph fault on THEDFRD3 to HOLT 345kV crt 1, near THEDFRD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-14 | 3-ph fault on ANTELOPE to HOLT 345kV crt 1, near ANTELOPE. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-15 | 3-ph fault on GR ISLD-LNX3 to HOLT 345kV crt 1, near GR ISLD-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-16 | 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-17 | 3-ph fault on MEADOWGROVE to FTRANDL4 230kV crt 1, near MEADOWGROVE. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-18 | SLG fault on S3456 to CBLUFFS3 345kV crt 1, near S3456 for 16 cycles. Clear fault by tripping the faulted crt and S3456 to S3458 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-19 | SLG fault on COOPER to ST JOE 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER to ATCHSN 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-20 | SLG fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER 345/161/13.8kV TF T5. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-21 | SLG fault on S3451 to RAUN 345kV crt 1, near S3451 for 16 cycles. Clear fault by tripping the faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-22 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-23 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-24 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the faulted crt, REDWILO3 to GENTLMN3 345kV crt 1 and REDWILO3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-25 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the faulted crt, KEYSTON3 to GENTLMN3 345kV crt 1 and KEYSTON3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-26 | SLG fault on S3458 to HOLT 345kV crt 1, near S3458 for 16 cycles. Clear fault by tripping the faulted crt and S3458 to COOPER 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-27 | SLG fault on ANTELOPE to HOLT.CO3 345kV crt 1, near ANTELOPE for 16 cycles. Clear fault by tripping ANTELOPE 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-28 | SLG fault on THEDFRD3 to HOLT.CO3 345kV crt 1, near THEDFRD3 for 16 cycles. Clear fault by tripping THEDFRD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-29 | SLG fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3 for 16 cycles. Clear fault by tripping the faulted crt, GR PRAIRIE 345kV bus, G16-075 Gen and GRPR11W/12W/21W/22W Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-SLG-30 | SLG fault on MEADOWGROVE to FTRANDL4 230kV crt 1, near MEADOWGROVE for 16 cycles. Clear fault by tripping MEADOWGROVE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-32 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-33 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-35 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-36 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-37 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-38 | Prior Outage of S3456 to CBLUFFS3 345kV crt 1. 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Normal | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 6 cycles. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-01 | 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-02 | 3-ph fault on 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-03 | 3-ph fault on CRETE to SHELDON 115kV crt 1, near CRETE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-04 | 3-ph fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-05 | 3-ph fault on GENEVA to SUTTON 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-06 | 3-ph fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-07 | 3-ph fault on SHELDON to MONOLITH 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-08 | 3-ph fault on SHELDON to SW7&BENNET7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-09 | 3-ph fault on SHELDON to FOLSM&PHIL7 115kV crt 1, near SHELDON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-10 | 3-ph fault on Moore 345/115/13.8kV TF T1, near SHELDON 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-11 | 3-ph fault on MCCOOL 345/115/13.8kV TF T2, near MCCOOL 115kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-12 | 3-ph fault on MCCOOL to YORK SW7 115kV crt 1, near MCCOOL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-13 | 3-ph fault on SUTTON to EGYCNTR7 115kV crt 1, near SUTTON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-14 | 3-ph fault on CARLJCT7 to HEBRN 115kV crt 1, near CARLJCT7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-15 | SLG fault on Friend to CRETE 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the Faulted crt, CRETE to SHELDON 115kV crt 1. and CRETE G Generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-16 | SLG fault on Friend to GENEVA 115kV crt 1, near Friend for 16 cycles. Clear fault by tripping the GENEVA 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-17 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to MONOLITH 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-18 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to SW7&BENNET7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-19 | SLG fault on CRETE to SHELDON 115kV crt 1, near CRETE for 16 cycles. Clear fault by tripping the Faulted crt and SHELDON to FOLSM&PHIL7 115kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-20 | SLG fault on GENEVA to CARLJCT7 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping CARLJCT7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-21 | SLG fault on GENEVA to SUTTON 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping SUTTON 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-SLG-22 | SLG fault on GENEVA to MCCOOL 115kV crt 1, near GENEVA for 16 cycles. Clear fault by tripping MCCOOL 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-23 | Prior Outage of Friend to CRETE 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-24 | Prior Outage of Friend to GENEVA 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-25 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to GENEVA 115kV crt 1, near Friend. Clear fault after 7 cycles , trip G17-085/G14-039 generator, CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | G17-085-3ph-26 | Prior Outage of CRETE to SHELDON 115kV crt 1. 3-ph fault on Friend to CRETE 115kV crt 1, near Friend. Clear fault after 7 cycles , trip CRETE G Generator and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-01 | 3-ph fault on S3456 to CBLUFFS3 345kV crt 1, near S3456. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-02 | 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-03 | 3-ph fault on COOPER to ATCHSN 3 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-04 | 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-05 | 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-06 | 3-ph fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-07 | 3-ph fault on G16-050-TAP to POSTROCK 345kV crt 1, near G16-050-TAP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-08 | 3-ph fault on REDWILO to POSTROCK 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-09 | 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes