## Executive Summary
Executive Summary: DISIS-2017-002-2 Restudy of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2017. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 3.0 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2017-002-2 Restudy includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest)
DISIS Manual Version 3.0
https://spp.org/documents/71111/DISIS%20Study%20Manual%2020240424.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
11172.94 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $635,537,983 Steady State Network Upgrade $221,367,707 Steady State/Stability Network Upgrade $41,157,960 Interconnection Costs: $373,012,316
Models Used in Steady State Study
2021 ITP Series
Winter: 2026
Summer: 2023, 2026
Light: 2026
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: 6/26/2024
Costs for Solar/Battery Requests were allocated using the 26SP (summer peak) model.
Costs for Wind Requests were allocated using the 26L (light load) model.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4537300% | SPP | Draft Posting
4539100% | SPP | Draft Posting #2
4546300% | SPP | Draft Posting #3 - Addition of Contingent Facility Analysis
4546900% | SPP | Final Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4539100% | Network Upgrade | 6 | Constraints Summary | Replaced the Arcadia - Seminole 345 kV and Draper Lake - Seminole 345 kV tap line at Horseshoe Lake 2023 ITP upgrade (not approved) with the Matthewson - Redbud 345 kV New Line 2023 ITP upgrade (approved)
4539100% | Network Upgrade | 7 | Assigned Upgrade Costs | Replaced the Arcadia - Seminole 345 kV and Draper Lake - Seminole 345 kV tap line at Horseshoe Lake 2023 ITP upgrade (not approved) with the Matthewson - Redbud 345 kV New Line 2023 ITP upgrade (approved)
4539100% | Network Upgrade | 8 | Upgrade Summary | Replaced the Arcadia - Seminole 345 kV and Draper Lake - Seminole 345 kV tap line at Horseshoe Lake 2023 ITP upgrade (not approved) with the Matthewson - Redbud 345 kV New Line 2023 ITP upgrade (approved)
4539100% | Network Upgrade | 6 | Constraints Summary | Removed the Border to G17-151 Tap 345 kV Network Upgrade and remove Tolk to Potter County 345 kV Network Upgrade assigned to Group 05 due to reconsideration of NL units being left at MDWG dispatch
4539100% | Network Upgrade | 7 | Assigned Upgrade Costs | Removed the Border to G17-151 Tap 345 kV Network Upgrade and remove Tolk to Potter County 345 kV Network Upgrade assigned to Group 05 due to reconsideration of NL units being left at MDWG dispatch
4539100% | Network Upgrade | 8 | Upgrade Summary | Removed the Border to G17-151 Tap 345 kV Network Upgrade and remove Tolk to Potter County 345 kV Network Upgrade assigned to Group 05 due to reconsideration of NL units being left at MDWG dispatch
4539100% | Stability Constraints | 12 | Stability Analysis Results | Removed stability constraints for the OKU and Yoakum identified faults due to fix in Group 05 dispatch.
4539100% | Contingent Upgrade | 9 | Contingent Upgrades - Screening | Removed GEN-2017-222 from meeting Contingent Upgrade criteria for the Multi - Sheldon - Monolith Contingent Facility
4539100% | Network Upgrade | 7 | Assigned Upgrade Costs | Removed Group 04 storage and solar requests being cost allocated to the Tolk - Potter County 345 kV Line. Network upgrade was identified in the Group 04 26L case only and only has wind requests dispatched in 26L.
4539100% | Network Upgrade | 6 | Constraints Summary | Added the Multi - Minco - Pleasant Valley - Draper 345 kV 2020 ITP upgrade into the 00NR result to mitigate the new thermal overload on the Cimarron transformer #1, after the network upgrade changes in the OKGE area during the ERIS analysis.
4539100% | Network Upgrade | 7 | Assigned Upgrade Costs | Added the Multi - Minco - Pleasant Valley - Draper 345 kV 2020 ITP upgrade into the 00NR result to mitigate the new thermal overload on the Cimarron transformer #1, after the network upgrade changes in the OKGE area during the ERIS analysis.
4539100% | Network Upgrade | 8 | Upgrade Summary | Added the Multi - Minco - Pleasant Valley - Draper 345 kV 2020 ITP upgrade into the 00NR result to mitigate the new thermal overload on the Cimarron transformer #1, after the network upgrade changes in the OKGE area during the ERIS analysis.
4539100% | Network Upgrade | 10 | All Thermal | Added the Multi - Minco - Pleasant Valley - Draper 345 kV 2020 ITP upgrade into the 00NR result to mitigate the new thermal overload on the Cimarron transformer #1, after the network upgrade changes in the OKGE area during the ERIS analysis.
4539100% | Network Upgrade | 6 | Constraints Summary | Updated the Upgrade Name from "Replace the Nashua Transformer #1" to "Replace the Nashua Transformer #1 (ID 11)"
4539100% | Network Upgrade | 7 | Assigned Upgrade Costs | Updated the Upgrade Name from "Replace the Nashua Transformer #1" to "Replace the Nashua Transformer #1 (ID 11)"
4539100% | Network Upgrade | 8 | Upgrade Summary | Updated the Upgrade Name from "Replace the Nashua Transformer #1" to "Replace the Nashua Transformer #1 (ID 11)"
4539100% | Network Upgrade | 10 | All Thermal | Updated the Upgrade Name from "Replace the Nashua Transformer #1" to "Replace the Nashua Transformer #1 (ID 11)"
4539100% | Upgrade ID | 8 | Upgrade Summary | Corrected the UIDs for several upgrades. Changed the UIDs for the model corrections from "TBD" to "N/A"
4539100% | Upgrade ID | 7 | Assigned Upgrade Costs | Corrected the UIDs for several upgrades.
4539100% | Project Status | 4 | Requests | Updated the GEN-2017-105 status from "IA pending" to "IA FULLY EXECUTED/ON SCHEDULE"
4539100% | Contingent Upgrade | 9 | Contingent Upgrades - Screening | Updated NTC IDs, Project Names, and Project descriptions to be in alignment with Quarter Project Tracking.
4546300% | Contingent Upgrade | 10 | All Thermal | Removal of invalid contingencies related to the ER G02 S0 non-cnv - Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
4546300% | Network Upgrade | 6 | Constraints Summary | Replace the Network Upgrade "Replace the Nashua Transformer #1 (ID 11)" with "Install a second 650 MVA TX at Nashua" as per KCPL feedback
4546300% | Network Upgrade | 7 | Assigned Upgrade Costs | Replace the Network Upgrade "Replace the Nashua Transformer #1 (ID 11)" with "Install a second 650 MVA TX at Nashua" as per KCPL feedback
4546300% | Network Upgrade | 8 | Upgrade Summary | Replace the Network Upgrade "Replace the Nashua Transformer #1 (ID 11)" with "Install a second 650 MVA TX at Nashua" as per KCPL feedback
4546300% | Network Upgrade | 10 | All Thermal | Replace the Network Upgrade "Replace the Nashua Transformer #1 (ID 11)" with "Install a second 650 MVA TX at Nashua" as per KCPL feedback
4546300% | Network Upgrade | 6 | Constraints Summary | Removed the Network Upgrade "Build a new Holt to Atchison 345kV line 1". The steady-state non-convergence and stability issues can be addressed following the MDAG model update and system adjustments in coordination with Evergy and local GOs. Further EMT study may still be required to verify local controller issues observed in the stability results.
4546300% | Network Upgrade | 7 | Assigned Upgrade Costs | Removed the Network Upgrade "Build a new Holt to Atchison 345kV line 1". The steady-state non-convergence and stability issues can be addressed following the MDAG model update and system adjustments in coordination with Evergy and local GOs. Further EMT study may still be required to verify local controller issues observed in the stability results.
4546300% | Network Upgrade | 8 | Upgrade Summary | Removed the Network Upgrade "Build a new Holt to Atchison 345kV line 1". The steady-state non-convergence and stability issues can be addressed following the MDAG model update and system adjustments in coordination with Evergy and local GOs. Further EMT study may still be required to verify local controller issues observed in the stability results.
4546300% | Network Upgrade | 10 | All Thermal | Removed the Network Upgrade "Build a new Holt to Atchison 345kV line 1". The steady-state non-convergence and stability issues can be addressed following the MDAG model update and system adjustments in coordination with Evergy and local GOs. Further EMT study may still be required to verify local controller issues observed in the stability results.
4546300% | Contingent Upgrade | 6 | Constraints Summary | Added Contingent Facility Analysis results, with the "Study Name" column labeled "DISIS-2017-002 CF"
4546300% | Contingent Upgrade | 7 | Assigned Upgrade Costs | Added Contingent Facility Analysis results, with the "Study Name" column labeled "DISIS-2017-002 CF"
4546300% | Contingent Upgrade | 8 | Upgrade Summary | Added Contingent Facility Analysis results, with the "Study Name" column labeled "DISIS-2017-002 CF"
4546300% | Contingent Upgrade | 10 | All Thermal | Added Contingent Facility Analysis results, with the "Study Name" column labeled "DISIS-2017-002 CF"
4546300% | Contingent Upgrade | 12 | Stability Analysis Results | Added Contingent Facility Analysis results, with the "Study Name" column labeled "DISIS-2017-002 CF"
4546300% | Project LOIS | 4 | Requests | Included seasonal LOIS values for each study request
4546300% | Project LOIS | 5 | Seasonal LOIS | Included seasonal LOIS values for each study request
4546900% | Request Status | 4 | Requests | Updated status of study requests as of the start of this study
4546900% | Seasonal LOIS | 4 | Requests | LOIS values for G02 and 03 units updated to be consistent with the power flow assignment approach in the DISIS manual
4546900% | Seasonal LOIS | 5 | Seasonal LOIS | LOIS values for G02 and 03 units updated to be consistent with the power flow assignment approach in the DISIS manual
4546900% | Network Upgrade | 7 | Assigned Upgrade Costs | Updated G02 and 03 units assigned to upgrades due to stability issues to be consistent with the power flow assignment approach in the DISIS manual
4546900% | Violation | 12 | Stability Analysis Results | Updated G02 and 03 units assigned to upgrades due to stability issues to be consistent with the power flow assignment approach in the DISIS manual
4546900% | Network Upgrade | 7 | Assigned Upgrade Costs | Updated cost of UID 156498 per facility study
4546900% | Network Upgrade | 8 | Upgrade Summary | Updated cost of UID 156498 per facility study
4546900% | Network Upgrade | 9 | Contingent Upgrades - Screening | Updated cost of UID 156498 per facility study
4546900% | Network Upgrade | 9 | Contingent Upgrades - Screening | Updated cost of UID 159068 per facility study

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | -14.5844 | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -1.85 | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -1.85 | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | 108.66 | 108.66 | 57.62 | 107.57 | 108.66 | 108.66 | 55.72 | 55.72 | -11.5097 | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 170.24 | 170.24 | -20.05 | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 72.63 | 72.63 | -16.75 | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | 0 | 0 | 115 | 115 | 0 | 0 | 65.25 | 65.25 | -0.16641 | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | -2.3552 | ER/NR | NPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.2808 | ER | WAPA | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 0 | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -5.222 | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid: Solar and Storage | 310 | 175.91 | 175.91 | 310 | 310 | 175.91 | 175.91 | 175.91 | 175.91 | -5.3914 | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-202 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -3.3671 | ER/NR | GRDA | New Madrid - Sikeston 161kV | IA PENDING
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | Hybrid: Solar and Storage | 300 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | -11.789 | ER | KCPL | LaCygne - Neosho 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1851 | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | -16.6236 | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | 140.27 | 140.27 | 180 | 180 | 140.27 | 140.27 | 180 | 180 | -23.0719 | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | -14.9991 | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | 0 | 0 | 200 | 200 | 0 | 0 | 0 | 0 | -9.9933 | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-125 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | -194.3778 | ER/NR | WERE | Swissvale 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 29.6 | 0 | 0 | 29.6 | 29.6 | 0 | 0 | 0 | 0 | 0 | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | 400 | 400 | 232.18 | 337.71 | 400 | 400 | 39.24 | 39.24 | -25.6 | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | 39.24 | 39.24 | 232.18 | 337.71 | 39.24 | 39.24 | 39.24 | 39.24 | -25.6 | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | 0 | 0 | 130 | 130 | 0 | 0 | 0 | 0 | -11.7168 | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | 500.4 | 500.4 | 500.4 | 500.4 | 500.4 | 500.4 | 500.4 | 500.4 | -4.7 | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 0 | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | 0 | 0 | 201.6 | 201.6 | 0 | 0 | 0 | 0 | -0.057 | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 152 | 0 | 0 | 152 | 152 | 0 | 0 | 0 | 0 | -0.043 | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | 0 | 0 | 201.6 | 201.6 | 0 | 0 | 0 | 0 | -1.9 | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | 0 | 0 | 201.6 | 201.6 | 0 | 0 | 0 | 0 | 0 | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -12.07 | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Storage | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | -12.07 | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Storage | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 0 | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-132 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | -200 | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -100 | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -100 | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | -100 | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | -460.72 | ER/NR | AEPW | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | 241.7 | 241.7 | 241.7 | 241.7 | 241.7 | 241.7 | 241.7 | 241.7 | -460.72 | ER/NR | AEPW | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | -36.47 | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | 26.27 | 234.26 | 26.27 | 234.26 | 26.27 | 234.26 | 250 | 250 | -16.92 | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-154 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | -36.47 | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-167 | 04 SOUTHEAST | 19 | DIS-17-2 | Storage | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | -15.43 | ER/NR | OKGE | Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -1.22 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -1.22 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -1.22 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Hybrid: Solar and Storage | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | -15.6 | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | -0.64 | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | -0.71 | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | 48.12 | 48.12 | 49.38 | 49.18 | 48.12 | 48.12 | 48.12 | 48.12 | -2.87 | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | 215 | 215 | 22.59 | 201.46 | 215 | 215 | 215 | 215 | -16.92 | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | -6.68 | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | -7.7 | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | -15.06 | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -2.5 | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | -0.48 | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation)
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-033 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | AEPW | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Cole 115kV | IA PENDING
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | WAPA | NELSON 7
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.12 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 238 | [9 empty] | ER/NR | AECI | 5MARYVL
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 01 NORTH | 16 | DIS-16-1 | Wind | 100.05 | [9 empty] | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 78.2 | [9 empty] | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 5.3 | [9 empty] | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Storage | 20 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-057 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 100 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 | [9 empty] | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [9 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [9 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 11.72 | [9 empty] | ER/NR | BEPC | Williston 115kV
MPC2100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP | Center - Mandan 230 kV
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.22 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 4 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | 8 | PQ | Wind | 150 | [9 empty] | ER | AECI | Remington 138kV
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 68.8 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 04 SOUTHEAST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 23SP | ERIS 26SP | ERIS 26L | ERIS 26WP | NRIS 23SP | NRIS 26SP | NRIS 26L | NRIS 26WP | Stability 25SP | Stability 25WP
GEN-2017-175 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-175 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-175 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-175 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-175 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-175 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-175 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300
GEN-2017-175 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300
GEN-2017-214 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-214 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-214 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A
GEN-2017-214 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | N/A | N/A | 100 | N/A | N/A | 100 | N/A
GEN-2017-214 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-214 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-214 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2017-214 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2017-215 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-215 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-215 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A
GEN-2017-215 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | N/A | N/A | 100 | N/A | N/A | 100 | N/A
GEN-2017-215 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-215 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 100 | 100 | None | None | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100 | 100
GEN-2017-215 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2017-215 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2017-222 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 180 | 108.66 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Denison to Boyer 69kV Terminal Upgrade | N/A | N/A | 108.66 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-222 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 180 | 108.66 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Denison to Boyer 69kV Terminal Upgrade | N/A | N/A | 108.66 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-222 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 180 | 57.62 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP) | Denison to Boyer 69kV Terminal Upgrade | 57.62 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 180 | N/A
GEN-2017-222 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 180 | 107.57 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Denison to Boyer 69kV Terminal Upgrade | N/A | 107.57 | N/A | N/A | N/A | N/A | N/A | N/A | 180 | N/A
GEN-2017-222 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 180 | 108.66 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Denison to Boyer 69kV Terminal Upgrade | N/A | N/A | 108.66 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-222 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 180 | 108.66 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Denison to Boyer 69kV Terminal Upgrade | N/A | N/A | 108.66 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-222 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 180 | 55.72 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Denison to Boyer 69kV Terminal Upgrade | N/A | N/A | N/A | 55.72 | N/A | N/A | N/A | N/A | N/A | 180
GEN-2017-222 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 180 | 55.72 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Denison to Boyer 69kV Terminal Upgrade | N/A | N/A | N/A | 55.72 | N/A | N/A | N/A | N/A | N/A | 180
GEN-2017-105 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 75 | 75 | None | None | N/A | N/A | 75 | N/A | N/A | N/A | 75 | N/A | 75 | 75
GEN-2017-105 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 75 | 75 | None | None | N/A | N/A | 75 | N/A | N/A | N/A | 75 | N/A | 75 | 75
GEN-2017-105 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 75 | 75 | None | None | 75 | N/A | N/A | N/A | 75 | N/A | N/A | N/A | 75 | N/A
GEN-2017-105 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 75 | 75 | None | None | N/A | 75 | N/A | N/A | N/A | 75 | N/A | N/A | 75 | N/A
GEN-2017-105 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 75 | 75 | None | None | N/A | N/A | 75 | N/A | N/A | N/A | 75 | N/A | 75 | 75
GEN-2017-105 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 75 | 75 | None | None | N/A | N/A | 75 | N/A | N/A | N/A | 75 | N/A | 75 | 75
GEN-2017-105 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 75 | 75 | None | None | N/A | N/A | N/A | 75 | N/A | N/A | N/A | 75 | N/A | 75
GEN-2017-105 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 75 | 75 | None | None | N/A | N/A | N/A | 75 | N/A | N/A | N/A | 75 | N/A | 75
GEN-2017-144 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2017-144 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2017-144 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2017-144 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2017-144 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2017-144 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2017-144 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2017-144 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 200 | 0 | Non-Cnv/Stability | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2017-181 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 300 | N/A | 300 | 300
GEN-2017-181 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 300 | N/A | 300 | 300
GEN-2017-181 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | N/A | 300 | N/A | N/A | N/A | 300 | N/A
GEN-2017-181 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | N/A | N/A | 151.58 | N/A | N/A | 300 | N/A
GEN-2017-181 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 300 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 300 | N/A | 300 | 300
GEN-2017-181 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 300 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 300 | N/A | 300 | 300
GEN-2017-181 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 300 | 170.24 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 170.24 | N/A | N/A | N/A | 87 | N/A | 300
GEN-2017-181 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 300 | 170.24 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 170.24 | N/A | N/A | N/A | 87 | N/A | 300
GEN-2017-182 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 128 | 128 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 128 | N/A | 128 | 128
GEN-2017-182 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 128 | 128 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 128 | N/A | 128 | 128
GEN-2017-182 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 128 | 128 | None | None | 128 | N/A | N/A | N/A | 128 | N/A | N/A | N/A | 128 | N/A
GEN-2017-182 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 128 | 128 | None | None | N/A | 128 | N/A | N/A | N/A | 64.67 | N/A | N/A | 128 | N/A
GEN-2017-182 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 128 | 128 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 128 | N/A | 128 | 128
GEN-2017-182 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 128 | 128 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 128 | N/A | 128 | 128
GEN-2017-182 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 128 | 72.63 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 72.63 | N/A | N/A | N/A | 37.12 | N/A | 128
GEN-2017-182 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 128 | 72.63 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 72.63 | N/A | N/A | N/A | 37.12 | N/A | 128
GEN-2017-198 | 02 NEBRASKA | Storage | April 1 - May 31 (Near Term) | 11.64 | 11.64 | None | None | 11.64 | N/A | N/A | 11.64 | N/A | N/A | N/A | N/A | 11.64 | 11.64
GEN-2017-198 | 02 NEBRASKA | Storage | April 1 - May 31 (Long Term) | 11.64 | 11.64 | None | None | N/A | 11.64 | N/A | 11.64 | N/A | N/A | N/A | N/A | 11.64 | 11.64
GEN-2017-198 | 02 NEBRASKA | Storage | June 1 - Sept 30 (Near Term) | 11.64 | 11.64 | None | None | 11.64 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11.64 | N/A
GEN-2017-198 | 02 NEBRASKA | Storage | June 1 - Sept 30 (Long Term) | 11.64 | 11.64 | None | None | N/A | 11.64 | N/A | N/A | N/A | N/A | N/A | N/A | 11.64 | N/A
GEN-2017-198 | 02 NEBRASKA | Storage | Oct 1 - Nov 30 (Near Term) | 11.64 | 11.64 | None | None | 11.64 | N/A | N/A | 11.64 | N/A | N/A | N/A | N/A | 11.64 | 11.64
GEN-2017-198 | 02 NEBRASKA | Storage | Oct 1 - Nov 30 (Long Term) | 11.64 | 11.64 | None | None | N/A | 11.64 | N/A | 11.64 | N/A | N/A | N/A | N/A | 11.64 | 11.64
GEN-2017-198 | 02 NEBRASKA | Storage | Dec 1 - March 31 (Near Term) | 11.64 | 11.64 | None | None | N/A | N/A | N/A | 11.64 | N/A | N/A | N/A | N/A | N/A | 11.64
GEN-2017-198 | 02 NEBRASKA | Storage | Dec 1 - March 31 (Long Term) | 11.64 | 11.64 | None | None | N/A | N/A | N/A | 11.64 | N/A | N/A | N/A | N/A | N/A | 11.64
GEN-2017-201 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-201 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-201 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A
GEN-2017-201 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | N/A | N/A | 126.32 | N/A | N/A | 250 | N/A
GEN-2017-201 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-201 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-201 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 72.5 | N/A | 250
GEN-2017-201 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 72.5 | N/A | 250
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | April 1 - May 31 (Near Term) | 310 | 175.91 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | 310 | N/A | N/A | 175.91 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | April 1 - May 31 (Long Term) | 310 | 175.91 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | 310 | N/A | 175.91 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | June 1 - Sept 30 (Near Term) | 310 | 310 | None | None | 310 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 310 | N/A
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | June 1 - Sept 30 (Long Term) | 310 | 310 | None | None | N/A | 310 | N/A | N/A | N/A | N/A | N/A | N/A | 310 | N/A
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Near Term) | 310 | 175.91 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | 310 | N/A | N/A | 175.91 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Long Term) | 310 | 175.91 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | 310 | N/A | 175.91 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | Dec 1 - March 31 (Near Term) | 310 | 175.91 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 175.91 | N/A | N/A | N/A | N/A | N/A | 310
GEN-2017-210 | 02 NEBRASKA | Hybrid: Solar and Storage | Dec 1 - March 31 (Long Term) | 310 | 175.91 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 175.91 | N/A | N/A | N/A | N/A | N/A | 310
GEN-2017-234 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 115 | 0 | Non-Cnv | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 115 | 115
GEN-2017-234 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 115 | 0 | Non-Cnv | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 115 | 115
GEN-2017-234 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 115 | 115 | None | None | 115 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 115 | N/A
GEN-2017-234 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 115 | 115 | None | None | N/A | 115 | N/A | N/A | N/A | N/A | N/A | N/A | 115 | N/A
GEN-2017-234 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 115 | 0 | Non-Cnv | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 115 | 115
GEN-2017-234 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 115 | 0 | Non-Cnv | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 115 | 115
GEN-2017-234 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 115 | 65.25 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 65.25 | N/A | N/A | N/A | N/A | N/A | 115
GEN-2017-234 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 115 | 65.25 | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 ftlo P42:345:NPPD:BKR-RW-3302::::: | Replace Mark Moore 345/115 kV Transformer | N/A | N/A | N/A | 65.25 | N/A | N/A | N/A | N/A | N/A | 115
GEN-2017-108 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | 282.14 | N/A | N/A | 314.22 | 312.72 | N/A | N/A | 400 | 0 | 0
GEN-2017-108 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | N/A | 322.66 | N/A | 314.22 | N/A | 225.02 | N/A | 400 | 0 | 0
GEN-2017-108 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | 282.14 | N/A | N/A | N/A | 312.72 | N/A | N/A | N/A | 0 | N/A
GEN-2017-108 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | N/A | 322.66 | N/A | N/A | N/A | 225.02 | N/A | N/A | 0 | N/A
GEN-2017-108 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | 282.14 | N/A | N/A | 314.22 | 312.72 | N/A | N/A | 400 | 0 | 0
GEN-2017-108 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | N/A | 322.66 | N/A | 314.22 | N/A | 225.02 | N/A | 400 | 0 | 0
GEN-2017-108 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | N/A | N/A | N/A | 314.22 | N/A | N/A | N/A | 400 | N/A | 0
GEN-2017-108 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 400 | 0 | Stability | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | N/A | N/A | N/A | 314.22 | N/A | N/A | N/A | 400 | N/A | 0
GEN-2017-115 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 244 | 244 | None | None | N/A | N/A | 244 | N/A | N/A | N/A | N/A | N/A | 244 | 244
GEN-2017-115 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 244 | 244 | None | None | N/A | N/A | 244 | N/A | N/A | N/A | N/A | N/A | 244 | 244
GEN-2017-115 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 244 | 244 | None | None | 244 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 244 | N/A
GEN-2017-115 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 244 | 244 | None | None | N/A | 244 | N/A | N/A | N/A | N/A | N/A | N/A | 244 | N/A
GEN-2017-115 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 244 | 244 | None | None | N/A | N/A | 244 | N/A | N/A | N/A | N/A | N/A | 244 | 244
GEN-2017-115 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 244 | 244 | None | None | N/A | N/A | 244 | N/A | N/A | N/A | N/A | N/A | 244 | 244
GEN-2017-115 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 244 | 244 | None | None | N/A | N/A | N/A | 244 | N/A | N/A | N/A | N/A | N/A | 244
GEN-2017-115 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 244 | 244 | None | None | N/A | N/A | N/A | 244 | N/A | N/A | N/A | N/A | N/A | 244
GEN-2017-119 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 180 | 140.27 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | N/A | N/A | 140.27 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-119 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 180 | 140.27 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | N/A | N/A | 140.27 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-119 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 180 | 180 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | 180 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 180 | N/A
GEN-2017-119 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 180 | 180 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | N/A | 180 | N/A | N/A | N/A | N/A | N/A | N/A | 180 | N/A
GEN-2017-119 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 180 | 140.27 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | N/A | N/A | 140.27 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-119 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 180 | 140.27 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | N/A | N/A | 140.27 | N/A | N/A | N/A | N/A | N/A | 180 | 180
GEN-2017-119 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 180 | 180 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 180
GEN-2017-119 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 180 | 180 | 532865 NMANHT6 230 539639 ELMCREK6 230 1 ftlo P23:345:WERE:SUMM_345-218:: | Partly rebuild the Elm Creek to North Manhattan 230 kV line | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 180
GEN-2017-120 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 260 | 260 | None | None | N/A | N/A | 260 | N/A | N/A | N/A | N/A | N/A | 260 | 260
GEN-2017-120 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 260 | 260 | None | None | N/A | N/A | 260 | N/A | N/A | N/A | N/A | N/A | 260 | 260
GEN-2017-120 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 260 | 260 | None | None | 260 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 260 | N/A
GEN-2017-120 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 260 | 260 | None | None | N/A | 260 | N/A | N/A | N/A | N/A | N/A | N/A | 260 | N/A
GEN-2017-120 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 260 | 260 | None | None | N/A | N/A | 260 | N/A | N/A | N/A | N/A | N/A | 260 | 260
GEN-2017-120 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 260 | 260 | None | None | N/A | N/A | 260 | N/A | N/A | N/A | N/A | N/A | 260 | 260
GEN-2017-120 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 260 | 260 | None | None | N/A | N/A | N/A | 260 | N/A | N/A | N/A | N/A | N/A | 260
GEN-2017-120 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 260 | 260 | None | None | N/A | N/A | N/A | 260 | N/A | N/A | N/A | N/A | N/A | 260
GEN-2017-121 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 0
GEN-2017-121 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 0
GEN-2017-121 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A
GEN-2017-121 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 200 | N/A
GEN-2017-121 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 0
GEN-2017-121 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 0
GEN-2017-121 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 0
GEN-2017-121 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 0
GEN-2017-125 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2017-125 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2017-125 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 252 | 252 | None | None | 252 | N/A | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A
GEN-2017-125 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 252 | 252 | None | None | N/A | 252 | N/A | N/A | N/A | 252 | N/A | N/A | 252 | N/A
GEN-2017-125 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2017-125 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2017-125 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 252 | 252 | None | None | N/A | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252
GEN-2017-125 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 252 | 252 | None | None | N/A | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252
GEN-2017-131 | 03 CENTRAL | Storage | April 1 - May 31 (Near Term) | 29.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 29.6 | N/A | N/A | 29.6 | 29.6 | N/A | N/A | 29.6 | 29.6 | 0
GEN-2017-131 | 03 CENTRAL | Storage | April 1 - May 31 (Long Term) | 29.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 29.6 | N/A | 29.6 | N/A | 29.6 | N/A | 29.6 | 29.6 | 0
GEN-2017-131 | 03 CENTRAL | Storage | June 1 - Sept 30 (Near Term) | 29.6 | 29.6 | None | None | 29.6 | N/A | N/A | N/A | 29.6 | N/A | N/A | N/A | 29.6 | N/A
GEN-2017-131 | 03 CENTRAL | Storage | June 1 - Sept 30 (Long Term) | 29.6 | 29.6 | None | None | N/A | 29.6 | N/A | N/A | N/A | 29.6 | N/A | N/A | 29.6 | N/A
GEN-2017-131 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Near Term) | 29.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 29.6 | N/A | N/A | 29.6 | 29.6 | N/A | N/A | 29.6 | 29.6 | 0
GEN-2017-131 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Long Term) | 29.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 29.6 | N/A | 29.6 | N/A | 29.6 | N/A | 29.6 | 29.6 | 0
GEN-2017-131 | 03 CENTRAL | Storage | Dec 1 - March 31 (Near Term) | 29.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 29.6 | N/A | N/A | N/A | 29.6 | N/A | 0
GEN-2017-131 | 03 CENTRAL | Storage | Dec 1 - March 31 (Long Term) | 29.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 29.6 | N/A | N/A | N/A | 29.6 | N/A | 0
GEN-2017-183 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-183 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-183 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 400 | 232.18 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | 232.18 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 400 | N/A
GEN-2017-183 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 400 | 337.71 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | 337.71 | N/A | N/A | N/A | 5.64 | N/A | N/A | 400 | N/A
GEN-2017-183 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-183 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-183 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | N/A | N/A | 39.24 | N/A | N/A | N/A | 0 | N/A | 400
GEN-2017-183 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | N/A | N/A | 39.24 | N/A | N/A | N/A | 0 | N/A | 400
GEN-2017-184 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | 232.18 | N/A | N/A | 39.24 | 0 | N/A | N/A | 0 | 400 | 400
GEN-2017-184 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | 337.71 | N/A | 39.24 | N/A | 5.64 | N/A | 0 | 400 | 400
GEN-2017-184 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 400 | 232.18 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | 232.18 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 400 | N/A
GEN-2017-184 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 400 | 337.71 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | 337.71 | N/A | N/A | N/A | 5.64 | N/A | N/A | 400 | N/A
GEN-2017-184 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | 232.18 | N/A | N/A | 39.24 | 0 | N/A | N/A | 0 | 400 | 400
GEN-2017-184 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | 337.71 | N/A | 39.24 | N/A | 5.64 | N/A | 0 | 400 | 400
GEN-2017-184 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | N/A | N/A | 39.24 | N/A | N/A | N/A | 0 | N/A | 400
GEN-2017-184 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 400 | 39.24 | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 ftlo 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | N/A | N/A | N/A | 39.24 | N/A | N/A | N/A | 0 | N/A | 400
GEN-2017-188 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 130 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 130 | N/A | N/A | 130 | N/A | N/A | N/A | N/A | 130 | 0
GEN-2017-188 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 130 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 130 | N/A | 130 | N/A | N/A | N/A | N/A | 130 | 0
GEN-2017-188 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 130 | 130 | None | None | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 130 | N/A
GEN-2017-188 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 130 | 130 | None | None | N/A | 130 | N/A | N/A | N/A | N/A | N/A | N/A | 130 | N/A
GEN-2017-188 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 130 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 130 | N/A | N/A | 130 | N/A | N/A | N/A | N/A | 130 | 0
GEN-2017-188 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 130 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 130 | N/A | 130 | N/A | N/A | N/A | N/A | 130 | 0
GEN-2017-188 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 130 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 130 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2017-188 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 130 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 130 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2017-195 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 500.4 | 500.4 | None | None | 408.59 | N/A | N/A | 500.4 | 500.4 | N/A | N/A | 500.4 | 500.4 | 500.4
GEN-2017-195 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 500.4 | 500.4 | None | None | N/A | 462.2 | N/A | 500.4 | N/A | 500.4 | N/A | 500.4 | 500.4 | 500.4
GEN-2017-195 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 500.4 | 500.4 | None | None | 408.59 | N/A | N/A | N/A | 500.4 | N/A | N/A | N/A | 500.4 | N/A
GEN-2017-195 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 500.4 | 500.4 | None | None | N/A | 462.2 | N/A | N/A | N/A | 500.4 | N/A | N/A | 500.4 | N/A
GEN-2017-195 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 500.4 | 500.4 | None | None | 408.59 | N/A | N/A | 500.4 | 500.4 | N/A | N/A | 500.4 | 500.4 | 500.4
GEN-2017-195 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 500.4 | 500.4 | None | None | N/A | 462.2 | N/A | 500.4 | N/A | 500.4 | N/A | 500.4 | 500.4 | 500.4
GEN-2017-195 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 500.4 | 500.4 | None | None | N/A | N/A | N/A | 500.4 | N/A | N/A | N/A | 500.4 | N/A | 500.4
GEN-2017-195 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 500.4 | 500.4 | None | None | N/A | N/A | N/A | 500.4 | N/A | N/A | N/A | 500.4 | N/A | 500.4
GEN-2017-196 | 03 CENTRAL | Storage | April 1 - May 31 (Near Term) | 128 | 128 | None | None | 104.51 | N/A | N/A | 128 | 128 | N/A | N/A | 128 | 128 | 128
GEN-2017-196 | 03 CENTRAL | Storage | April 1 - May 31 (Long Term) | 128 | 128 | None | None | N/A | 118.23 | N/A | 128 | N/A | 128 | N/A | 128 | 128 | 128
GEN-2017-196 | 03 CENTRAL | Storage | June 1 - Sept 30 (Near Term) | 128 | 128 | None | None | 104.51 | N/A | N/A | N/A | 128 | N/A | N/A | N/A | 128 | N/A
GEN-2017-196 | 03 CENTRAL | Storage | June 1 - Sept 30 (Long Term) | 128 | 128 | None | None | N/A | 118.23 | N/A | N/A | N/A | 128 | N/A | N/A | 128 | N/A
GEN-2017-196 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Near Term) | 128 | 128 | None | None | 104.51 | N/A | N/A | 128 | 128 | N/A | N/A | 128 | 128 | 128
GEN-2017-196 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Long Term) | 128 | 128 | None | None | N/A | 118.23 | N/A | 128 | N/A | 128 | N/A | 128 | 128 | 128
GEN-2017-196 | 03 CENTRAL | Storage | Dec 1 - March 31 (Near Term) | 128 | 128 | None | None | N/A | N/A | N/A | 128 | N/A | N/A | N/A | 128 | N/A | 128
GEN-2017-196 | 03 CENTRAL | Storage | Dec 1 - March 31 (Long Term) | 128 | 128 | None | None | N/A | N/A | N/A | 128 | N/A | N/A | N/A | 128 | N/A | 128
GEN-2017-202 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 200 | 200
GEN-2017-202 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 200 | 200
GEN-2017-202 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A
GEN-2017-202 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 200 | N/A
GEN-2017-202 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 200 | 200
GEN-2017-202 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 200 | 200
GEN-2017-202 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2017-202 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | April 1 - May 31 (Near Term) | 300 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 300 | N/A | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 0
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | April 1 - May 31 (Long Term) | 300 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 300 | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 0
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | June 1 - Sept 30 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | June 1 - Sept 30 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 300 | N/A | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 0
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 300 | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 0
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2017-209 | 03 CENTRAL | Hybrid: Solar and Storage | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2017-220 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 0
GEN-2017-220 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 0
GEN-2017-220 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 201.6 | 201.6 | None | None | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A
GEN-2017-220 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 201.6 | 201.6 | None | None | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | 201.6 | N/A
GEN-2017-220 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 0
GEN-2017-220 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 0
GEN-2017-220 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 0
GEN-2017-220 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 0
GEN-2017-221 | 03 CENTRAL | Storage | April 1 - May 31 (Near Term) | 152 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 152 | N/A | N/A | 152 | 152 | N/A | N/A | 152 | 152 | 0
GEN-2017-221 | 03 CENTRAL | Storage | April 1 - May 31 (Long Term) | 152 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 152 | N/A | 152 | N/A | 152 | N/A | 152 | 152 | 0
GEN-2017-221 | 03 CENTRAL | Storage | June 1 - Sept 30 (Near Term) | 152 | 152 | None | None | 152 | N/A | N/A | N/A | 152 | N/A | N/A | N/A | 152 | N/A
GEN-2017-221 | 03 CENTRAL | Storage | June 1 - Sept 30 (Long Term) | 152 | 152 | None | None | N/A | 152 | N/A | N/A | N/A | 152 | N/A | N/A | 152 | N/A
GEN-2017-221 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Near Term) | 152 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 152 | N/A | N/A | 152 | 152 | N/A | N/A | 152 | 152 | 0
GEN-2017-221 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Long Term) | 152 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 152 | N/A | 152 | N/A | 152 | N/A | 152 | 152 | 0
GEN-2017-221 | 03 CENTRAL | Storage | Dec 1 - March 31 (Near Term) | 152 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 152 | N/A | N/A | N/A | 152 | N/A | 0
GEN-2017-221 | 03 CENTRAL | Storage | Dec 1 - March 31 (Long Term) | 152 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 152 | N/A | N/A | N/A | 152 | N/A | 0
GEN-2017-226 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 0
GEN-2017-226 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 0
GEN-2017-226 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 201.6 | 201.6 | None | None | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A
GEN-2017-226 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 201.6 | 201.6 | None | None | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | 201.6 | N/A
GEN-2017-226 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 0
GEN-2017-226 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 0
GEN-2017-226 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 0
GEN-2017-226 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 0
GEN-2017-227 | 03 CENTRAL | Storage | April 1 - May 31 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 0
GEN-2017-227 | 03 CENTRAL | Storage | April 1 - May 31 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 0
GEN-2017-227 | 03 CENTRAL | Storage | June 1 - Sept 30 (Near Term) | 201.6 | 201.6 | None | None | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A
GEN-2017-227 | 03 CENTRAL | Storage | June 1 - Sept 30 (Long Term) | 201.6 | 201.6 | None | None | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | 201.6 | N/A
GEN-2017-227 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 0
GEN-2017-227 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 0
GEN-2017-227 | 03 CENTRAL | Storage | Dec 1 - March 31 (Near Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 0
GEN-2017-227 | 03 CENTRAL | Storage | Dec 1 - March 31 (Long Term) | 201.6 | 0 | Stability | Line - Wolf Creek - Blackberry 345 kV | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 0
GEN-2017-117 | 04 SOUTHEAST | Storage | April 1 - May 31 (Near Term) | 19.8 | 19.8 | None | None | 19.8 | N/A | N/A | 19.8 | 0 | N/A | N/A | 19.8 | 19.8 | 19.8
GEN-2017-117 | 04 SOUTHEAST | Storage | April 1 - May 31 (Long Term) | 19.8 | 19.8 | None | None | N/A | 19.8 | N/A | 19.8 | N/A | 19.8 | N/A | 19.8 | 19.8 | 19.8
GEN-2017-117 | 04 SOUTHEAST | Storage | June 1 - Sept 30 (Near Term) | 19.8 | 19.8 | None | None | 19.8 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 19.8 | N/A
GEN-2017-117 | 04 SOUTHEAST | Storage | June 1 - Sept 30 (Long Term) | 19.8 | 19.8 | None | None | N/A | 19.8 | N/A | N/A | N/A | 19.8 | N/A | N/A | 19.8 | N/A
GEN-2017-117 | 04 SOUTHEAST | Storage | Oct 1 - Nov 30 (Near Term) | 19.8 | 19.8 | None | None | 19.8 | N/A | N/A | 19.8 | 0 | N/A | N/A | 19.8 | 19.8 | 19.8
GEN-2017-117 | 04 SOUTHEAST | Storage | Oct 1 - Nov 30 (Long Term) | 19.8 | 19.8 | None | None | N/A | 19.8 | N/A | 19.8 | N/A | 19.8 | N/A | 19.8 | 19.8 | 19.8
GEN-2017-117 | 04 SOUTHEAST | Storage | Dec 1 - March 31 (Near Term) | 19.8 | 19.8 | None | None | N/A | N/A | N/A | 19.8 | N/A | N/A | N/A | 19.8 | N/A | 19.8
GEN-2017-117 | 04 SOUTHEAST | Storage | Dec 1 - March 31 (Long Term) | 19.8 | 19.8 | None | None | N/A | N/A | N/A | 19.8 | N/A | N/A | N/A | 19.8 | N/A | 19.8
GEN-2017-132 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-132 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-132 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 400 | 400 | None | None | 262.54 | N/A | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A
GEN-2017-132 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 400 | 400 | None | None | N/A | 375.86 | N/A | N/A | N/A | 400 | N/A | N/A | 400 | N/A
GEN-2017-132 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-132 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 400 | 400 | None | None | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400 | 400
GEN-2017-132 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 400 | 400 | None | None | N/A | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400
GEN-2017-132 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 400 | 400 | None | None | N/A | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | 400
GEN-2017-133 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 200 | 200 | None | None | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 200
GEN-2017-133 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 200 | 200 | None | None | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 200
GEN-2017-133 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 200 | 200 | None | None | 131.27 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A
GEN-2017-133 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 200 | 200 | None | None | N/A | 187.93 | N/A | N/A | N/A | 200 | N/A | N/A | 200 | N/A
GEN-2017-133 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 200 | None | None | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 200
GEN-2017-133 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 200 | None | None | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200 | 200
GEN-2017-133 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2017-133 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2017-134 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-134 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-134 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 250 | 250 | None | None | 164.09 | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A
GEN-2017-134 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 250 | 250 | None | None | N/A | 234.91 | N/A | N/A | N/A | 250 | N/A | N/A | 250 | N/A
GEN-2017-134 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-134 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250 | 250
GEN-2017-134 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2017-134 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2017-137 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 295 | 295 | None | None | N/A | N/A | 295 | N/A | N/A | N/A | 295 | N/A | 295 | 295
GEN-2017-137 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 295 | 295 | None | None | N/A | N/A | 295 | N/A | N/A | N/A | 295 | N/A | 295 | 295
GEN-2017-137 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 295 | 295 | None | None | 193.63 | N/A | N/A | N/A | 295 | N/A | N/A | N/A | 295 | N/A
GEN-2017-137 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 295 | 295 | None | None | N/A | 277.2 | N/A | N/A | N/A | 295 | N/A | N/A | 295 | N/A
GEN-2017-137 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 295 | 295 | None | None | N/A | N/A | 295 | N/A | N/A | N/A | 295 | N/A | 295 | 295
GEN-2017-137 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 295 | 295 | None | None | N/A | N/A | 295 | N/A | N/A | N/A | 295 | N/A | 295 | 295
GEN-2017-137 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 295 | 295 | None | None | N/A | N/A | N/A | 295 | N/A | N/A | N/A | 295 | N/A | 295
GEN-2017-137 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 295 | 295 | None | None | N/A | N/A | N/A | 295 | N/A | N/A | N/A | 295 | N/A | 295
GEN-2017-140 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 160 | 160 | None | None | 160 | N/A | N/A | 160 | 160 | N/A | N/A | 160 | 160 | 160
GEN-2017-140 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 160 | 160 | None | None | N/A | 160 | N/A | 160 | N/A | 160 | N/A | 160 | 160 | 160
GEN-2017-140 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 160 | 160 | None | None | 160 | N/A | N/A | N/A | 160 | N/A | N/A | N/A | 160 | N/A
GEN-2017-140 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 160 | 160 | None | None | N/A | 160 | N/A | N/A | N/A | 160 | N/A | N/A | 160 | N/A
GEN-2017-140 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 160 | 160 | None | None | 160 | N/A | N/A | 160 | 160 | N/A | N/A | 160 | 160 | 160
GEN-2017-140 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 160 | 160 | None | None | N/A | 160 | N/A | 160 | N/A | 160 | N/A | 160 | 160 | 160
GEN-2017-140 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 160 | 160 | None | None | N/A | N/A | N/A | 160 | N/A | N/A | N/A | 160 | N/A | 160
GEN-2017-140 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 160 | 160 | None | None | N/A | N/A | N/A | 160 | N/A | N/A | N/A | 160 | N/A | 160
GEN-2017-141 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 241.7 | 241.7 | None | None | 241.7 | N/A | N/A | 241.7 | 241.7 | N/A | N/A | 241.7 | 241.7 | 241.7
GEN-2017-141 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 241.7 | 241.7 | None | None | N/A | 241.7 | N/A | 241.7 | N/A | 241.7 | N/A | 241.7 | 241.7 | 241.7
GEN-2017-141 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 241.7 | 241.7 | None | None | 241.7 | N/A | N/A | N/A | 241.7 | N/A | N/A | N/A | 241.7 | N/A
GEN-2017-141 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 241.7 | 241.7 | None | None | N/A | 241.7 | N/A | N/A | N/A | 241.7 | N/A | N/A | 241.7 | N/A
GEN-2017-141 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 241.7 | 241.7 | None | None | 241.7 | N/A | N/A | 241.7 | 241.7 | N/A | N/A | 241.7 | 241.7 | 241.7
GEN-2017-141 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 241.7 | 241.7 | None | None | N/A | 241.7 | N/A | 241.7 | N/A | 241.7 | N/A | 241.7 | 241.7 | 241.7
GEN-2017-141 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 241.7 | 241.7 | None | None | N/A | N/A | N/A | 241.7 | N/A | N/A | N/A | 241.7 | N/A | 241.7
GEN-2017-141 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 241.7 | 241.7 | None | None | N/A | N/A | N/A | 241.7 | N/A | N/A | N/A | 241.7 | N/A | 241.7
GEN-2017-149 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 258 | 258 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 258 | N/A | 258 | 258
GEN-2017-149 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 258 | 258 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 258 | N/A | 258 | 258
GEN-2017-149 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 258 | 258 | None | None | 258 | N/A | N/A | N/A | 258 | N/A | N/A | N/A | 258 | N/A
GEN-2017-149 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 258 | 258 | None | None | N/A | 258 | N/A | N/A | N/A | 258 | N/A | N/A | 258 | N/A
GEN-2017-149 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 258 | 258 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 258 | N/A | 258 | 258
GEN-2017-149 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 258 | 258 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 258 | N/A | 258 | 258
GEN-2017-149 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 258 | 258 | None | None | N/A | N/A | N/A | 258 | N/A | N/A | N/A | 258 | N/A | 258
GEN-2017-149 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 258 | 258 | None | None | N/A | N/A | N/A | 258 | N/A | N/A | N/A | 258 | N/A | 258
GEN-2017-150 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 250 | 26.27 | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 ftlo P13:138-345:OKGE:BKRBKR_3W021:::: | Multi - Minco - Pleasant Valley - Draper 345 kV | 0 | N/A | N/A | 250 | 26.27 | N/A | N/A | 250 | 250 | 250
GEN-2017-150 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 250 | 234.26 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 ftlo P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | Multi - Border - Woodward 345 kV Tap | N/A | 0 | N/A | 250 | N/A | 234.26 | N/A | 250 | 250 | 250
GEN-2017-150 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 250 | 26.27 | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 ftlo P13:138-345:OKGE:BKRBKR_3W021:::: | Multi - Minco - Pleasant Valley - Draper 345 kV | 0 | N/A | N/A | N/A | 26.27 | N/A | N/A | N/A | 250 | N/A
GEN-2017-150 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 250 | 234.26 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 ftlo P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | Multi - Border - Woodward 345 kV Tap | N/A | 0 | N/A | N/A | N/A | 234.26 | N/A | N/A | 250 | N/A
GEN-2017-150 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 250 | 26.27 | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 ftlo P13:138-345:OKGE:BKRBKR_3W021:::: | Multi - Minco - Pleasant Valley - Draper 345 kV | 0 | N/A | N/A | 250 | 26.27 | N/A | N/A | 250 | 250 | 250
GEN-2017-150 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 250 | 234.26 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 ftlo P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | Multi - Border - Woodward 345 kV Tap | N/A | 0 | N/A | 250 | N/A | 234.26 | N/A | 250 | 250 | 250
GEN-2017-150 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2017-150 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2017-154 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 255 | 255 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 255 | N/A | 255 | 255
GEN-2017-154 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 255 | 255 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 255 | N/A | 255 | 255
GEN-2017-154 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 255 | 255 | None | None | 255 | N/A | N/A | N/A | 255 | N/A | N/A | N/A | 255 | N/A
GEN-2017-154 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 255 | 255 | None | None | N/A | 255 | N/A | N/A | N/A | 255 | N/A | N/A | 255 | N/A
GEN-2017-154 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 255 | 255 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 255 | N/A | 255 | 255
GEN-2017-154 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 255 | 255 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 255 | N/A | 255 | 255
GEN-2017-154 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 255 | 255 | None | None | N/A | N/A | N/A | 255 | N/A | N/A | N/A | 255 | N/A | 255
GEN-2017-154 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 255 | 255 | None | None | N/A | N/A | N/A | 255 | N/A | N/A | N/A | 255 | N/A | 255
GEN-2017-164 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | 26.27 | N/A | N/A | 250 | 250 | 250
GEN-2017-164 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | 250 | N/A | 250 | 250 | 250
GEN-2017-164 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | N/A | 26.27 | N/A | N/A | N/A | 250 | N/A
GEN-2017-164 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | N/A | N/A | 250 | N/A | N/A | 250 | N/A
GEN-2017-164 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | 26.27 | N/A | N/A | 250 | 250 | 250
GEN-2017-164 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | 250 | N/A | 250 | 250 | 250
GEN-2017-164 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2017-164 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2017-167 | 04 SOUTHEAST | Storage | April 1 - May 31 (Near Term) | 52 | 52 | None | None | 52 | N/A | N/A | 52 | 52 | N/A | N/A | 52 | 52 | 52
GEN-2017-167 | 04 SOUTHEAST | Storage | April 1 - May 31 (Long Term) | 52 | 52 | None | None | N/A | 52 | N/A | 52 | N/A | 52 | N/A | 52 | 52 | 52
GEN-2017-167 | 04 SOUTHEAST | Storage | June 1 - Sept 30 (Near Term) | 52 | 52 | None | None | 52 | N/A | N/A | N/A | 52 | N/A | N/A | N/A | 52 | N/A
GEN-2017-167 | 04 SOUTHEAST | Storage | June 1 - Sept 30 (Long Term) | 52 | 52 | None | None | N/A | 52 | N/A | N/A | N/A | 52 | N/A | N/A | 52 | N/A
GEN-2017-167 | 04 SOUTHEAST | Storage | Oct 1 - Nov 30 (Near Term) | 52 | 52 | None | None | 52 | N/A | N/A | 52 | 52 | N/A | N/A | 52 | 52 | 52
GEN-2017-167 | 04 SOUTHEAST | Storage | Oct 1 - Nov 30 (Long Term) | 52 | 52 | None | None | N/A | 52 | N/A | 52 | N/A | 52 | N/A | 52 | 52 | 52
GEN-2017-167 | 04 SOUTHEAST | Storage | Dec 1 - March 31 (Near Term) | 52 | 52 | None | None | N/A | N/A | N/A | 52 | N/A | N/A | N/A | 52 | N/A | 52
GEN-2017-167 | 04 SOUTHEAST | Storage | Dec 1 - March 31 (Long Term) | 52 | 52 | None | None | N/A | N/A | N/A | 52 | N/A | N/A | N/A | 52 | N/A | 52
GEN-2017-171 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 0 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2017-171 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 0 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2017-171 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 0 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2017-171 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 0 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2017-171 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 0 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2017-171 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 0 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2017-171 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2017-171 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2017-172 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 50 | 50 | None | None | 0 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2017-172 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 50 | 50 | None | None | N/A | 0 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2017-172 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 50 | 50 | None | None | 0 | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A
GEN-2017-172 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 50 | 50 | None | None | N/A | 0 | N/A | N/A | N/A | 50 | N/A | N/A | 50 | N/A
GEN-2017-172 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 50 | 50 | None | None | 0 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2017-172 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 50 | 50 | None | None | N/A | 0 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2017-172 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2017-172 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2017-173 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 50 | 50 | None | None | 0 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2017-173 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 50 | 50 | None | None | N/A | 0 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2017-173 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 50 | 50 | None | None | 0 | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A
GEN-2017-173 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 50 | 50 | None | None | N/A | 0 | N/A | N/A | N/A | 50 | N/A | N/A | 50 | N/A
GEN-2017-173 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 50 | 50 | None | None | 0 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2017-173 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 50 | 50 | None | None | N/A | 0 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2017-173 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2017-173 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2017-178 | 04 SOUTHEAST | Storage | April 1 - May 31 (Near Term) | 52 | 52 | None | None | 52 | N/A | N/A | 52 | 5.46 | N/A | N/A | 52 | 52 | 52
GEN-2017-178 | 04 SOUTHEAST | Storage | April 1 - May 31 (Long Term) | 52 | 52 | None | None | N/A | 52 | N/A | 52 | N/A | 52 | N/A | 52 | 52 | 52
GEN-2017-178 | 04 SOUTHEAST | Storage | June 1 - Sept 30 (Near Term) | 52 | 52 | None | None | 52 | N/A | N/A | N/A | 5.46 | N/A | N/A | N/A | 52 | N/A
GEN-2017-178 | 04 SOUTHEAST | Storage | June 1 - Sept 30 (Long Term) | 52 | 52 | None | None | N/A | 52 | N/A | N/A | N/A | 52 | N/A | N/A | 52 | N/A
GEN-2017-178 | 04 SOUTHEAST | Storage | Oct 1 - Nov 30 (Near Term) | 52 | 52 | None | None | 52 | N/A | N/A | 52 | 5.46 | N/A | N/A | 52 | 52 | 52
GEN-2017-178 | 04 SOUTHEAST | Storage | Oct 1 - Nov 30 (Long Term) | 52 | 52 | None | None | N/A | 52 | N/A | 52 | N/A | 52 | N/A | 52 | 52 | 52
GEN-2017-178 | 04 SOUTHEAST | Storage | Dec 1 - March 31 (Near Term) | 52 | 52 | None | None | N/A | N/A | N/A | 52 | N/A | N/A | N/A | 52 | N/A | 52
GEN-2017-178 | 04 SOUTHEAST | Storage | Dec 1 - March 31 (Long Term) | 52 | 52 | None | None | N/A | N/A | N/A | 52 | N/A | N/A | N/A | 52 | N/A | 52
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | April 1 - May 31 (Near Term) | 210 | 210 | None | None | 210 | N/A | N/A | 210 | N/A | N/A | N/A | N/A | 210 | 210
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | April 1 - May 31 (Long Term) | 210 | 210 | None | None | N/A | 210 | N/A | 210 | N/A | N/A | N/A | N/A | 210 | 210
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | June 1 - Sept 30 (Near Term) | 210 | 210 | None | None | 210 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 210 | N/A
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | June 1 - Sept 30 (Long Term) | 210 | 210 | None | None | N/A | 210 | N/A | N/A | N/A | N/A | N/A | N/A | 210 | N/A
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Near Term) | 210 | 210 | None | None | 210 | N/A | N/A | 210 | N/A | N/A | N/A | N/A | 210 | 210
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Long Term) | 210 | 210 | None | None | N/A | 210 | N/A | 210 | N/A | N/A | N/A | N/A | 210 | 210
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | Dec 1 - March 31 (Near Term) | 210 | 210 | None | None | N/A | N/A | N/A | 210 | N/A | N/A | N/A | N/A | N/A | 210
GEN-2017-203 | 04 SOUTHEAST | Hybrid: Solar and Storage | Dec 1 - March 31 (Long Term) | 210 | 210 | None | None | N/A | N/A | N/A | 210 | N/A | N/A | N/A | N/A | N/A | 210
GEN-2017-230 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 72.5 | 72.5 | None | None | 47.58 | N/A | N/A | 72.5 | 72.5 | N/A | N/A | 72.5 | 72.5 | 72.5
GEN-2017-230 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 72.5 | 72.5 | None | None | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | 72.5 | 72.5
GEN-2017-230 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 72.5 | 72.5 | None | None | 47.58 | N/A | N/A | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A
GEN-2017-230 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 72.5 | 72.5 | None | None | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A | N/A | 72.5 | N/A
GEN-2017-230 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 72.5 | 72.5 | None | None | 47.58 | N/A | N/A | 72.5 | 72.5 | N/A | N/A | 72.5 | 72.5 | 72.5
GEN-2017-230 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 72.5 | 72.5 | None | None | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | 72.5 | 72.5
GEN-2017-230 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 72.5 | 72.5 | None | None | N/A | N/A | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A | 72.5
GEN-2017-230 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 72.5 | 72.5 | None | None | N/A | N/A | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A | 72.5
GEN-2017-231 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 72.5 | 72.5 | None | None | 72.5 | N/A | N/A | 72.5 | 72.5 | N/A | N/A | 72.5 | 72.5 | 72.5
GEN-2017-231 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 72.5 | 72.5 | None | None | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | 72.5 | 72.5
GEN-2017-231 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 72.5 | 72.5 | None | None | 72.5 | N/A | N/A | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A
GEN-2017-231 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 72.5 | 72.5 | None | None | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A | N/A | 72.5 | N/A
GEN-2017-231 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 72.5 | 72.5 | None | None | 72.5 | N/A | N/A | 72.5 | 72.5 | N/A | N/A | 72.5 | 72.5 | 72.5
GEN-2017-231 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 72.5 | 72.5 | None | None | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | N/A | 72.5 | 72.5 | 72.5
GEN-2017-231 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 72.5 | 72.5 | None | None | N/A | N/A | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A | 72.5
GEN-2017-231 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 72.5 | 72.5 | None | None | N/A | N/A | N/A | 72.5 | N/A | N/A | N/A | 72.5 | N/A | 72.5
GEN-2017-232 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 52.2 | 48.12 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | 16.23 | N/A | N/A | 3.65 | 49.38 | N/A | N/A | 48.12 | 52.2 | 52.2
GEN-2017-232 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 52.2 | 48.12 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | N/A | 24.84 | N/A | 3.65 | N/A | 49.18 | N/A | 48.12 | 52.2 | 52.2
GEN-2017-232 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 52.2 | 49.38 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | 16.23 | N/A | N/A | N/A | 49.38 | N/A | N/A | N/A | 52.2 | N/A
GEN-2017-232 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 52.2 | 49.18 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | N/A | 24.84 | N/A | N/A | N/A | 49.18 | N/A | N/A | 52.2 | N/A
GEN-2017-232 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 52.2 | 48.12 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | 16.23 | N/A | N/A | 3.65 | 49.38 | N/A | N/A | 48.12 | 52.2 | 52.2
GEN-2017-232 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 52.2 | 48.12 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | N/A | 24.84 | N/A | 3.65 | N/A | 49.18 | N/A | 48.12 | 52.2 | 52.2
GEN-2017-232 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 52.2 | 48.12 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | N/A | N/A | N/A | 3.65 | N/A | N/A | N/A | 48.12 | N/A | 52.2
GEN-2017-232 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 52.2 | 48.12 | 505602 S BROWN4 138 515157 BROWN 4 138 1 ftlo P12:138:OKGE:BKRBKR261:::: | SPA Brown to Brown 138 kV Equipment Upgrade | N/A | N/A | N/A | 3.65 | N/A | N/A | N/A | 48.12 | N/A | 52.2
GEN-2017-233 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 215 | 215 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 215 | N/A | 215 | 215
GEN-2017-233 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 215 | 215 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 215 | N/A | 215 | 215
GEN-2017-233 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 215 | 22.59 | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 ftlo P13:138-345:OKGE:BKRBKR_3W021:::: | Multi - Minco - Pleasant Valley - Draper 345 kV | 0 | N/A | N/A | N/A | 22.59 | N/A | N/A | N/A | 215 | N/A
GEN-2017-233 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 215 | 201.46 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 ftlo P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | Multi - Border - Woodward 345 kV Tap | N/A | 0 | N/A | N/A | N/A | 201.46 | N/A | N/A | 215 | N/A
GEN-2017-233 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 215 | 215 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 215 | N/A | 215 | 215
GEN-2017-233 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 215 | 215 | None | None | N/A | N/A | 0 | N/A | N/A | N/A | 215 | N/A | 215 | 215
GEN-2017-233 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 215 | 215 | None | None | N/A | N/A | N/A | 215 | N/A | N/A | N/A | 215 | N/A | 215
GEN-2017-233 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 215 | 215 | None | None | N/A | N/A | N/A | 215 | N/A | N/A | N/A | 215 | N/A | 215
GEN-2017-146 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 151.8 | 151.8 | None | None | N/A | N/A | 151.8 | N/A | N/A | N/A | N/A | N/A | 151.8 | 151.8
GEN-2017-146 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 151.8 | 151.8 | None | None | N/A | N/A | 151.8 | N/A | N/A | N/A | N/A | N/A | 151.8 | 151.8
GEN-2017-146 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 151.8 | 151.8 | None | None | 151.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 151.8 | N/A
GEN-2017-146 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 151.8 | 151.8 | None | None | N/A | 151.8 | N/A | N/A | N/A | N/A | N/A | N/A | 151.8 | N/A
GEN-2017-146 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 151.8 | 151.8 | None | None | N/A | N/A | 151.8 | N/A | N/A | N/A | N/A | N/A | 151.8 | 151.8
GEN-2017-146 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 151.8 | 151.8 | None | None | N/A | N/A | 151.8 | N/A | N/A | N/A | N/A | N/A | 151.8 | 151.8
GEN-2017-146 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 151.8 | 151.8 | None | None | N/A | N/A | N/A | 151.8 | N/A | N/A | N/A | N/A | N/A | 151.8
GEN-2017-146 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 151.8 | 151.8 | None | None | N/A | N/A | N/A | 151.8 | N/A | N/A | N/A | N/A | N/A | 151.8
GEN-2017-151 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-151 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-151 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-151 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-151 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-151 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-151 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300
GEN-2017-151 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300
GEN-2017-158 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 265 | 265 | None | None | N/A | N/A | 265 | N/A | N/A | N/A | N/A | N/A | 265 | 265
GEN-2017-158 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 265 | 265 | None | None | N/A | N/A | 265 | N/A | N/A | N/A | N/A | N/A | 265 | 265
GEN-2017-158 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 265 | 265 | None | None | 265 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 265 | N/A
GEN-2017-158 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 265 | 265 | None | None | N/A | 265 | N/A | N/A | N/A | N/A | N/A | N/A | 265 | N/A
GEN-2017-158 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 265 | 265 | None | None | N/A | N/A | 265 | N/A | N/A | N/A | N/A | N/A | 265 | 265
GEN-2017-158 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 265 | 265 | None | None | N/A | N/A | 265 | N/A | N/A | N/A | N/A | N/A | 265 | 265
GEN-2017-158 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 265 | 265 | None | None | N/A | N/A | N/A | 265 | N/A | N/A | N/A | N/A | N/A | 265
GEN-2017-158 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 265 | 265 | None | None | N/A | N/A | N/A | 265 | N/A | N/A | N/A | N/A | N/A | 265
GEN-2017-187 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2017-187 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2017-187 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 150 | N/A
GEN-2017-187 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | N/A | N/A | N/A | 150 | N/A
GEN-2017-187 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2017-187 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2017-187 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | N/A | N/A | 150
GEN-2017-187 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | N/A | N/A | 150
GEN-2017-239 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-239 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-239 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-239 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2017-239 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-239 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | 300 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2017-239 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300
GEN-2017-239 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
01ALL | DISIS-2017-002 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
01ALL | DISIS-2017-002 | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
01ALL | DISIS-2017-002 | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
01ALL | DISIS-2017-002 | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26SP, 26WP | P12:161:WAPA:DENISON-EXIRA:1 | 72 | 80 | <90% | 137.61 |  |  |  | Denison to Boyer 69kV Terminal Upgrade
01ALL | DISIS-2017-002 | ERIS | Thermal | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 23SP, 26L | 652526 UTICAJC4 230 655484 RASMUSN-ER4 230 1 | 120 | 120 | <90% | 108.27 |  |  |  | Utica to Napa 115kV Rating Update
01ALL | DISIS-2017-002 | ERIS | Thermal | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 26WP | P12:115:UMZ:# 5503 #: PROPER N-1 (LINE) FOR 603023-652440-1 | 200 | 203 | <90% | 101.99 |  |  |  | Logan 230-115 kV Transformer Rating Update
01ALL | DISIS-2017-002 CF | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
01ALL | DISIS-2017-002 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
01ALL | DISIS-2017-002 CF | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
01ALL | DISIS-2017-002 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 23SP | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 23SP | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 | ERIS | Thermal | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 26WP, 26L | P42:345:NPPD:BKR-RW-3302::::: | 336 | 336 | <90% | 116.89 |  |  |  | Replace Mark Moore 345/115 kV Transformer
02ALL | DISIS-2017-002 | ERIS | Thermal | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 26WP, 26L | P42:345:NPPD:BKR-RW-3302::::: | 336 | 336 | <90% | 113.25 |  |  |  | Replace Mark Moore 345/115 kV Transformer
02ALL | DISIS-2017-002 | ERIS | Thermal | None | 23SP, 26SP | None | [7 empty] | None
02ALL | DISIS-2017-002 | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | DISIS-2017-002 | ERIS | Non-Converge | None | 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | DISIS-2017-002 | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 23SP, 26L, 26SP | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | 720 | 720 | 102.34 | 133.98 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 23SP, 26L, 26SP | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | 720 | 720 | 102.34 | 133.98 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 23SP, 26L, 26SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | 720 | 720 | 102.34 | 133.98 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 652506 FTTHOMP3 345 996799 FT2 KU1B 230 1 | 23SP | PROXY_P4_345kV_POI_640510_2 | 250 | 313 | <90% | 101.88 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 652507 FTTHOMP4 230 996799 FT2 KU1B 230 1 | 23SP | PROXY_P4_345kV_POI_640510_2 | 250 | 313 | <90% | 102.64 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 23SP, 26L, 26SP | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | 717 | 717 | 102.24 | 134 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 23SP, 26L, 26SP | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | 717 | 717 | 102.24 | 134 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 23SP, 26L, 26SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | 717 | 717 | 102.24 | 134 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Stability | Active power oscillations observed at several nearby generating sites following the event. | 25S, 25W | GROUP2_LOCAL_P1_Fault79 | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP, 26L | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP, 26L | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP, 26L | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 26L | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 26L | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 26L | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 26L | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 26L | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Non-Converge | Non-Converge | 26L | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | [7 empty] | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02ALL | DISIS-2017-002 CF | ERIS | Thermal | None | 26WP | None | [7 empty] | None
02ALL | DISIS-2017-002 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | DISIS-2017-002 | ERIS | Stability | Inadequate reactive support to increase the stabilized voltage above the 0.9 p.u threshold at terminal | 25S, 25W | GROUP3_P1_LOCAL_FAULT577 | [7 empty] | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
03ALL | DISIS-2017-002 | ERIS | Thermal | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 26L | P23:345:WERE:SUMM_345-218:: | 324 | 359 | <90% | 107.59 |  |  |  | Partly rebuild the Elm Creek to North Manhattan 230 kV line
03ALL | DISIS-2017-002 | ERIS | Thermal | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 26L | P23:345:WERE:SUMM-345-218:::EHV: | 324 | 359 | <90% | 107.59 |  |  |  | Partly rebuild the Elm Creek to North Manhattan 230 kV line
03ALL | DISIS-2017-002 | ERIS | Thermal | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 23SP, 26SP, 26WP | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 223 | 223 | 104.76 | 125.02 |  |  |  | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
03ALL | DISIS-2017-002 | ERIS | Thermal | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 23SP, 26SP | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 293 | 334 | <90% | 127.79 |  |  |  | Terminal Upgrades at Archie 161kV
03ALL | DISIS-2017-002 | ERIS | Thermal | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 23SP, 26SP | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 293 | 334 | <90% | 127.79 |  |  |  | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
03ALL | DISIS-2017-002 | ERIS | Thermal | 543028 NASHUA-5 161 997413 NASHUA11 _1 161 11 | 26WP | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 650 | 715 | <90% | 100.15 |  |  |  | Install a second 650 MVA TX at Nashua
03ALL | DISIS-2017-002 | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | DISIS-2017-002 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | DISIS-2017-002 CF | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 23SP, 26SP, 26WP | 541207 ARCHIE 5 161 541240 ADRIAN 5 161 1 | 311 | 334 | <90% | 115.54 |  |  |  | Terminal upgrades at Clinton (owned by AECI)
03ALL | DISIS-2017-002 CF | ERIS | Thermal | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | 26WP | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 280 | 280 | <90% | 100.37 |  |  |  | Line - Wolf Creek - Blackberry 345 kV
03ALL | DISIS-2017-002 CF | ERIS | Stability | Active power oscillations observed at WCGS U1 (532751) following the event. | 25S, 25W | GROUP3_P4_LOCAL_FAULT350 | [7 empty] | Line - Wolf Creek - Blackberry 345 kV
03ALL | DISIS-2017-002 CF | ERIS | Thermal | None | 23SP, 26L, 26SP | None | [7 empty] | None
03ALL | DISIS-2017-002 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | DISIS-2017-002 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | P23:345:AEPW:OKLAUNION CB 3401A NBTB | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | P23:345:AEPW:OKLAUNION CB 3409A NBTB | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | P43:345:SPS:TUCO:NR05:SLG:EHV: | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | Non-Converge | 26L | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | [7 empty] | Build Tolk to Potter County 345 kV Circuit 1
04ALL | DISIS-2017-002 | ERIS | Non-Converge | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 23SP, 26SP, 26WP | 515152 BROWNTP4 138 515155 BODLE 4 138 1 |  | 143 | 81.76 | 123.08 |  |  |  | SPA Brown to Brown 138 kV Equipment Upgrade
04ALL | DISIS-2017-002 | ERIS | Non-Converge | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 | 23SP | P12:345:OKGE:BKRBKR143:::: |  | 308 | 81.43 | 112.48 |  |  |  | Matthewson - Redbud 345 kV New Line
04ALL | DISIS-2017-002 | ERIS | Non-Converge | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 | 23SP, 26SP | P13:138-345:OKGE:BKRBKR_3W023:::: |  | 448 | 83.59 | 106.38 |  |  |  | Matthewson - Redbud 345 kV New Line
04ALL | DISIS-2017-002 | ERIS | Non-Converge | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 | 23SP, 26SP | P13:138-345:OKGE:BKRBKR_3W023:::: |  | 448 | 82.31 | 104.62 |  |  |  | Matthewson - Redbud 345 kV New Line
04ALL | DISIS-2017-002 | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2017-002 | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2017-002 | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
04ALL | DISIS-2017-002 CF | ERIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 23SP, 26SP | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | 353 | 353 | 73.9 | 113.25 |  |  |  | Multi - Border - Woodward 345 kV Tap
04ALL | DISIS-2017-002 CF | ERIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 23SP, 26SP | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | 349 | 395 | 88.65 | 121.64 |  |  |  | Multi - Border - Woodward 345 kV Tap
04ALL | DISIS-2017-002 CF | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 23SP, 26L, 26SP | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | 353 | 353 | 99.2 | 136.12 |  |  |  | Multi - Border - Woodward 345 kV Tap
04ALL | DISIS-2017-002 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2017-002 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2017-002 CF | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
05ALL | DISIS-2017-002 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2017-002 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2017-002 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2017-002 | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
05ALL | DISIS-2017-002 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2017-002 CF | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2017-002 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2017-002 CF | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
00NR | DISIS-2017-002 | NRIS | Non-Converge | 514898 CIMARON4 138 997999 CIMARON1 _1 138 1 | 23SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | <90% | 103.54 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2017-002 | NRIS | Non-Converge | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 | 23SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | <90% | 107.46 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2017-002 | NRIS | Non-Converge | None | 26SP, 26WP | None | [7 empty] | None
00NR | DISIS-2017-002 | NRIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 23SP | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | 311 | 334 | <90% | 102.75 |  |  |  | Terminal upgrades at Clinton (owned by AECI)
00NR | DISIS-2017-002 | NRIS | Thermal | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 26SP | 541225 PHILL 5 161 541313 HARRIS 161 1 | 334 | 334 | 103.83 | 105.62 |  |  |  | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
00NR | DISIS-2017-002 | NRIS | Voltage | None | 23SP, 26WP, 26SP | None | [7 empty] | None
00NR | DISIS-2017-002 | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 23SP, 26SP | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 311 | 334 | 94.56 | 103.69 |  |  |  | Craig to Lenexa 161 kV line 1 Rating Update
00NR | DISIS-2017-002 CF | NRIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 26SP, 23SP | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 311 | 334 | <90% | 118.66 |  |  |  | Terminal upgrades at Clinton (owned by AECI)
00NR | DISIS-2017-002 CF | NRIS | Thermal | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 23SP, 26SP, 26WP | P12:138:OKGE:BKRBKR261:::: | 143 | 143 | <90% | 102.85 |  |  |  | SPA Brown to Brown 138 kV Equipment Upgrade
00NR | DISIS-2017-002 CF | NRIS | Thermal | 514946 MIDWEST4 138 520917 FRNKLNS4 138 1 | 23SP | P12:345:OKGE:BKRBKR367:::: | 268 | 287 | <90% | 104.46 |  |  |  | Multi - Park Community - Sunshine 138 kV
00NR | DISIS-2017-002 CF | NRIS | Thermal | 514946 MIDWEST4 138 520917 FRNKLNS4 138 1 | 23SP | PROXY_P4_345kV_POI_514801_12 | 268 | 287 | <90% | 104.46 |  |  |  | Multi - Park Community - Sunshine 138 kV
00NR | DISIS-2017-002 CF | NRIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 26SP | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | 353 | 353 | <90% | 100.28 |  |  |  | Multi - Border - Woodward 345 kV Tap
00NR | DISIS-2017-002 CF | NRIS | Thermal | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 23SP, 26WP | System Intact | 223 | 223 | 92.07 | 106.96 |  |  |  | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
00NR | DISIS-2017-002 CF | NRIS | Thermal | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 23SP, 26SP, 26WP | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 223 | 223 | 125.49 | 151.24 |  |  |  | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
00NR | DISIS-2017-002 CF | NRIS | Thermal | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 23SP, 26SP | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 293 | 334 | <90% | 126.13 |  |  |  | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
00NR | DISIS-2017-002 CF | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 23SP, 26SP | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 311 | 334 | 93.3 | 102.26 |  |  |  | Craig to Lenexa 161 kV line 1 Rating Update
00NR | DISIS-2017-002 CF | NRIS | Thermal | 603023 MALLARD7 115 655655 E.RUTHVL-CP7 115 1 | 26WP | 655657 SW.MINOT-CP7 115 659155 LOGAN___-BE7 115 1 | 120 | 120 | 105.58 | 110.1 |  |  |  | Millard to E.Ruth 115 kV line 1 Rating Update
00NR | DISIS-2017-002 CF | NRIS | Thermal | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 26WP | System Intact | 336 | 336 | <90% | 100.21 |  |  |  | Replace Mark Moore 345/115 kV Transformer
00NR | DISIS-2017-002 CF | NRIS | Thermal | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 26WP | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | 336 | 336 | <90% | 113.94 |  |  |  | Replace Mark Moore 345/115 kV Transformer
00NR | DISIS-2017-002 CF | NRIS | Thermal | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 26SP | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | 336 | 336 | <90% | 110.48 |  |  |  | Replace Mark Moore 345/115 kV Transformer
00NR | DISIS-2017-002 CF | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | DISIS-2017-002 CF | NRIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01NR | DISIS-2017-002 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
01NR | DISIS-2017-002 | NRIS | Thermal | None | 26L | None | [7 empty] | None
01NR | DISIS-2017-002 | NRIS | Voltage | None | 26L | None | [7 empty] | None
01NR | DISIS-2017-002 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
01NR | DISIS-2017-002 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
01NR | DISIS-2017-002 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
02NR | DISIS-2017-002 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
02NR | DISIS-2017-002 | NRIS | Thermal | None | 26L | None | [7 empty] | None
02NR | DISIS-2017-002 | NRIS | Voltage | None | 26L | None | [7 empty] | None
02NR | DISIS-2017-002 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
02NR | DISIS-2017-002 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
02NR | DISIS-2017-002 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
03NR | DISIS-2017-002 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
03NR | DISIS-2017-002 | NRIS | Thermal | None | 26L | None | [7 empty] | None
03NR | DISIS-2017-002 | NRIS | Voltage | None | 26L | None | [7 empty] | None
03NR | DISIS-2017-002 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
03NR | DISIS-2017-002 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
03NR | DISIS-2017-002 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
04NR | DISIS-2017-002 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
04NR | DISIS-2017-002 | NRIS | Thermal | None | 26L | None | [7 empty] | None
04NR | DISIS-2017-002 | NRIS | Voltage | None | 26L | None | [7 empty] | None
04NR | DISIS-2017-002 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
04NR | DISIS-2017-002 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
04NR | DISIS-2017-002 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2017-175 | DISIS-2017-002 | 01 NORTH | 143440 | ERIS | Vfodnes - Utica Jct. 230kV GEN-2017-175 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2017-175 | 15570000 | 100% | 15570000 | 1
GEN-2017-175 | DISIS-2017-002 | 01 NORTH | 143441 | ERIS | Vfodnes - Utica Jct. 230kV GEN-2017-175 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2017-175 | 515000 | 100% | 515000 | 1
GEN-2017-214 | DISIS-2017-002 | 01 NORTH | 143507 | ERIS | Logan 230kV GEN-2017-214, GEN-2017-215 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2017-214 | 468892.5 | 50% | 937785 | 1
GEN-2017-214 | DISIS-2017-002 | 01 NORTH | 143506 | ERIS | Logan 230kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-214 and GEN-2017-215 | 658531.5 | 50% | 1317063 | 1
GEN-2017-215 | DISIS-2017-002 | 01 NORTH | 143507 | ERIS | Logan 230kV GEN-2017-214, GEN-2017-215 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2017-214 | 468892.5 | 50% | 937785 | 1
GEN-2017-215 | DISIS-2017-002 | 01 NORTH | 143509 | ERIS | Logan 230kV GEN-2017-215 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2017-215 | 100000 | 100% | 100000 | 1
GEN-2017-215 | DISIS-2017-002 | 01 NORTH | 143506 | ERIS | Logan 230kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-214 and GEN-2017-215 | 658531.5 | 50% | 1317063 | 1
GEN-2017-222 | DISIS-2017-002 | 01 NORTH | 143522 | ERIS | Denison 230kV GEN-2017-222 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2017-222 | 9960000 | 100% | 9960000 | 1
GEN-2017-222 | DISIS-2017-002 | 01 NORTH | 143523 | ERIS | Denison 230kV GEN-2017-222 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2017-222 | 265000 | 100% | 265000 | 1
GEN-2017-222 | DISIS-2017-002 | 01 NORTH | 143686 | ERIS | Denison to Boyer 69kV Terminal Upgrade | Current Study | Upgrade terminal equipment at Denison 69kV to achieve a minimum rating of 117 MVA | 135000 | 100% | 135000 | 0.18502
GEN-2017-105 | DISIS-2017-002 | 02 NEBRASKA | 143336 | ERIS | Tekamah - Raun 161kV GEN-2017-105 Interconnection (Non-Shared NU) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2017-105 | 6684356 | 100% | 6684356 | 1
GEN-2017-105 | DISIS-2017-002 | 02 NEBRASKA | 143337 | ERIS | Tekamah - Raun 161kV GEN-2017-105 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2017-105 | 3142178 | 100% | 3142178 | 1
GEN-2017-144 | DISIS-2017-002 | 02 NEBRASKA | 50442, 50445, 50444 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County(NTC - 200220) | 0 | 100% | 451409958 | 0.22035
GEN-2017-144 | DISIS-2017-002 | 02 NEBRASKA | 143390 | ERIS | Holt County 345kV GEN-2017-144 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-144 | 2500000 | 100% | 2500000 | 1
GEN-2017-144 | DISIS-2017-002 | 02 NEBRASKA | 156456 | ERIS | Replace Mark Moore 345/115 kV Transformer | Current Study | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 681941.6911 | 8.216% | 8300000 | 0.007
GEN-2017-144 | DISIS-2017-002 CF | 02 NEBRASKA | 50442, 50445, 50444 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County(NTC - 200220) | 0 |  | 451409958
GEN-2017-181 | DISIS-2017-002 | 02 NEBRASKA | 156456 | ERIS | Replace Mark Moore 345/115 kV Transformer | Current Study | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 3903141.979 | 47.03% | 8300000 | 0.02671
GEN-2017-181 | DISIS-2017-002 | 02 NEBRASKA | 143449 | ERIS | Tobias 345kV GEN-2017-181 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-181 | 0 | 100% | 0 | 1
GEN-2017-181 | DISIS-2017-002 | 02 NEBRASKA | 143448 | ERIS | Tobias 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-181 and GEN-2017-182 | 5046480 | 70.09% | 7200000 | 1
GEN-2017-181 | DISIS-2017-002 CF | 02 NEBRASKA | 50442, 50445, 50444 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County(NTC - 200220) | 0 |  | 451409958
GEN-2017-181 | DISIS-2017-002 CF | 02 NEBRASKA | 156456 | NRIS | Replace Mark Moore 345/115 kV Transformer | Contingent | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 0 |  | 8300000
GEN-2017-182 | DISIS-2017-002 | 02 NEBRASKA | 156456 | ERIS | Replace Mark Moore 345/115 kV Transformer | Current Study | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 1665340.578 | 20.06% | 8300000 | 0.02671
GEN-2017-182 | DISIS-2017-002 | 02 NEBRASKA | 143451 | ERIS | Tobias 345kV GEN-2017-182 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-182 | 0 | 100% | 0 | 1
GEN-2017-182 | DISIS-2017-002 | 02 NEBRASKA | 143448 | ERIS | Tobias 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-181 and GEN-2017-182 | 2153520 | 29.91% | 7200000 | 1
GEN-2017-182 | DISIS-2017-002 CF | 02 NEBRASKA | 50442, 50445, 50444 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County(NTC - 200220) | 0 |  | 451409958
GEN-2017-182 | DISIS-2017-002 CF | 02 NEBRASKA | 156456 | NRIS | Replace Mark Moore 345/115 kV Transformer | Contingent | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 0 |  | 8300000
GEN-2017-198 | DISIS-2017-002 | 02 NEBRASKA | 143482 | ERIS | Jones St. No 901 69kV GEN-2017-198 Interconnection (Non-Shared NU) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2017-198 | 923949 | 100% | 923949 | 1
GEN-2017-198 | DISIS-2017-002 | 02 NEBRASKA | 143483 | ERIS | Jones St. No 901 69kV GEN-2017-198 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2017-198 | 0 | 100% | 0 | 1
GEN-2017-201 | DISIS-2017-002 | 02 NEBRASKA | 143488 | ERIS | Hoskins 345k GEN-2017-201 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-201 | 50000 | 100% | 50000 | 1
GEN-2017-201 | DISIS-2017-002 | 02 NEBRASKA | 143489 | ERIS | Hoskins 345k GEN-2017-201 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-201 | 0 | 100% | 0 | 1
GEN-2017-201 | DISIS-2017-002 CF | 02 NEBRASKA | 156456 | NRIS | Replace Mark Moore 345/115 kV Transformer | Contingent | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 0 |  | 8300000
GEN-2017-210 | DISIS-2017-002 | 02 NEBRASKA | 143502 | ERIS | McCool 345kV GEN-2017-210 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-210 | 9900000 | 100% | 9900000 | 1
GEN-2017-210 | DISIS-2017-002 | 02 NEBRASKA | 143503 | ERIS | McCool 345kV GEN-2017-210 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-210 | 0 | 100% | 0 | 1
GEN-2017-210 | DISIS-2017-002 | 02 NEBRASKA | 156456 | ERIS | Replace Mark Moore 345/115 kV Transformer | Current Study | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 1816546.535 | 21.89% | 8300000 | 0.01203
GEN-2017-234 | DISIS-2017-002 | 02 NEBRASKA | 156456 | ERIS | Replace Mark Moore 345/115 kV Transformer | Current Study | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 233029.2179 | 2.808% | 8300000 | 0.00416
GEN-2017-234 | DISIS-2017-002 | 02 NEBRASKA | 143544 | ERIS | Spalding to North Loup 115kV GEN-2017-234 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-234 | 11300000 | 100% | 11300000 | 1
GEN-2017-234 | DISIS-2017-002 | 02 NEBRASKA | 143545 | ERIS | Spalding to North Loup 115kV GEN-2017-234 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2017-234 | 0 | 100% | 0 | 1
GEN-2017-234 | DISIS-2017-002 CF | 02 NEBRASKA | 50442, 50445, 50444 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County(NTC - 200220) | 0 |  | 451409958
GEN-2017-108 | DISIS-2017-002 | 03 CENTRAL | 143343 | ERIS | Stillwell - Clinton 161kV GEN-2017-108 Interconnection (TOIF) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2017-108 | 631241 | 100% | 631241 | 1
GEN-2017-108 | DISIS-2017-002 | 03 CENTRAL | 156516 | ERIS | Terminal Upgrades at Archie 161kV | Current Study | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | 1455934 | 100% | 1455934 | 0.36133
GEN-2017-108 | DISIS-2017-002 | 03 CENTRAL | 156851 | ERIS | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Current Study | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | 41157960 | 100% | 41157960 | 0.36133
GEN-2017-108 | DISIS-2017-002 | 03 CENTRAL | 143342 | ERIS | Stillwell - Clinton 161kV New Three (3) Breaker Ring Bus Interconnection Substation (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-108 | 11780128 | 100% | 11780128 | 1
GEN-2017-108 | DISIS-2017-002 | 03 CENTRAL | 159066 | ERIS | Terminal upgrades at Clinton (owned by AECI) | Current Study | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | 0 | 100% | 0 | 0.50369
GEN-2017-108 | DISIS-2017-002 CF | 03 CENTRAL | 159066 | ERIS | Terminal upgrades at Clinton (owned by AECI) | Contingent | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | 0 |  | 0
GEN-2017-115 | DISIS-2017-002 | 03 CENTRAL | 143354 | ERIS | Holt County 345kV GEN-2017-115 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2017-115 | 646575 | 100% | 646575 | 1
GEN-2017-115 | DISIS-2017-002 | 03 CENTRAL | 143355 | ERIS | Holt County 345kV GEN-2017-115 Interconnection (TOIF) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2017-115 | 1016593 | 100% | 1016593 | 1
GEN-2017-119 | DISIS-2017-002 | 03 CENTRAL | 159067 | ERIS | Partly rebuild the Elm Creek to North Manhattan 230 kV line | Current Study | Partly reconductor 2.9 mile of the Elm Creek to North Manhattan 230 kV line to achieve a minimum rating of 390 MVA | 7095222 | 100% | 7095222 | 0.1926
GEN-2017-119 | DISIS-2017-002 | 03 CENTRAL | 143363 | ERIS | Elm Creek 345kV GEN-2017-119 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2017-119 | 805608 | 100% | 805608 | 1
GEN-2017-119 | DISIS-2017-002 | 03 CENTRAL | 143360 | ERIS | Elm Creek 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-119 | 3404822 | 100% | 3404822 | 1
GEN-2017-120 | DISIS-2017-002 | 03 CENTRAL | 143364 | ERIS | Abilene Energy Center - Northview 115kV GEN-2017-120 Interconnection (Non-Shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-120 | 10641981 | 100% | 10641981 | 1
GEN-2017-120 | DISIS-2017-002 | 03 CENTRAL | 143365 | ERIS | Abilene Energy Center - Northview 115kV GEN-2017-120 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-120 | 842712 | 100% | 842712 | 1
GEN-2017-121 | DISIS-2017-002 | 03 CENTRAL | 143366 | ERIS | Sumner 138kV GEN-2017-121 Interconnection (Non-Shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-121 | 591564 | 100% | 591564 | 1
GEN-2017-121 | DISIS-2017-002 | 03 CENTRAL | 143367 | ERIS | Sumner 138kV GEN-2017-121 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-121 | 648516 | 100% | 648516 | 1
GEN-2017-121 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-125 | DISIS-2017-002 | 03 CENTRAL | 143371 | ERIS | Swissvale 345kV GEN-2017-125 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-125 | 1325114 | 100% | 1325114 | 1
GEN-2017-125 | DISIS-2017-002 | 03 CENTRAL | 143370 | ERIS | Swissvale 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-125 | 25565648 | 100% | 25565648 | 1
GEN-2017-131 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-131 | DISIS-2017-002 | 03 CENTRAL | 143374 | ERIS | Altoona - NE Parson 138kV GEN-2017-131 Interconnection (Non-Shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-131 | 12381 | 100% | 12381 | 1
GEN-2017-131 | DISIS-2017-002 | 03 CENTRAL | 143375 | ERIS | Altoona - NE Parson 138kV GEN-2017-131 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-131 | 24762 | 100% | 24762 | 1
GEN-2017-183 | DISIS-2017-002 | 03 CENTRAL | 159069 | ERIS | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Current Study | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | 55140.0943 | 48.84% | 112911 | 0.05156
GEN-2017-183 | DISIS-2017-002 | 03 CENTRAL | 159068 | ERIS | Install a second 650 MVA TX at Nashua | Current Study | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650 MVA | 11197741.7507 | 49.28% | 22759204 | 0.06927
GEN-2017-183 | DISIS-2017-002 | 03 CENTRAL | 143453 | ERIS | Nashua - St. Joe 345kV GEN-2017-183 Interconnection (TOIF) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2017-183 | 614710 | 100% | 614710 | 1
GEN-2017-183 | DISIS-2017-002 | 03 CENTRAL | 143452 | ERIS | Nashua - St. Joe 345kV New Interconnection Substation (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-183 and GEN-2017-184 | 13945200.5 | 50% | 27890401 | 1
GEN-2017-183 | DISIS-2017-002 CF | 03 CENTRAL | 159069 | NRIS | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Contingent | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | 0 |  | 112911
GEN-2017-184 | DISIS-2017-002 | 03 CENTRAL | 159069 | ERIS | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Current Study | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | 57770.9057 | 51.16% | 112911 | 0.05402
GEN-2017-184 | DISIS-2017-002 | 03 CENTRAL | 159068 | ERIS | Install a second 650 MVA TX at Nashua | Current Study | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650 MVA | 11561462.2493 | 50.72% | 22759204 | 0.07152
GEN-2017-184 | DISIS-2017-002 | 03 CENTRAL | 143455 | ERIS | Nashua -St. Joe 345kV GEN-2017-184 Interconnection (TOIF) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2017-184 | 614709 | 100% | 614709 | 1
GEN-2017-184 | DISIS-2017-002 | 03 CENTRAL | 143452 | ERIS | Nashua - St. Joe 345kV New Interconnection Substation (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-183 and GEN-2017-184 | 13945200.5 | 50% | 27890401 | 1
GEN-2017-184 | DISIS-2017-002 CF | 03 CENTRAL | 159069 | NRIS | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Contingent | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | 0 |  | 112911
GEN-2017-188 | DISIS-2017-002 | 03 CENTRAL | 143462 | ERIS | Asbury 161 kV GEN-2017-188 Interconnection (Non-Shared NU) (EDE) | Interconnection | Facilitate the interconnection of GEN-2017-188 | 1520000 | 100% | 1520000 | 1
GEN-2017-188 | DISIS-2017-002 | 03 CENTRAL | 143567 | ERIS | Asbury 161 kV GEN-2017-188 Interconnection (Non-Shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-188 | 10317 | 100% | 10317 | 1
GEN-2017-188 | DISIS-2017-002 | 03 CENTRAL | 143463 | ERIS | Asbury 161 kV GEN-2017-188 Interconnection (TOIF) (EDE) | Interconnection | Facilitate the interconnection of GEN-2017-188 | 0 | 100% | 0 | 1
GEN-2017-188 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-195 | DISIS-2017-002 | 03 CENTRAL | 143477 | ERIS | West Gardner 345kV GEN-2017-195 Interconnection (TOIF) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2017-195 | 1446166 | 100% | 1446166 | 1
GEN-2017-195 | DISIS-2017-002 | 03 CENTRAL | 143476 | ERIS | West Gardner 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-195 and GEN-2017-196 | 24844357 | 79.63% | 31199745 | 1
GEN-2017-195 | DISIS-2017-002 CF | 03 CENTRAL | 159066 | ERIS | Terminal upgrades at Clinton (owned by AECI) | Contingent | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | 0 |  | 0
GEN-2017-196 | DISIS-2017-002 | 03 CENTRAL | 143479 | ERIS | West Gardner 345kV GEN-2017-196 Interconnection (TOIF) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2017-196 | 112911 | 100% | 112911 | 1
GEN-2017-196 | DISIS-2017-002 | 03 CENTRAL | 143476 | ERIS | West Gardner 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-195 and GEN-2017-196 | 6355388 | 20.37% | 31199745 | 1
GEN-2017-196 | DISIS-2017-002 CF | 03 CENTRAL | 159066 | ERIS | Terminal upgrades at Clinton (owned by AECI) | Contingent | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | 0 |  | 0
GEN-2017-202 | DISIS-2017-002 | 03 CENTRAL | 143490 | ERIS | New Madrid - Sikeston 161kV GEN-2017-202 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Facilitate the interconnection of GEN-2017-202 | 7069000 | 100% | 7069000 | 1
GEN-2017-202 | DISIS-2017-002 | 03 CENTRAL | 143491 | ERIS | New Madrid - Sikeston 161kV GEN-2017-202 Interconnection (TOIF) (SWPA) | Interconnection | Facilitate the interconnection of GEN-2017-202 | 746000 | 100% | 746000 | 1
GEN-2017-209 | DISIS-2017-002 | 03 CENTRAL | 143500 | ERIS | LaCygne - Neosho 345kV GEN-2017-209 Interconnection (Non-Shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-209 | 23413493 | 100% | 23413493 | 1
GEN-2017-209 | DISIS-2017-002 | 03 CENTRAL | 143501 | ERIS | LaCygne - Neosho 345kV GEN-2017-209 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-209 | 1705965 | 100% | 1705965 | 1
GEN-2017-209 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-220 | DISIS-2017-002 | 03 CENTRAL | 143519 | ERIS | Buffalo Flats 345kV GEN-2017-220 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-220 | 579336 | 100% | 579336 | 1
GEN-2017-220 | DISIS-2017-002 | 03 CENTRAL | 143518 | ERIS | Buffalo Flats 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-220 and GEN-2017-221 | 1303973.43 | 57.01% | 2287128 | 1
GEN-2017-220 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-221 | DISIS-2017-002 | 03 CENTRAL | 143521 | ERIS | Buffalo Flats 345kV GEN-2017-221 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-221 | 579336 | 100% | 579336 | 1
GEN-2017-221 | DISIS-2017-002 | 03 CENTRAL | 143518 | ERIS | Buffalo Flats 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-220 and GEN-2017-221 | 983154.5701 | 42.99% | 2287128 | 1
GEN-2017-221 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-226 | DISIS-2017-002 | 03 CENTRAL | 143529 | ERIS | Gordon Evans 138kV GEN-2017-226 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-226 | 750415 | 100% | 750415 | 1
GEN-2017-226 | DISIS-2017-002 | 03 CENTRAL | 143446 | ERIS | Gordon Evans 138kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-226 and GEN-2017-227 | 636214.5 | 50% | 1272429 | 1
GEN-2017-226 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-227 | DISIS-2017-002 | 03 CENTRAL | 143531 | ERIS | Gordon Evans 138kV GEN-2017-227 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2017-227 | 0 | 100% | 0 | 1
GEN-2017-227 | DISIS-2017-002 | 03 CENTRAL | 143446 | ERIS | Gordon Evans 138kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-226 and GEN-2017-227 | 636214.5 | 50% | 1272429 | 1
GEN-2017-227 | DISIS-2017-002 CF | 03 CENTRAL | 112509/122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | 0 |  | 142601178
GEN-2017-117 | DISIS-2017-002 | 04 SOUTHEAST | 143580 | ERIS | EL Reno SW 138kV GEN-2017-117 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-117 | 15000 | 100% | 15000 | 1
GEN-2017-117 | DISIS-2017-002 | 04 SOUTHEAST | 143358 | ERIS | El Reno SW 138kV GEN-2017-117 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Facilitate the interconnection of GEN-2017-117 | 500000 | 100% | 500000 | 1
GEN-2017-117 | DISIS-2017-002 | 04 SOUTHEAST | 143359 | ERIS | El Reno SW 138kV GEN-2017-117 Interconnection (TOIF) (WFEC) | Interconnection | Facilitate the interconnection of GEN-2017-117 | 500000 | 100% | 500000 | 1
GEN-2017-117 | DISIS-2017-002 CF | 04 SOUTHEAST | 72013-72016, 72018 - 72027, 72029 - 72031 | NRIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW.(NTC - 210483, 210669) | 0 |  | 66482000
GEN-2017-132 | DISIS-2017-002 | 04 SOUTHEAST | 143377 | ERIS | Arcadia 345kV GEN-2017-132 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-132 | 397914 | 100% | 397914 | 1
GEN-2017-132 | DISIS-2017-002 | 04 SOUTHEAST | 143376 | ERIS | Arcadia 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-132, GEN-2017-133, GEN-134 and GEN-2017-137 | 4155355.46 | 34.93% | 11894705 | 1
GEN-2017-132 | DISIS-2017-002 | 04 SOUTHEAST | 158573/158574/TBD | ERIS | Matthewson - Redbud 345 kV New Line | Contingent | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | 0 | 34.67% | 110770850 | 0.22979
GEN-2017-133 | DISIS-2017-002 | 04 SOUTHEAST | 143379 | ERIS | Arcadia 345kV GEN-2017-133 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-133 | 397914 | 100% | 397914 | 1
GEN-2017-133 | DISIS-2017-002 | 04 SOUTHEAST | 143376 | ERIS | Arcadia 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-132, GEN-2017-133, GEN-134 and GEN-2017-137 | 2077677.73 | 17.47% | 11894705 | 1
GEN-2017-133 | DISIS-2017-002 | 04 SOUTHEAST | 158573/158574/TBD | ERIS | Matthewson - Redbud 345 kV New Line | Contingent | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | 0 | 17.33% | 110770850 | 0.22979
GEN-2017-134 | DISIS-2017-002 | 04 SOUTHEAST | 143381 | ERIS | Arcadia 345kV GEN-2017-134 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-134 | 397913 | 100% | 397913 | 1
GEN-2017-134 | DISIS-2017-002 | 04 SOUTHEAST | 143376 | ERIS | Arcadia 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-132, GEN-2017-133, GEN-134 and GEN-2017-137 | 2597097.16 | 21.83% | 11894705 | 1
GEN-2017-134 | DISIS-2017-002 | 04 SOUTHEAST | 158573/158574/TBD | ERIS | Matthewson - Redbud 345 kV New Line | Contingent | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | 0 | 21.67% | 110770850 | 0.22979
GEN-2017-137 | DISIS-2017-002 | 04 SOUTHEAST | 143383 | ERIS | Arcadia 345kV GEN-2017-137 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-137 | 397913 | 100% | 397913 | 1
GEN-2017-137 | DISIS-2017-002 | 04 SOUTHEAST | 143376 | ERIS | Arcadia 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-132, GEN-2017-133, GEN-134 and GEN-2017-137 | 3064574.65 | 25.76% | 11894705 | 1
GEN-2017-137 | DISIS-2017-002 | 04 SOUTHEAST | 158573/158574/TBD | ERIS | Matthewson - Redbud 345 kV New Line | Contingent | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | 0 | 25.57% | 110770850 | 0.22979
GEN-2017-140 | DISIS-2017-002 | 04 SOUTHEAST | 143385 | ERIS | Clarksville 345kV GEN-2017-140 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2017-140 | 2936547 | 100% | 2936547 | 1
GEN-2017-140 | DISIS-2017-002 | 04 SOUTHEAST | 143561 | ERIS | Clarksville 345kV GEN-2017-140 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-140 | 15000 | 100% | 15000 | 1
GEN-2017-140 | DISIS-2017-002 | 04 SOUTHEAST | 143384 | ERIS | Clarksville 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-140 and GEN-2017-141 | 995380.78 | 39.83% | 2499073 | 1
GEN-2017-141 | DISIS-2017-002 | 04 SOUTHEAST | 143562 | ERIS | Clarksville 345kV GEN-2017-141 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-141 | 15000 | 100% | 15000 | 1
GEN-2017-141 | DISIS-2017-002 | 04 SOUTHEAST | 143387 | ERIS | Clarksville 345kV GEN-2017-141 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2017-141 | 2936547 | 100% | 2936547 | 1
GEN-2017-141 | DISIS-2017-002 | 04 SOUTHEAST | 143384 | ERIS | Clarksville 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-140 and GEN-2017-141 | 1503692.22 | 60.17% | 2499073 | 1
GEN-2017-149 | DISIS-2017-002 | 04 SOUTHEAST | 159070 | ERIS | Build Tolk to Potter County 345 kV Circuit 1 | Current Study | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | 66832850.6266 | 36.99% | 180684436 | 0.01643
GEN-2017-149 | DISIS-2017-002 | 04 SOUTHEAST | 143401 | ERIS | Johnson County 345kV GEN-2017-149 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-149 | 795827 | 100% | 795827 | 1
GEN-2017-149 | DISIS-2017-002 | 04 SOUTHEAST | 143572 | ERIS | Johnson County 345kV GEN-2017-149 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2017-149 | 250000 | 100% | 250000 | 1
GEN-2017-149 | DISIS-2017-002 | 04 SOUTHEAST | 143400 | ERIS | Johnson County 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-149 and GEN-2017-154 | 5544459.23 | 50.29% | 11024448 | 1
GEN-2017-150 | DISIS-2017-002 | 04 SOUTHEAST | 143403 | ERIS | Minco 345kV GEN-2017-150 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-150 | 795827 | 100% | 795827 | 1
GEN-2017-150 | DISIS-2017-002 | 04 SOUTHEAST | 143402 | ERIS | Minco 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-150 and GEN-2017-233 | 962606.45 | 53.76% | 1790448 | 1
GEN-2017-150 | DISIS-2017-002 | 04 SOUTHEAST | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 | 51.4% | 100405248 | 0.30008
GEN-2017-150 | DISIS-2017-002 CF | 04 SOUTHEAST | 122796/122823/14382 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | 0 |  | 38547935
GEN-2017-150 | DISIS-2017-002 CF | 04 SOUTHEAST | 122796/122823/14382 | NRIS | Multi - Border - Woodward 345 kV Tap | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | 0 |  | 38547935
GEN-2017-154 | DISIS-2017-002 | 04 SOUTHEAST | 159070 | ERIS | Build Tolk to Potter County 345 kV Circuit 1 | Current Study | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | 66055724.4566 | 36.56% | 180684436 | 0.01643
GEN-2017-154 | DISIS-2017-002 | 04 SOUTHEAST | 143411 | ERIS | Johnson County 345kV GEN-2017-154 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-154 | 795827 | 100% | 795827 | 1
GEN-2017-154 | DISIS-2017-002 | 04 SOUTHEAST | 143573 | ERIS | Johnson County 345kV GEN-2017-154 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2017-154 | 250000 | 100% | 250000 | 1
GEN-2017-154 | DISIS-2017-002 | 04 SOUTHEAST | 143400 | ERIS | Johnson County 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-149 and GEN-2017-154 | 5479988.77 | 49.71% | 11024448 | 1
GEN-2017-164 | DISIS-2017-002 | 04 SOUTHEAST | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 | 7.658% | 100405248 | 0.04471
GEN-2017-164 | DISIS-2017-002 | 04 SOUTHEAST | 143425 | ERIS | Woodring 345kV GEN-2017-164 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-164 | 795827 | 100% | 795827 | 1
GEN-2017-164 | DISIS-2017-002 | 04 SOUTHEAST | 143424 | ERIS | Woodring 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-164 and GEN-2017-178 | 1482158.94 | 82.78% | 1790448 | 1
GEN-2017-167 | DISIS-2017-002 | 04 SOUTHEAST | 143429 | ERIS | Sunnyside 345kV GEN-2017-167 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-167 | 1591654 | 100% | 1591654 | 1
GEN-2017-167 | DISIS-2017-002 | 04 SOUTHEAST | 143426 | ERIS | Sunnyside 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-167 | 8195816 | 100% | 8195816 | 1
GEN-2017-171 | DISIS-2017-002 | 04 SOUTHEAST | 143435 | ERIS | Lawton Eastside - Terry Road 345kV Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2017-171, GEN-2017-172 and GEN-2017-173 | 2325791.4 | 60% | 3876319 | 1
GEN-2017-171 | DISIS-2017-002 | 04 SOUTHEAST | 143434 | ERIS | Lawton Eastside - Terry Road 345kV New Interconnection Substation (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-171, GEN-2017-172, and GEN-2017-173 | 10882780.8 | 60% | 18137968 | 1
GEN-2017-171 | DISIS-2017-002 CF | 04 SOUTHEAST | 122796/122823/14382 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | 0 |  | 38547935
GEN-2017-172 | DISIS-2017-002 | 04 SOUTHEAST | 143435 | ERIS | Lawton Eastside - Terry Road 345kV Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2017-171, GEN-2017-172 and GEN-2017-173 | 775263.8 | 20% | 3876319 | 1
GEN-2017-172 | DISIS-2017-002 | 04 SOUTHEAST | 143434 | ERIS | Lawton Eastside - Terry Road 345kV New Interconnection Substation (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-171, GEN-2017-172, and GEN-2017-173 | 3627593.6 | 20% | 18137968 | 1
GEN-2017-172 | DISIS-2017-002 CF | 04 SOUTHEAST | 122796/122823/14382 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | 0 |  | 38547935
GEN-2017-173 | DISIS-2017-002 | 04 SOUTHEAST | 143435 | ERIS | Lawton Eastside - Terry Road 345kV Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2017-171, GEN-2017-172 and GEN-2017-173 | 775263.8 | 20% | 3876319 | 1
GEN-2017-173 | DISIS-2017-002 | 04 SOUTHEAST | 143434 | ERIS | Lawton Eastside - Terry Road 345kV New Interconnection Substation (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-171, GEN-2017-172, and GEN-2017-173 | 3627593.6 | 20% | 18137968 | 1
GEN-2017-173 | DISIS-2017-002 CF | 04 SOUTHEAST | 122796/122823/14382 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | 0 |  | 38547935
GEN-2017-178 | DISIS-2017-002 | 04 SOUTHEAST | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 | 1.593% | 100405248 | 0.04471
GEN-2017-178 | DISIS-2017-002 | 04 SOUTHEAST | 143445 | ERIS | Woodring 345kV GEN-2017-178 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-178 | 795827 | 100% | 795827 | 1
GEN-2017-178 | DISIS-2017-002 | 04 SOUTHEAST | 143424 | ERIS | Woodring 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-164 and GEN-2017-178 | 308289.06 | 17.22% | 1790448 | 1
GEN-2017-203 | DISIS-2017-002 | 04 SOUTHEAST | 143492 | ERIS | Renfrow 345kV GEN-2017-203 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-203 | 1790448 | 100% | 1790448 | 1
GEN-2017-203 | DISIS-2017-002 | 04 SOUTHEAST | 143493 | ERIS | Renfrow 345kV GEN-2017-203 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-203 | 1591654 | 100% | 1591654 | 1
GEN-2017-230 | DISIS-2017-002 | 04 SOUTHEAST | 158573/158574/TBD | ERIS | Matthewson - Redbud 345 kV New Line | Contingent | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | 0 | 0.7599% | 110770850 | 0.02779
GEN-2017-230 | DISIS-2017-002 | 04 SOUTHEAST | 143536 | ERIS | Tryon 138kV GEN-2017-230 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-230 | 1133420 | 100% | 1133420 | 1
GEN-2017-230 | DISIS-2017-002 | 04 SOUTHEAST | 143537 | ERIS | Tryon 138kV GEN-2017-230 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-230 | 934626 | 100% | 934626 | 1
GEN-2017-231 | DISIS-2017-002 | 04 SOUTHEAST | 143538 | ERIS | Branch 161kV GEN-2017-231 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-231 | 6030786 | 100% | 6030786 | 1
GEN-2017-231 | DISIS-2017-002 | 04 SOUTHEAST | 143539 | ERIS | Branch 161kV GEN-2017-231 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-231 | 934626 | 100% | 934626 | 1
GEN-2017-232 | DISIS-2017-002 | 04 SOUTHEAST | 143540 | ERIS | Brown 138kV GEN-2017-232 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-232 | 15000 | 100% | 15000 | 1
GEN-2017-232 | DISIS-2017-002 | 04 SOUTHEAST | 143577 | ERIS | Brown 138kV GEN-2017-232 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Facilitate the interconnection of GEN-2017-232 | 40000 | 100% | 40000 | 1
GEN-2017-232 | DISIS-2017-002 | 04 SOUTHEAST | 143541 | ERIS | Brown 138kV GEN-2017-232 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-232 | 0 | 100% | 0 | 1
GEN-2017-232 | DISIS-2017-002 | 04 SOUTHEAST | 156498 | ERIS | SPA Brown to Brown 138 kV Equipment Upgrade | Current Study | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | 825000 | 100% | 825000 | 0.71814
GEN-2017-232 | DISIS-2017-002 CF | 04 SOUTHEAST | 156498 | NRIS | SPA Brown to Brown 138 kV Equipment Upgrade | Contingent | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | 0 |  | 825000
GEN-2017-233 | DISIS-2017-002 | 04 SOUTHEAST | 159070 | ERIS | Build Tolk to Potter County 345 kV Circuit 1 | Current Study | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | 47795860.9168 | 26.45% | 180684436 | 0.0141
GEN-2017-233 | DISIS-2017-002 | 04 SOUTHEAST | 143543 | ERIS | Minco 345kV GEN-2017-233 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2017-233 | 795827 | 100% | 795827 | 1
GEN-2017-233 | DISIS-2017-002 | 04 SOUTHEAST | 143402 | ERIS | Minco 345kV Interconnection Expansion (DISIS-2017-002) | Interconnection | Facilitate the interconnection of GEN-2017-150 and GEN-2017-233 | 827841.55 | 46.24% | 1790448 | 1
GEN-2017-233 | DISIS-2017-002 | 04 SOUTHEAST | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 | 39.35% | 100405248 | 0.26718
GEN-2017-233 | DISIS-2017-002 CF | 04 SOUTHEAST | 122796/122823/14382 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | 0 |  | 38547935
GEN-2017-233 | DISIS-2017-002 CF | 04 SOUTHEAST | 122796/122823/14382 | NRIS | Multi - Border - Woodward 345 kV Tap | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | 0 |  | 38547935
GEN-2017-146 | DISIS-2017-002 | 05 SOUTHWEST | 143394 | ERIS | Deaf Smith - Plant X 230kV GEN-2017-146 Interconnection (Non-Shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-146 | 9822164 | 100% | 9822164 | 1
GEN-2017-146 | DISIS-2017-002 | 05 SOUTHWEST | 143395 | ERIS | Deaf Smith - Plant X 230kV GEN-2017-146 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-146 | 1284070 | 100% | 1284070 | 1
GEN-2017-151 | DISIS-2017-002 | 05 SOUTHWEST | 143404 | ERIS | TUCO - Oklaunion 345kV GEN-2017-151 Interconnection (Non-Shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-151 | 18991050 | 100% | 18991050 | 1
GEN-2017-151 | DISIS-2017-002 | 05 SOUTHWEST | 143405 | ERIS | TUCO - Oklaunion 345kV GEN-2017-151 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-151 | 1569115 | 100% | 1569115 | 1
GEN-2017-158 | DISIS-2017-002 | 05 SOUTHWEST | 143418 | ERIS | Tolk 230kV GEN-2017-158 Interconnection (Non-Shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-158 | 3935078 | 100% | 3935078 | 1
GEN-2017-158 | DISIS-2017-002 | 05 SOUTHWEST | 143419 | ERIS | Tolk 230kV GEN-2017-158 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-158 | 1329304 | 100% | 1329304 | 1
GEN-2017-187 | DISIS-2017-002 | 05 SOUTHWEST | 143460 | ERIS | Sulphur Springs 115kV GEN-2017-187 Interconnection (Non-Shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-187 | 16197956 | 100% | 16197956 | 1
GEN-2017-187 | DISIS-2017-002 | 05 SOUTHWEST | 143461 | ERIS | Sulphur Springs 115kV GEN-2017-187 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-187 | 841906 | 100% | 841906 | 1
GEN-2017-239 | DISIS-2017-002 | 05 SOUTHWEST | 143552 | ERIS | Mahoney 230kV GEN-2017-239 Interconnection (Non-Shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-239 | 820698 | 100% | 820698 | 1
GEN-2017-239 | DISIS-2017-002 | 05 SOUTHWEST | 143553 | ERIS | Mahoney 230kV GEN-2017-239 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2017-239 | 1049789 | 100% | 1049789 | 1
635537983.0011

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Interconnection | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Denison 230kV GEN-2017-222 Interconnection (Non-Shared NU) (WAPA) | 143522 | Facilitate the interconnection of GEN-2017-222 | WAPA | 30 | 9960000
Interconnection | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Denison 230kV GEN-2017-222 Interconnection (TOIF) (WAPA) | 143523 | Facilitate the interconnection of GEN-2017-222 | WAPA | 30 | 265000
Current Study | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Denison to Boyer 69kV Terminal Upgrade | 143686 | Upgrade terminal equipment at Denison 69kV to achieve a minimum rating of 117 MVA | BEPC | 36 | 135000
Model Correction | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Logan 230-115 kV Transformer Rating Update | N/A | Update rating of Logan 230-115 kV Transformer to 239 MVA | BEPC | N/A | 0
Interconnection | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Logan 230kV GEN-2017-214, GEN-2017-215 Interconnection (TOIF) (BEPC) | 143507 | Facilitate the interconnection of GEN-2017-214 | BEPC | 15 | 937785
Interconnection | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Logan 230kV GEN-2017-215 Interconnection (TOIF) (BEPC) | 143509 | Facilitate the interconnection of GEN-2017-215 | BEPC | 15 | 100000
Interconnection | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Logan 230kV Interconnection Expansion (DISIS-2017-002) | 143506 | Facilitate the interconnection of GEN-2017-214 and GEN-2017-215 | BEPC | 15 | 1317063
Model Correction | DISIS-2017-002 CF | Steady State | 01 NORTH | DISIS-2017-002 | NRIS | Millard to E.Ruth 115 kV line 1 Rating Update | N/A | Update ratings on Millard to E.Ruth 115 kV line 1 to 159 MVA | BEPC | N/A | 0
Model Correction | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Utica to Napa 115kV Rating Update | N/A | Update rating of Utica to Napa 115kV line 1 to 146.8 MVA | WAPA/ NorthWestern | N/A | 0
Interconnection | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Vfodnes - Utica Jct. 230kV GEN-2017-175 Interconnection (Non-Shared NU) (WAPA) | 143440 | Facilitate the interconnection of GEN-2017-175 | WAPA | 42 | 15570000
Interconnection | DISIS-2017-002 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | Vfodnes - Utica Jct. 230kV GEN-2017-175 Interconnection (TOIF) (WAPA) | 143441 | Facilitate the interconnection of GEN-2017-175 | WAPA | 42 | 515000
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Holt County 345kV GEN-2017-144 Interconnection (Non-Shared NU) (NPPD) | 143390 | Facilitate the interconnection of GEN-2017-144 | NPPD | 36 | 2500000
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Hoskins 345k GEN-2017-201 Interconnection (Non-Shared NU) (NPPD) | 143488 | Facilitate the interconnection of GEN-2017-201 | NPPD | 12 | 50000
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Hoskins 345k GEN-2017-201 Interconnection (TOIF) (NPPD) | 143489 | Facilitate the interconnection of GEN-2017-201 | NPPD | 36 | 0
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Jones St. No 901 69kV GEN-2017-198 Interconnection (Non-Shared NU) (OPPD) | 143482 | Facilitate the interconnection of GEN-2017-198 | OPPD | 24 | 923949
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Jones St. No 901 69kV GEN-2017-198 Interconnection (TOIF) (OPPD) | 143483 | Facilitate the interconnection of GEN-2017-198 | OPPD | 36 | 0
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | McCool 345kV GEN-2017-210 Interconnection (Non-Shared NU) (NPPD) | 143502 | Facilitate the interconnection of GEN-2017-210 | NPPD | 36 | 9900000
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | McCool 345kV GEN-2017-210 Interconnection (TOIF) (NPPD) | 143503 | Facilitate the interconnection of GEN-2017-210 | NPPD | 36 | 0
Contingent | DISIS-2017-002 | Steady State/Stability | 02 NEBRASKA | 2012 ITP10 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | 50442, 50445, 50444 | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County(NTC - 200220) | NPPD |  | 451409958
Contingent | DISIS-2017-002 CF | Steady State/Stability | 02 NEBRASKA | 2012 ITP10 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | 50442, 50445, 50444 | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County(NTC - 200220) | NPPD |  | 451409958
Current Study | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Replace Mark Moore 345/115 kV Transformer | 156456 | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | NPPD | 36 | 8300000
Contingent | DISIS-2017-002 CF | Steady State | 02 NEBRASKA | DISIS-2017-002 | NRIS | Replace Mark Moore 345/115 kV Transformer | 156456 | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | NPPD |  | 8300000
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Spalding to North Loup 115kV GEN-2017-234 Interconnection (Non-Shared NU) (NPPD) | 143544 | Facilitate the interconnection of GEN-2017-234 | NPPD | 36 | 11300000
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Spalding to North Loup 115kV GEN-2017-234 Interconnection (TOIF) (NPPD) | 143545 | Facilitate the interconnection of GEN-2017-234 | NPPD | 36 | 0
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Tekamah - Raun 161kV GEN-2017-105 Interconnection (Non-Shared NU) (OPPD) | 143336 | Facilitate the interconnection of GEN-2017-105 | OPPD | 36 | 6684356
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Tekamah - Raun 161kV GEN-2017-105 Interconnection (TOIF) (OPPD) | 143337 | Facilitate the interconnection of GEN-2017-105 | OPPD | 36 | 3142178
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Tobias 345kV GEN-2017-181 Interconnection (TOIF) (NPPD) | 143449 | Facilitate the interconnection of GEN-2017-181 | NPPD | 36 | 0
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Tobias 345kV GEN-2017-182 Interconnection (TOIF) (NPPD) | 143451 | Facilitate the interconnection of GEN-2017-182 | NPPD | 36 | 0
Interconnection | DISIS-2017-002 | Steady State | 02 NEBRASKA | DISIS-2017-002 | ERIS | Tobias 345kV Interconnection Expansion (DISIS-2017-002) | 143448 | Facilitate the interconnection of GEN-2017-181 and GEN-2017-182 | NPPD | 36 | 7200000
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Abilene Energy Center - Northview 115kV GEN-2017-120 Interconnection (Non-Shared NU) (WERE) | 143364 | Facilitate the interconnection of GEN-2017-120 | Evergy | 36 | 10641981
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Abilene Energy Center - Northview 115kV GEN-2017-120 Interconnection (TOIF) (WERE) | 143365 | Facilitate the interconnection of GEN-2017-120 | Evergy | 36 | 842712
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Altoona - NE Parson 138kV GEN-2017-131 Interconnection (Non-Shared NU) (WERE) | 143374 | Facilitate the interconnection of GEN-2017-131 | Evergy | 36 | 12381
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Altoona - NE Parson 138kV GEN-2017-131 Interconnection (TOIF) (WERE) | 143375 | Facilitate the interconnection of GEN-2017-131 | Evergy | 36 | 24762
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Asbury 161 kV GEN-2017-188 Interconnection (Non-Shared NU) (EDE) | 143462 | Facilitate the interconnection of GEN-2017-188 | EDE | 24 | 1520000
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Asbury 161 kV GEN-2017-188 Interconnection (Non-Shared NU) (WERE) | 143567 | Facilitate the interconnection of GEN-2017-188 | Evergy | 36 | 10317
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Asbury 161 kV GEN-2017-188 Interconnection (TOIF) (EDE) | 143463 | Facilitate the interconnection of GEN-2017-188 | EDE | 36 | 0
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Buffalo Flats 345kV GEN-2017-220 Interconnection (TOIF) (WERE) | 143519 | Facilitate the interconnection of GEN-2017-220 | Evergy | 36 | 579336
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Buffalo Flats 345kV GEN-2017-221 Interconnection (TOIF) (WERE) | 143521 | Facilitate the interconnection of GEN-2017-221 | Evergy | 36 | 579336
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Buffalo Flats 345kV Interconnection Expansion (DISIS-2017-002) | 143518 | Facilitate the interconnection of GEN-2017-220 and GEN-2017-221 | Evergy | 36 | 2287128
Current Study | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Install a second 650 MVA TX at Nashua | 159068 | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650 MVA | KCPL | 48 | 22759204
Model Correction | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | NRIS | Craig to Lenexa 161 kV line 1 Rating Update | N/A | Update rating of Craig to Lenexa 161 kV line 1 to 535 MVA | KCPL | N/A | 0
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Elm Creek 345kV GEN-2017-119 Interconnection (TOIF) (ITCGP) | 143363 | Facilitate the interconnection of GEN-2017-119 | ITCGP | 15 | 805608
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Elm Creek 345kV Interconnection Expansion (DISIS-2017-002) | 143360 | Facilitate the interconnection of GEN-2017-119 | ITCGP | 30 | 3404822
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Gordon Evans 138kV GEN-2017-226 Interconnection (TOIF) (WERE) | 143529 | Facilitate the interconnection of GEN-2017-226 | Evergy | 36 | 750415
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Gordon Evans 138kV GEN-2017-227 Interconnection (TOIF) (WERE) | 143531 | Facilitate the interconnection of GEN-2017-227 | Evergy | 36 | 0
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Gordon Evans 138kV Interconnection Expansion (DISIS-2017-002) | 143446 | Facilitate the interconnection of GEN-2017-226 and GEN-2017-227 | Evergy | 36 | 1272429
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Holt County 345kV GEN-2017-115 Interconnection (Non-Shared NU) (KCPL) | 143354 | Facilitate the interconnection of GEN-2017-115 | Evergy | 36 | 646575
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Holt County 345kV GEN-2017-115 Interconnection (TOIF) (KCPL) | 143355 | Facilitate the interconnection of GEN-2017-115 | Evergy | 36 | 1016593
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | LaCygne - Neosho 345kV GEN-2017-209 Interconnection (Non-Shared NU) (WERE) | 143500 | Facilitate the interconnection of GEN-2017-209 | Evergy | 36 | 23413493
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | LaCygne - Neosho 345kV GEN-2017-209 Interconnection (TOIF) (WERE) | 143501 | Facilitate the interconnection of GEN-2017-209 | Evergy | 36 | 1705965
Contingent | DISIS-2017-002 CF | Steady State/Stability | 03 CENTRAL | 2019 ITP | ERIS | Line - Wolf Creek - Blackberry 345 kV | 112509/122598 | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA(NTC - 210592/210626) | NEET |  | 142601178
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Nashua - St. Joe 345kV GEN-2017-183 Interconnection (TOIF) (KCPL) | 143453 | Facilitate the interconnection of GEN-2017-183 | Evergy | 36 | 614710
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Nashua -St. Joe 345kV GEN-2017-184 Interconnection (TOIF) (KCPL) | 143455 | Facilitate the interconnection of GEN-2017-184 | Evergy | 36 | 614709
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Nashua - St. Joe 345kV New Interconnection Substation (DISIS-2017-002) | 143452 | Facilitate the interconnection of GEN-2017-183 and GEN-2017-184 | Evergy | 36 | 27890401
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | New Madrid - Sikeston 161kV GEN-2017-202 Interconnection (Non-Shared NU) (SWPA) | 143490 | Facilitate the interconnection of GEN-2017-202 | SWPA | 36 | 7069000
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | New Madrid - Sikeston 161kV GEN-2017-202 Interconnection (TOIF) (SWPA) | 143491 | Facilitate the interconnection of GEN-2017-202 | SWPA | 36 | 746000
Current Study | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Partly rebuild the Elm Creek to North Manhattan 230 kV line | 159067 | Partly reconductor 2.9 mile of the Elm Creek to North Manhattan 230 kV line to achieve a minimum rating of 390 MVA | WERE | 48 | 7095222
Model Correction | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | NRIS | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update | N/A | Update rating to 542/557MVA Summer normal and emergencies and Winter 557/557 for both normal and emergency | KCPL | N/A | 0
Current Study | DISIS-2017-002 | Steady State/Stability | 03 CENTRAL | DISIS-2017-002 | ERIS | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | 156851 | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | KCPL | 48 | 41157960
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Stillwell - Clinton 161kV GEN-2017-108 Interconnection (TOIF) (KCPL) | 143343 | Facilitate the interconnection of GEN-2017-108 | Evergy | 36 | 631241
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Stillwell - Clinton 161kV New Three (3) Breaker Ring Bus Interconnection Substation (DISIS-2017-002) | 143342 | Facilitate the interconnection of GEN-2017-108 | Evergy | 36 | 11780128
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Sumner 138kV GEN-2017-121 Interconnection (Non-Shared NU) (WERE) | 143366 | Facilitate the interconnection of GEN-2017-121 | Evergy | 36 | 591564
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Sumner 138kV GEN-2017-121 Interconnection (TOIF) (WERE) | 143367 | Facilitate the interconnection of GEN-2017-121 | Evergy | 36 | 648516
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Swissvale 345kV GEN-2017-125 Interconnection (TOIF) (WERE) | 143371 | Facilitate the interconnection of GEN-2017-125 | Evergy | 36 | 1325114
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Swissvale 345kV Interconnection Expansion (DISIS-2017-002) | 143370 | Facilitate the interconnection of GEN-2017-125 | Evergy | 36 | 25565648
Current Study | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Terminal Upgrades at Archie 161kV | 156516 | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | KCPL | 48 | 1455934
Current Study | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Terminal upgrades at Clinton (owned by AECI) | 159066 | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | AECI | N/A | 0
Contingent | DISIS-2017-002 CF | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Terminal upgrades at Clinton (owned by AECI) | 159066 | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | AECI | N/A | 0
Current Study | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | 159069 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | KCPL | 24 | 112911
Contingent | DISIS-2017-002 CF | Steady State | 03 CENTRAL | DISIS-2017-002 | NRIS | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | 159069 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | KCPL | 24 | 112911
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | West Gardner 345kV GEN-2017-195 Interconnection (TOIF) (KCPL) | 143477 | Facilitate the interconnection of GEN-2017-195 | Evergy | 56 | 1446166
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | West Gardner 345kV GEN-2017-196 Interconnection (TOIF) (KCPL) | 143479 | Facilitate the interconnection of GEN-2017-196 | Evergy | 56 | 112911
Interconnection | DISIS-2017-002 | Steady State | 03 CENTRAL | DISIS-2017-002 | ERIS | West Gardner 345kV Interconnection Expansion (DISIS-2017-002) | 143476 | Facilitate the interconnection of GEN-2017-195 and GEN-2017-196 | Evergy | 56 | 31199745
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Arcadia 345kV GEN-2017-132 Interconnection (TOIF) (OKGE) | 143377 | Facilitate the interconnection of GEN-2017-132 | OKGE | 36 | 397914
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Arcadia 345kV GEN-2017-133 Interconnection (TOIF) (OKGE) | 143379 | Facilitate the interconnection of GEN-2017-133 | OKGE | 36 | 397914
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Arcadia 345kV GEN-2017-134 Interconnection (TOIF) (OKGE) | 143381 | Facilitate the interconnection of GEN-2017-134 | OKGE | 36 | 397913
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Arcadia 345kV GEN-2017-137 Interconnection (TOIF) (OKGE) | 143383 | Facilitate the interconnection of GEN-2017-137 | OKGE | 36 | 397913
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Arcadia 345kV Interconnection Expansion (DISIS-2017-002) | 143376 | Facilitate the interconnection of GEN-2017-132, GEN-2017-133, GEN-134 and GEN-2017-137 | OKGE | 36 | 11894705
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Branch 161kV GEN-2017-231 Interconnection (Non-Shared NU) (OKGE) | 143538 | Facilitate the interconnection of GEN-2017-231 | OKGE | 24 | 6030786
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Branch 161kV GEN-2017-231 Interconnection (TOIF) (OKGE) | 143539 | Facilitate the interconnection of GEN-2017-231 | OKGE | 24 | 934626
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Brown 138kV GEN-2017-232 Interconnection (Non-Shared NU) (OKGE) | 143540 | Facilitate the interconnection of GEN-2017-232 | OKGE | 6 | 15000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Brown 138kV GEN-2017-232 Interconnection (Non-Shared NU) (SWPA) | 143577 | Facilitate the interconnection of GEN-2017-232 | SWPA | 12 | 40000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Brown 138kV GEN-2017-232 Interconnection (TOIF) (OKGE) | 143541 | Facilitate the interconnection of GEN-2017-232 | OKGE | 36 | 0
Current Study | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Build Tolk to Potter County 345 kV Circuit 1 | 159070 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | SPS | 36 | 180684436
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Clarksville 345kV GEN-2017-140 Interconnection (TOIF) (AEP) | 143385 | Facilitate the interconnection of GEN-2017-140 | AEP | 36 | 2936547
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Clarksville 345kV GEN-2017-140 Interconnection (Non-Shared NU) (OKGE) | 143561 | Facilitate the interconnection of GEN-2017-140 | OKGE | 4 | 15000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Clarksville 345kV GEN-2017-141 Interconnection (Non-Shared NU) (OKGE) | 143562 | Facilitate the interconnection of GEN-2017-141 | OKGE | 4 | 15000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Clarksville 345kV GEN-2017-141 Interconnection (TOIF) (AEP) | 143387 | Facilitate the interconnection of GEN-2017-141 | AEP | 36 | 2936547
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Clarksville 345kV Interconnection Expansion (DISIS-2017-002) | 143384 | Facilitate the interconnection of GEN-2017-140 and GEN-2017-141 | AEP | 36 | 2499073
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | EL Reno SW 138kV GEN-2017-117 Interconnection (Non-Shared NU) (OKGE) | 143580 | Facilitate the interconnection of GEN-2017-117 | OKGE | 4 | 15000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | El Reno SW 138kV GEN-2017-117 Interconnection (Non-Shared NU) (WFEC) | 143358 | Facilitate the interconnection of GEN-2017-117 | WFEC | 36 | 500000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | El Reno SW 138kV GEN-2017-117 Interconnection (TOIF) (WFEC) | 143359 | Facilitate the interconnection of GEN-2017-117 | WFEC | 36 | 500000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Johnson County 345kV GEN-2017-149 Interconnection (TOIF) (OKGE) | 143401 | Facilitate the interconnection of GEN-2017-149 | OKGE | 36 | 795827
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Johnson County 345kV GEN-2017-154 Interconnection (TOIF) (OKGE) | 143411 | Facilitate the interconnection of GEN-2017-154 | OKGE | 36 | 795827
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Johnson County 345kV GEN-2017-149 Interconnection (Non-shared NU) (AEP) | 143572 | Facilitate the interconnection of GEN-2017-149 | AEP | 36 | 250000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Johnson County 345kV GEN-2017-154 Interconnection (Non-shared NU) (AEP) | 143573 | Facilitate the interconnection of GEN-2017-154 | AEP | 36 | 250000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Johnson County 345kV Interconnection Expansion (DISIS-2017-002) | 143400 | Facilitate the interconnection of GEN-2017-149 and GEN-2017-154 | OKGE | 36 | 11024448
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Lawton Eastside - Terry Road 345kV Interconnection (TOIF) (AEP) | 143435 | Facilitate the interconnection of GEN-2017-171, GEN-2017-172 and GEN-2017-173 | AEP | 36 | 3876319
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Lawton Eastside - Terry Road 345kV New Interconnection Substation (DISIS-2017-002) | 143434 | Facilitate the interconnection of GEN-2017-171, GEN-2017-172, and GEN-2017-173 | AEP | 36 | 18137968
Contingent | DISIS-2017-002 | Steady State | 04 SOUTHEAST | 2023 ITP | ERIS | Matthewson - Redbud 345 kV New Line | 158573/158574/TBD | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | OKGE |  | 110770850
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Minco 345kV GEN-2017-150 Interconnection (TOIF) (OKGE) | 143403 | Facilitate the interconnection of GEN-2017-150 | OKGE | 20 | 795827
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Minco 345kV GEN-2017-233 Interconnection (TOIF) (OKGE) | 143543 | Facilitate the interconnection of GEN-2017-233 | OKGE | 20 | 795827
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Minco 345kV Interconnection Expansion (DISIS-2017-002) | 143402 | Facilitate the interconnection of GEN-2017-150 and GEN-2017-233 | OKGE | 20 | 1790448
Contingent | DISIS-2017-002 CF | Steady State | 04 SOUTHEAST | 2020 ITP | ERIS | Multi - Border - Woodward 345 kV Tap | 122796/122823/14382 | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA(NTC - 210627/210628) | AEP/OKGE |  | 38547935
Contingent | DISIS-2017-002 | Steady State | 04 SOUTHEAST | 2020 ITP | NRIS | Multi - Minco - Pleasant Valley - Draper 345 Kv | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | OKGE/TBD |  | 100405248
Contingent | DISIS-2017-002 CF | Steady State | 04 SOUTHEAST | DPA-2017-August-767-774-776 | NRIS | Multi - Park Community - Sunshine 138 kV | 72013-72016, 72018 - 72027, 72029 - 72031 | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW.(NTC - 210483, 210669) | WFEC |  | 66482000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Renfrow 345kV GEN-2017-203 Interconnection (Non-Shared NU) (OKGE) | 143492 | Facilitate the interconnection of GEN-2017-203 | OKGE | 20 | 1790448
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Renfrow 345kV GEN-2017-203 Interconnection (TOIF) (OKGE) | 143493 | Facilitate the interconnection of GEN-2017-203 | OKGE | 20 | 1591654
Current Study | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | SPA Brown to Brown 138 kV Equipment Upgrade | 156498 | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | SWPA | 36 | 825000
Contingent | DISIS-2017-002 CF | Steady State | 04 SOUTHEAST | DISIS-2017-002 | NRIS | SPA Brown to Brown 138 kV Equipment Upgrade | 156498 | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | SWPA |  | 825000
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Sunnyside 345kV GEN-2017-167 Interconnection (TOIF) (OKGE) | 143429 | Facilitate the interconnection of GEN-2017-167 | OKGE | 36 | 1591654
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Sunnyside 345kV Interconnection Expansion (DISIS-2017-002) | 143426 | Facilitate the interconnection of GEN-2017-167 | OKGE | 36 | 8195816
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Tryon 138kV GEN-2017-230 Interconnection (Non-Shared NU) (OKGE) | 143536 | Facilitate the interconnection of GEN-2017-230 | OKGE | 20 | 1133420
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Tryon 138kV GEN-2017-230 Interconnection (TOIF) (OKGE) | 143537 | Facilitate the interconnection of GEN-2017-230 | OKGE | 20 | 934626
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Woodring 345kV GEN-2017-164 Interconnection (TOIF) (OKGE) | 143425 | Facilitate the interconnection of GEN-2017-164 | OKGE | 20 | 795827
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Woodring 345kV GEN-2017-178 Interconnection (TOIF) (OKGE) | 143445 | Facilitate the interconnection of GEN-2017-178 | OKGE | 20 | 795827
Interconnection | DISIS-2017-002 | Steady State | 04 SOUTHEAST | DISIS-2017-002 | ERIS | Woodring 345kV Interconnection Expansion (DISIS-2017-002) | 143424 | Facilitate the interconnection of GEN-2017-164 and GEN-2017-178 | OKGE | 20 | 1790448
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Deaf Smith - Plant X 230kV GEN-2017-146 Interconnection (Non-Shared NU) (SPS) | 143394 | Facilitate the interconnection of GEN-2017-146 | SPS | 36 | 9822164
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Deaf Smith - Plant X 230kV GEN-2017-146 Interconnection (TOIF) (SPS) | 143395 | Facilitate the interconnection of GEN-2017-146 | SPS | 36 | 1284070
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Mahoney 230kV GEN-2017-239 Interconnection (Non-Shared NU) (SPS) | 143552 | Facilitate the interconnection of GEN-2017-239 | SPS | 36 | 820698
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Mahoney 230kV GEN-2017-239 Interconnection (TOIF) (SPS) | 143553 | Facilitate the interconnection of GEN-2017-239 | SPS | 36 | 1049789
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Sulphur Springs 115kV GEN-2017-187 Interconnection (Non-Shared NU) (SPS) | 143460 | Facilitate the interconnection of GEN-2017-187 | SPS | 36 | 16197956
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Sulphur Springs 115kV GEN-2017-187 Interconnection (TOIF) (SPS) | 143461 | Facilitate the interconnection of GEN-2017-187 | SPS | 36 | 841906
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Tolk 230kV GEN-2017-158 Interconnection (Non-Shared NU) (SPS) | 143418 | Facilitate the interconnection of GEN-2017-158 | SPS | 30 | 3935078
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | Tolk 230kV GEN-2017-158 Interconnection (TOIF) (SPS) | 143419 | Facilitate the interconnection of GEN-2017-158 | SPS | 30 | 1329304
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | TUCO - Oklaunion 345kV GEN-2017-151 Interconnection (Non-Shared NU) (SPS) | 143404 | Facilitate the interconnection of GEN-2017-151 | SPS | 36 | 18991050
Interconnection | DISIS-2017-002 | Steady State | 05 SOUTHWEST | DISIS-2017-002 | ERIS | TUCO - Oklaunion 345kV GEN-2017-151 Interconnection (TOIF) (SPS) | 143405 | Facilitate the interconnection of GEN-2017-151 | SPS | 36 | 1569115
2006403021

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 26L and 26SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2017-144 | 02 NEBRASKA | ERIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 2012 ITP10 | Yes | Yes | 0.22035 | 4638700% | 451409958 | 0
GEN-2017-105 | 02 NEBRASKA | ERIS | 210680 | 143660/143661/143662 | Line - S3454 - S3740 345 kV | Build an approximately 29 mile 345 kV line from S3454 to S3740 Circuit 1. Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04445 | 4638700% | 35572073.7399 | 0
GEN-2017-105 | 02 NEBRASKA | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.10635 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-105 | 02 NEBRASKA | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.03261 | 4593100% | 60475092 | 0
GEN-2017-183 | 03 CENTRAL | NRIS |  | 159068 | Install a second 650 MVA TX at Nashua | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650 MVA | DISIS-2017-002 | No | Yes | 0.11755 | TBD (48 month lead time) | 22759204 | 0
GEN-2017-105 | 02 NEBRASKA | ERIS | 220723 | 158448 | Tap S1345 - S1236 161 kV | Tap the existing S1345 - S1236 161 kV line and connect to substation S1252 | SUS-038 | Yes | Yes | 0.0322 | 3/1/2024 (delayed) | 13199959 | 0
GEN-2017-108 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.0355 | 4593100% | 60475092 | 0
GEN-2017-108 | 03 CENTRAL | NRIS |  | 156851 | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to archieve a minimum rating of 280 MVA | DISIS-2017-002 | No | Yes | 0.378 | TBD (48 month lead time) | 41157960 | 0
GEN-2017-115 | 03 CENTRAL | ERIS | 210680 | 143660/143661/143662 | Line - S3454 - S3740 345 kV | Build an approximately 29 mile 345 kV line from S3454 to S3740 Circuit 1. Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05965 | 4638700% | 35572073.7399 | 0
GEN-2017-115 | 03 CENTRAL | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.12989 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-115 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04094 | 4593100% | 60475092 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210489 | 82111/82112/82114/82115 | Line - Cogar - OU SW 138 kV | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.14354 | 4650700% | 23560000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210489 | 82111/82112/82114/82115 | Line - Cogar - OU SW 138 kV | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.04075 | 4650700% | 23560000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210545 | 112435 | Line - East Kingfisher - Kingfisher 138kV | Rebuild 2.03 miles of 138 kV line from Kingfisher to East Kingfisher and upgrade any necessary terminal equipment at East Kingfisher and/or Kingfisher to increase the summer emergency rating to 187 MVA | 2019 ITP | Yes | Yes | 0.04363 | 4653800% | 1000000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05361 | 4574700% | 38547935 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.03495 | 4565800% | 100405248 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.14354 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.28043 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.14354 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.13689 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.13553 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.13689 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.0724 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06449 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210483, 210669 | 72013-72016, 72018 - 72027, 72029 - 72031 | Multi - Park Community - Sunshine 138 kV | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 9.0 mile 138 kV line from Kingfisher SW - Park Community. Tap the East Kingfisher - Reeding 138 kV line and construct new Kingfisher SW 138 kV substation with 4-terminal ring bus. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | Yes | 0.0724 | 4623400% | 66482000 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03002 | 4607900% | 115124697 | 0
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.03292 | 4570000% | 25800000 | 9453182
GEN-2017-117 | 04 SOUTHEAST | ERIS | 210556 |  | Rebuild Hennessey - Bull Foot Tap 138kV to rating 268/287 MVA | Rebuild Hennessey - Bull Foot Tap 138kV to rating 268/287 MVA | DISIS-2016-002 | Yes | Yes | 0.04866 | TBD (36 month lead time) | - | 0
GEN-2017-119 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.03316 | 4593100% | 60475092 | 0
GEN-2017-120 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.03181 | 4593100% | 60475092 | 0
GEN-2017-121 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.03475 | 4565800% | 142601178 | 0
GEN-2017-125 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04858 | 4593100% | 60475092 | 0
GEN-2017-132 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22899 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-132 | 04 SOUTHEAST | ERIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22979 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-132 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03993 | 4574700% | 38547935 | 0
GEN-2017-132 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.031 | 4565800% | 100405248 | 0
GEN-2017-133 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22899 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-133 | 04 SOUTHEAST | ERIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22979 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-133 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03993 | 4574700% | 38547935 | 0
GEN-2017-133 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.031 | 4565800% | 100405248 | 0
GEN-2017-134 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22899 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-134 | 04 SOUTHEAST | ERIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22979 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-134 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03993 | 4574700% | 38547935 | 0
GEN-2017-134 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.031 | 4565800% | 100405248 | 0
GEN-2017-137 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22899 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-137 | 04 SOUTHEAST | ERIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.22979 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-137 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03993 | 4574700% | 38547935 | 0
GEN-2017-137 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.031 | 4565800% | 100405248 | 0
GEN-2017-140 | 04 SOUTHEAST | ERIS | 210708/210711 | 156293/156294 | Multi - Siloam Springs-Siloam Springs City 161 kV Terminal Upgrades | Upgrade terminal equipment at Siloam Springs 161 kV substation and upgrade terminal equipment at Siloam Springs City 161 kV substation | 2022 ITP | Yes | Yes | 0.03591 | 4557600% | 1022030 | 0
GEN-2017-140 | 04 SOUTHEAST | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07932 | 4607900% | 115124697 | 0
GEN-2017-140 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.03124 | 4570000% | 25800000 | 9453182
GEN-2017-141 | 04 SOUTHEAST | ERIS | 210708/210711 | 156293/156294 | Multi - Siloam Springs-Siloam Springs City 161 kV Terminal Upgrades | Upgrade terminal equipment at Siloam Springs 161 kV substation and upgrade terminal equipment at Siloam Springs City 161 kV substation | 2022 ITP | Yes | Yes | 0.03591 | 4557600% | 1022030 | 0
GEN-2017-141 | 04 SOUTHEAST | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07932 | 4607900% | 115124697 | 0
GEN-2017-141 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.03124 | 4570000% | 25800000 | 9453182
GEN-2017-175 | 01 NORTH | ERIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 2012 ITP10 | Yes | Yes | 0.04038 | 4638700% | 451409958 | 0
GEN-2017-214 | 01 NORTH | ERIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 2012 ITP10 | Yes | Yes | 0.04316 | 4638700% | 451409958 | 0
GEN-2017-144 | 02 NEBRASKA | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.11671 | 4593100% | 60475092 | 0
GEN-2017-144 | 02 NEBRASKA | ERIS | 200277 | 50889 | Thedford 345/115 kV Transformer | Install new 345/115 kV 400 MVA transformer at Thedford substation. Install any necessary 115 kV terminal equipment. | HPILS | Yes | Yes | 0.03988 | 4638700% | 451409958 | 0
GEN-2017-146 | 05 SOUTHWEST | ERIS |  | 122645 | Curry - Deafsmith 115 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild Curry - Deafsmith 115 kV Ckt 1 line to achieve minimum normal/emergency rating of 90/90 MVA. | DISIS-2016-002 | Yes | Yes | 0.03283 | 12/15/2021 (delayed) | 4852215 | 4852215
GEN-2017-146 | 05 SOUTHWEST | ERIS |  | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild Deaf Smith - Plant X 230 kV Ckt 1 line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.45248 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2017-146 | 05 SOUTHWEST | ERIS |  | 122648 | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVar at Deafsmith 115 kV substation | DISIS-2016-002 | Yes | Yes | 0.08792 | 10/28/2021 (delayed) | 3318137 | 3318137
GEN-2017-146 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.17089 | 4576700% | 12000000 | 12000000
GEN-2017-146 | 05 SOUTHWEST | ERIS | 210574 | 143167 | Line - Cargill - Friona 115 kV | Rebuild 1.15 miles of existing 115 kV line from Cargill to Friona and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 2020 ITP | Yes | Yes | 0.03309 | 4579200% | 1301898 | 0
GEN-2017-146 | 05 SOUTHWEST | ERIS | 210574 | 122876 | Line - Deaf Smith #6 - Hereford 115 kV | Rebuild 2.33 miles of 115 kV line from Deaf Smith #6 to Hereford and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA | 2020 ITP | Yes | Yes | 0.03309 | 4579200% | 6583793 | 0
GEN-2017-146 | 05 SOUTHWEST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.1682 | 4574700% | 38547935 | 0
GEN-2017-146 | 05 SOUTHWEST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.05581 | 4565800% | 100405248 | 0
GEN-2017-146 | 05 SOUTHWEST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.1842 | 4570000% | 25800000 | 9453182
GEN-2017-146 | 05 SOUTHWEST | ERIS | 210574 | 122871 | Sub - Deaf Smith #6 - Friona 115 kV | Rebuild 18.9 miles of 115 kV line from Deaf Smith #6 to Friona and upgrade any necessary terminal equipment at Deaf Smith #6 and/or Friona to achieve a summer emergency rating of 120 MVA | 2020 ITP | Yes | Yes | 0.03309 | 4563400% | 138360016 | 0
GEN-2017-146 | 05 SOUTHWEST | ERIS |  | 122647 | Tuco 230 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.11991 | 12/31/2020 (delayed) | 5943138 | 5943138
GEN-2017-149 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06313 | 4574700% | 38547935 | 0
GEN-2017-149 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.07226 | 4565800% | 100405248 | 0
GEN-2017-149 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.0483 | 4570000% | 25800000 | 9453182
GEN-2017-150 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.08059 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-150 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07414 | 4574700% | 38547935 | 0
GEN-2017-150 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.2734 | 4565800% | 100405248 | 0
GEN-2017-150 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.04063 | 4570000% | 25800000 | 9453182
GEN-2017-151 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.24934 | 4576700% | 12000000 | 12000000
GEN-2017-151 | 05 SOUTHWEST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.2466 | 4574700% | 38547935 | 0
GEN-2017-151 | 05 SOUTHWEST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.07104 | 4565800% | 100405248 | 0
GEN-2017-151 | 05 SOUTHWEST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.34856 | 4570000% | 25800000 | 9453182
GEN-2017-151 | 05 SOUTHWEST | ERIS |  | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. | DISIS-2016-002 | Yes | Yes | 0.06644 | 12/15/2020 (delayed) | 968567 | 968567
GEN-2017-151 | 05 SOUTHWEST | ERIS |  | 122647 | Tuco 230 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.12904 | 12/31/2020 (delayed) | 5943138 | 5943138
GEN-2017-154 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06313 | 4574700% | 38547935 | 0
GEN-2017-154 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.07226 | 4565800% | 100405248 | 0
GEN-2017-154 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.0483 | 4570000% | 25800000 | 9453182
GEN-2017-158 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.21733 | 4576700% | 12000000 | 12000000
GEN-2017-158 | 05 SOUTHWEST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.21466 | 4574700% | 38547935 | 0
GEN-2017-158 | 05 SOUTHWEST | ERIS | 210681/220726 | 156407 - 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA. Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.04562 | 4615700% | 61648149 | 0
GEN-2017-158 | 05 SOUTHWEST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.06083 | 4565800% | 100405248 | 0
GEN-2017-158 | 05 SOUTHWEST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.22388 | 4570000% | 25800000 | 9453182
GEN-2017-158 | 05 SOUTHWEST | ERIS |  | 122647 | Tuco 230 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.2071 | 12/31/2020 (delayed) | 5943138 | 5943138
GEN-2017-164 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.08592 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-164 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.03732 | 4565800% | 100405248 | 0
GEN-2017-164 | 04 SOUTHEAST | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.08701 | 4607900% | 115124697 | 0
GEN-2017-167 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.03402 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-167 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05874 | 4574700% | 38547935 | 0
GEN-2017-167 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.03322 | 4565800% | 100405248 | 0
GEN-2017-167 | 04 SOUTHEAST | ERIS | 210656/210657 | 143806/143815/143816/143817 | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | Build new 2.1 mile 138 kV line from Marietta Tap (OKGE) – Marietta Switchyard (WFEC) Convert the Marietta 2 substation from 69 kV to 138 kV and install terminal equipment to support a new 138 kV line from Marietta 4 Rebuild the existing 69 kV line from Rocky Point to Marietta 2 as a 138 kV line Replace the existing relays at Rocky Point Install terminal equipment at WFEC Marietta Switch to support a new 138 kV line from OG&E Marietta. | 2021 ITP | Yes | Yes | 0.03164 | 4602200% | 34759778 | 0
GEN-2017-167 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.0663 | 4570000% | 25800000 | 9453182
GEN-2017-171 | 04 SOUTHEAST | ERIS | 210489 | 82111/82112/82114/82115 | Line - Cogar - OU SW 138 kV | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.0318 | 4650700% | 23560000 | 0
GEN-2017-171 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.03544 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-171 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08299 | 4574700% | 38547935 | 0
GEN-2017-171 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.09338 | 4565800% | 100405248 | 0
GEN-2017-171 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.09853 | 4570000% | 25800000 | 9453182
GEN-2017-172 | 04 SOUTHEAST | ERIS | 210489 | 82111/82112/82114/82115 | Line - Cogar - OU SW 138 kV | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.0318 | 4650700% | 23560000 | 0
GEN-2017-172 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.03544 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-172 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08299 | 4574700% | 38547935 | 0
GEN-2017-172 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.09338 | 4565800% | 100405248 | 0
GEN-2017-172 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.09853 | 4570000% | 25800000 | 9453182
GEN-2017-173 | 04 SOUTHEAST | ERIS | 210489 | 82111/82112/82114/82115 | Line - Cogar - OU SW 138 kV | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.0318 | 4650700% | 23560000 | 0
GEN-2017-173 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.03544 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-173 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08299 | 4574700% | 38547935 | 0
GEN-2017-173 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.09338 | 4565800% | 100405248 | 0
GEN-2017-173 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.09853 | 4570000% | 25800000 | 9453182
GEN-2017-215 | 01 NORTH | ERIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 2012 ITP10 | Yes | Yes | 0.04316 | 4638700% | 451409958 | 0
GEN-2017-175 | 01 NORTH | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.05897 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-175 | 01 NORTH | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04858 | 4593100% | 60475092 | 0
GEN-2017-178 | 04 SOUTHEAST | NRIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.08592 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-178 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.03732 | 4565800% | 100405248 | 0
GEN-2017-178 | 04 SOUTHEAST | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.08701 | 4607900% | 115124697 | 0
GEN-2017-181 | 02 NEBRASKA | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.24158 | 4593100% | 60475092 | 0
GEN-2017-184 | 03 CENTRAL | NRIS |  | 159068 | Install a second 650 MVA TX at Nashua | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650 MVA | DISIS-2017-002 | No | Yes | 0.12319 | TBD (48 month lead time) | 22759204 | 0
GEN-2017-182 | 02 NEBRASKA | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.24158 | 4593100% | 60475092 | 0
GEN-2017-105 | 02 NEBRASKA | NRIS |  | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | No | Yes | 0.03633 | TBD (36 month lead time) | 8300000 | 0
GEN-2017-183 | 03 CENTRAL | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.04031 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-183 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.08455 | 4593100% | 60475092 | 0
GEN-2017-183 | 03 CENTRAL | ERIS | 30601 | 50772 | Nashua 345/161 kV Transformer Upgrade Ckt11 | Increase rating of Nashua transformer to 650/715 MVA. | 2023 ITP | Yes | Yes | 0.10673 | TBD (48 month lead time) | 8306343 | 0
GEN-2017-181 | 02 NEBRASKA | NRIS |  | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | No | Yes | 0.06089 | TBD (36 month lead time) | 8300000 | 0
GEN-2017-182 | 02 NEBRASKA | NRIS |  | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | No | Yes | 0.06089 | TBD (36 month lead time) | 8300000 | 0
GEN-2017-184 | 03 CENTRAL | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.03058 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-184 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.07083 | 4593100% | 60475092 | 0
GEN-2017-184 | 03 CENTRAL | ERIS | 30601 | 50772 | Nashua 345/161 kV Transformer Upgrade Ckt11 | Increase rating of Nashua transformer to 650/715 MVA. | 2023 ITP | Yes | Yes | 0.11019 | TBD (48 month lead time) | 8306343 | 0
GEN-2017-201 | 02 NEBRASKA | NRIS |  | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | No | Yes | 0.03762 | TBD (36 month lead time) | 8300000 | 0
GEN-2017-183 | 03 CENTRAL | NRIS |  | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 286 MVA | DISIS-2017-002 | No | Yes | 0.04808 | TBD (48 month lead time) | 112911 | 0
GEN-2017-187 | 05 SOUTHWEST | ERIS |  | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild Deaf Smith - Plant X 230 kV Ckt 1 line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.12466 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2017-187 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.23969 | 4576700% | 12000000 | 12000000
GEN-2017-187 | 05 SOUTHWEST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.23969 | 4574700% | 38547935 | 0
GEN-2017-187 | 05 SOUTHWEST | ERIS | 210681/220726 | 156407 - 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA. Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.04999 | 4615700% | 61648149 | 0
GEN-2017-187 | 05 SOUTHWEST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.07946 | 4565800% | 100405248 | 0
GEN-2017-187 | 05 SOUTHWEST | ERIS |  | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum emergency rating of 456 MVA. | DISIS-2016-002 | Yes | Yes | 0.12367 | 12/31/2020 (delayed) | 697514 | 697514
GEN-2017-187 | 05 SOUTHWEST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.25061 | 4570000% | 25800000 | 9453182
GEN-2017-187 | 05 SOUTHWEST | ERIS |  | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. | DISIS-2016-002 | Yes | Yes | 0.06268 | 12/15/2020 (delayed) | 968567 | 968567
GEN-2017-187 | 05 SOUTHWEST | ERIS |  | 122647 | Tuco 230 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.12706 | 12/31/2020 (delayed) | 5943138 | 5943138
GEN-2017-188 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.0574 | 4565800% | 142601178 | 0
GEN-2017-188 | 03 CENTRAL | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03579 | 4607900% | 115124697 | 0
GEN-2017-195 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.04018 | 4565800% | 142601178 | 0
GEN-2017-195 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04078 | 4593100% | 60475092 | 0
GEN-2017-196 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.04018 | 4565800% | 142601178 | 0
GEN-2017-196 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04078 | 4593100% | 60475092 | 0
GEN-2017-198 | 02 NEBRASKA | ERIS | 210680 | 143660/143661/143662 | Line - S3454 - S3740 345 kV | Build an approximately 29 mile 345 kV line from S3454 to S3740 Circuit 1. Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04238 | 4638700% | 35572073.7399 | 0
GEN-2017-105 | 02 NEBRASKA | NRIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | DISIS-2017-002 (Originally identified in 2012 ITP10) | Yes | Yes | 0.03408 | 4638700% | 451409958 | 0
GEN-2017-201 | 02 NEBRASKA | ERIS | 210680 | 143660/143661/143662 | Line - S3454 - S3740 345 kV | Build an approximately 29 mile 345 kV line from S3454 to S3740 Circuit 1. Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03112 | 4638700% | 35572073.7399 | 0
GEN-2017-201 | 02 NEBRASKA | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.05375 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-201 | 02 NEBRASKA | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.07585 | 4593100% | 60475092 | 0
GEN-2017-184 | 03 CENTRAL | NRIS |  | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 286 MVA | DISIS-2017-002 | No | Yes | 0.05 | TBD (48 month lead time) | 112911 | 0
GEN-2017-203 | 04 SOUTHEAST | ERIS | 200397 | 51526/51527 | Multi - Driftwood 138/69 kV Substation and Transformer | Tap the 138 kV line from Byron to Cherokee City to construct new Driftwood substation. Install any required 138 kV terminal upgrades required to install 138/69 kV transformer. Install new 138/69 kV transformer at new Driftwood substation. Install new 69 kV terminal for 69 kV line from Hazelton Junction. | 2016 ITPNT | Yes | Yes | 0.03439 | 7/31/2023 (delayed) | 4200000 | 0
GEN-2017-203 | 04 SOUTHEAST | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06657 | 4607900% | 115124697 | 0
GEN-2017-209 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.05225 | 4565800% | 142601178 | 0
GEN-2017-209 | 03 CENTRAL | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.03344 | 4593100% | 60475092 | 0
GEN-2017-144 | 02 NEBRASKA | ERIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | DISIS-2017-002 (Originally identified in 2012 ITP10) | Yes | Yes | 0.22035 | 4638700% | 451409958 | 0
GEN-2017-210 | 02 NEBRASKA | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.19928 | 4593100% | 60475092 | 0
GEN-2017-201 | 02 NEBRASKA | NRIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | DISIS-2017-002 (Originally identified in 2012 ITP10) | Yes | Yes | 0.03389 | 4638700% | 451409958 | 0
GEN-2017-214 | 01 NORTH | ERIS |  | 143226 | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.1083 | TBD (36 month lead time) | 10061320 | 10061320
GEN-2017-214 | 01 NORTH | ERIS | 210585 | 143159 | Device - Moorehead 230 kV | Install 2x40 MVAR reactors at Moorehead to control voltage on the 115 kV and 230 kV transmission systems | 2020 ITP | Yes | Yes | 0.03188 | 4565700% | 6499045.72 | 0
GEN-2017-214 | 01 NORTH | ERIS | 210648/210639 | 122734/122735/143613/143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation. Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line. Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.05217 | 4565800% | 4486175 | 0
GEN-2017-214 | 01 NORTH | ERIS | 220720 | 143588, 143589 | Multi - Kummer Ridge - Roundup 345 kV New Line and Patent Gate and Roundup 345/115 kV Substations | Build 33.2 mile new 345 kV line from Kummer Ridge to Round Up and install terminal equipment at Kummer Ridge substation 345 kV to support a new 345 kV line from Round Up | 2021 ITP | Yes | Yes | 0.04769 | 4574800% | 81950669 | 0
GEN-2017-214 | 01 NORTH | ERIS | 210663/210675 | 144163/144171/144177/144178/144198/144199 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. Build a new 4.5 mile 115 kV line from NE Williston to Folvag. Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | 2021 ITP | Yes | Yes | 0.08248 | 4562700% | 38004996 | 0
GEN-2017-214 | 01 NORTH | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.04811 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-214 | 01 NORTH | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04153 | 4593100% | 60475092 | 0
GEN-2017-214 | 01 NORTH | ERIS | 210663/210675 | 143714, 144226, 144227, 144230, 144231, 144233, 144235 - 144239 | Multi - Tande - Finstad - Leland Olds 345 kV | Build a 48 mile 345 kV line from Finstad to Tande. Build a 5-mile 115 kV line from Finstad to Vanhook. Build a new 115 kV Substation with terminal equipment to support a line from Vanhook 115 kV substation. Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer Install a switched shunt at Finstad. Install a 345/115 kV Ckt 1 Transformer at Finstad 345 Install a 345/115 kV Ckt 2 transformer at Finstad 115 and upgrade any necessary 115 kV terminal equipment. Build a 123 mile 345 kV line from Leland Olds to Finstad. Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. Install new 115 kV terminal equipment at Vanhook to support a new 115 kV line from Finstad. | 2021 ITP | Yes | Yes | 0.1055 | 4635600% | 341281863 | 0
GEN-2017-214 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04702 | 4602200% | 3277470 | 0
GEN-2017-214 | 01 NORTH | ERIS | 210562 | 122602 | Sub - Jamestown 230 kV Redundant Bus Tie | Add a redundant bus to Jamestown 230 kV substation to mitigate for a fault and breaker fail of CB 9182. | DISIS-2016-001 | Yes | Yes | 0.04519 | 4565700% | 1510000 | 1510000
GEN-2017-210 | 02 NEBRASKA | ERIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | DISIS-2017-002 (Originally identified in 2012 ITP10) | Yes | Yes | 0.03007 | 4638700% | 451409958 | 0
GEN-2017-215 | 01 NORTH | ERIS |  | 143226 | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.1083 | TBD (36 month lead time) | 10061320 | 10061320
GEN-2017-215 | 01 NORTH | ERIS | 210585 | 143159 | Device - Moorehead 230 kV | Install 2x40 MVAR reactors at Moorehead to control voltage on the 115 kV and 230 kV transmission systems | 2020 ITP | Yes | Yes | 0.03188 | 4565700% | 6499045.72 | 0
GEN-2017-215 | 01 NORTH | ERIS | 210648/210639 | 122734/122735/143613/143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation. Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line. Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.05217 | 4565800% | 4486175 | 0
GEN-2017-215 | 01 NORTH | ERIS | 220720 | 143588, 143589 | Multi - Kummer Ridge - Roundup 345 kV New Line and Patent Gate and Roundup 345/115 kV Substations | Build 33.2 mile new 345 kV line from Kummer Ridge to Round Up and install terminal equipment at Kummer Ridge substation 345 kV to support a new 345 kV line from Round Up | 2021 ITP | Yes | Yes | 0.04769 | 4574800% | 81950669 | 0
GEN-2017-215 | 01 NORTH | ERIS | 210663/210675 | 144163/144171/144177/144178/144198/144199 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. Build a new 4.5 mile 115 kV line from NE Williston to Folvag. Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | 2021 ITP | Yes | Yes | 0.08248 | 4562700% | 38004996 | 0
GEN-2017-215 | 01 NORTH | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.04811 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-215 | 01 NORTH | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04153 | 4593100% | 60475092 | 0
GEN-2017-215 | 01 NORTH | ERIS | 210663/210675 | 143714, 144226, 144227, 144230, 144231, 144233, 144235 - 144239 | Multi - Tande - Finstad - Leland Olds 345 kV | Build a 48 mile 345 kV line from Finstad to Tande. Build a 5-mile 115 kV line from Finstad to Vanhook. Build a new 115 kV Substation with terminal equipment to support a line from Vanhook 115 kV substation. Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer Install a switched shunt at Finstad. Install a 345/115 kV Ckt 1 Transformer at Finstad 345 Install a 345/115 kV Ckt 2 transformer at Finstad 115 and upgrade any necessary 115 kV terminal equipment. Build a 123 mile 345 kV line from Leland Olds to Finstad. Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. Install new 115 kV terminal equipment at Vanhook to support a new 115 kV line from Finstad. | 2021 ITP | Yes | Yes | 0.1055 | 4635600% | 341281863 | 0
GEN-2017-215 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04702 | 4602200% | 3277470 | 0
GEN-2017-215 | 01 NORTH | ERIS | 210562 | 122602 | Sub - Jamestown 230 kV Redundant Bus Tie | Add a redundant bus to Jamestown 230 kV substation to mitigate for a fault and breaker fail of CB 9182. | DISIS-2016-001 | Yes | Yes | 0.04519 | 4565700% | 1510000 | 1510000
GEN-2017-220 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.04918 | 4565800% | 142601178 | 0
GEN-2017-220 | 03 CENTRAL | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0375 | 4607900% | 115124697 | 0
GEN-2017-221 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.04918 | 4565800% | 142601178 | 0
GEN-2017-221 | 03 CENTRAL | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0375 | 4607900% | 115124697 | 0
GEN-2017-222 | 01 NORTH | ERIS | 210600 | 143178, 143179 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | Rebuild 0.9 miles of 161 kV line from S1260 to S1362 line to achieve 243 MVA summer emergency rating. Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA-2018-October-949 | Yes | Yes | 0.07517 | 4/1/2024 (delayed) | 733400 | 0
GEN-2017-226 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.05355 | 4565800% | 142601178 | 0
GEN-2017-226 | 03 CENTRAL | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03928 | 4607900% | 115124697 | 0
GEN-2017-227 | 03 CENTRAL | ERIS | 210592/210626 | 112509/122598 | Line - Wolf Creek - Blackberry 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA. Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Yes | Yes | 0.05355 | 4565800% | 142601178 | 0
GEN-2017-227 | 03 CENTRAL | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03928 | 4607900% | 115124697 | 0
GEN-2017-230 | 04 SOUTHEAST | ERIS | 220738/TBD | 158573/158574/TBD | Matthewson - Redbud 345 kV New Line | Build approximately 38 miles of 345 kV line from Matthewson to Redbud with a minimal normal/emergency rating of 1792 MVA. | DISIS-2017-002 (Identified in 2023 ITP) | No | Yes | 0.02779 | TBD (48 month lead time) | 110770850 | 0
GEN-2017-230 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.03077 | 4565800% | 100405248 | 0
GEN-2017-230 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.03124 | 4570000% | 25800000 | 9453182
GEN-2017-231 | 04 SOUTHEAST | ERIS | 210544/210593/210540 | 112502/112460/112458/112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04604 | 4607900% | 115124697 | 0
GEN-2017-231 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.0313 | 4570000% | 25800000 | 9453182
GEN-2017-232 | 04 SOUTHEAST | ERIS | 210586 | 112443 | Line - Russett - South Brown 138 kV | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Yes | Yes | 0.32914 | 4672200% | 10267390.81 | 0
GEN-2017-232 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04995 | 4574700% | 38547935 | 0
GEN-2017-232 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.05161 | 4565800% | 100405248 | 0
GEN-2017-232 | 04 SOUTHEAST | ERIS | 210656/210657 | 143806/143815/143816/143817 | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | Build new 2.1 mile 138 kV line from Marietta Tap (OKGE) – Marietta Switchyard (WFEC) Convert the Marietta 2 substation from 69 kV to 138 kV and install terminal equipment to support a new 138 kV line from Marietta 4 Rebuild the existing 69 kV line from Rocky Point to Marietta 2 as a 138 kV line Replace the existing relays at Rocky Point Install terminal equipment at WFEC Marietta Switch to support a new 138 kV line from OG&E Marietta. | 2021 ITP | Yes | Yes | 0.05579 | 4602200% | 34759778 | 0
GEN-2017-232 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.05246 | 4570000% | 25800000 | 9453182
GEN-2017-232 | 04 SOUTHEAST | NRIS |  | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | No | Yes | 0.71662 | TBD (36 month lead time) | 825000 | 0
GEN-2017-232 | 04 SOUTHEAST | ERIS | 200433 | 51764 | Sub - Tupelo - Tupelo Tap 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Tupelo to increase the rating of the 138 kV line between Tupelo substation and Tupelo Tap substation. | 2017 ITP10 | Yes | Yes | 0.10003 | 12/31/2023 (delayed) | 410000 | 0
GEN-2017-233 | 04 SOUTHEAST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0849 | 4574700% | 38547935 | 0
GEN-2017-233 | 04 SOUTHEAST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.26717 | 4565800% | 100405248 | 0
GEN-2017-233 | 04 SOUTHEAST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.03098 | 4570000% | 25800000 | 9453182
GEN-2017-234 | 02 NEBRASKA | ERIS | 200220 | 50442, 50445, 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | DISIS-2017-002 (Originally identified in 2012 ITP10) | Yes | Yes | 0.02851 | 4638700% | 451409958 | 0
GEN-2017-234 | 02 NEBRASKA | ERIS | 200477/210682 | 71963 - 71968 | Multi - Sheldon - Monolith 115 kV | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.10772 | 4593100% | 60475092 | 0
GEN-2017-234 | 02 NEBRASKA | ERIS | 210645 | 122739 | XFR - Columbus 230/115 | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 2021 ITP | Yes | Yes | 0.03446 | 4580900% | 4600000 | 0
GEN-2017-239 | 05 SOUTHWEST | ERIS |  | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild Deaf Smith - Plant X 230 kV Ckt 1 line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.12748 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2017-239 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.23957 | 4576700% | 12000000 | 12000000
GEN-2017-239 | 05 SOUTHWEST | ERIS | 210627/210628 | 122796/122823/14382 | Multi - Border - Woodward 345 kV Tap | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station. Build 0.84-miles of new 345 kV line from the new station to Chisholm with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.23957 | 4574700% | 38547935 | 0
GEN-2017-239 | 05 SOUTHWEST | ERIS | 210681/220726 | 156407 - 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA. Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.06125 | 4615700% | 61648149 | 0
GEN-2017-239 | 05 SOUTHWEST | ERIS | 210616, 210656, 210000 | 122863, 122848, 122849, 122850, 122851, 122858, 133085, 133106, 143176, 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Yes | Yes | 0.07945 | 4565800% | 100405248 | 0
GEN-2017-239 | 05 SOUTHWEST | ERIS |  | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum emergency rating of 456 MVA. | DISIS-2016-002 | Yes | Yes | 0.13058 | 12/31/2020 (delayed) | 697514 | 697514
GEN-2017-239 | 05 SOUTHWEST | ERIS | 210611 | 112307 | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Yes | Yes | 0.25052 | 4570000% | 25800000 | 9453182
GEN-2017-239 | 05 SOUTHWEST | ERIS |  | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. | DISIS-2016-002 | Yes | Yes | 0.0783 | 12/15/2020 (delayed) | 968567 | 968567
GEN-2017-239 | 05 SOUTHWEST | ERIS |  | 122647 | Tuco 230 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.09084 | 12/31/2020 (delayed) | 5943138 | 5943138

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44038 | 114.57 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43998 | 114.46 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCHIE_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43998 | 114.46 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCH:::HV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66725 | 112.9 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43857 | 110.12 | 301342 5BUTLER 161 541208 NEVADA 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66753 | 105.07 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44045 | 100.59 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44001 | 100.58 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCH:::HV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44001 | 100.58 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCHIE_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44118 | 108.76 | 541207 ARCHIE 5 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44118 | 108.15 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44078 | 108.03 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCH:::HV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44078 | 108.03 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCHIE_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66376 | 117.17 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66374 | 111.06 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 107.7 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66733 | 108.28 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66606 | 108.66 | 300949 7JASPER 345 709400 GI94_POI 345 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.6675 | 107.55 | 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.6675 | 107.55 | 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66666 | 107.52 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66556 | 116.43 | 541207 ARCHIE 5 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66593 | 107.72 | 541207 ARCHIE 5 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 1 | 118.77 | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 1 | 118.73 | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.6675 | 108.38 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.63861 | 117.3 | P12:161:AECI:CLINTON-HOLDEN | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.63906 | 110.7 | P12:161:AECI:CLINTON-HOLDEN | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.63861 | 117.3 | P12:161:AECI:CLINTON-HOLDEN:::HV:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.63906 | 110.7 | P12:161:AECI:CLINTON-HOLDEN:::HV:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66587 | 116.78 | P12:345:WERE:N345-AECI_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 120.34 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 117.04 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66928 | 109.56 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 120.34 | P12:345:WERE:N345-LACY-345:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 117.04 | P12:345:WERE:N345-LACY-345:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66928 | 109.56 | P12:345:WERE:N345-LACY-345:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.6675 | 108.22 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66796 | 116.38 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66829 | 107.52 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66796 | 116.38 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66796 | 116.38 | P23:345:GMO:SIBLEY-R3-8:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66829 | 107.52 | P23:345:GMO:SIBLEY-R3-8:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66731 | 108.64 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66731 | 108.64 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 117.19 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 117.19 | P23:345:KCPL-WERE:236LACYGNE-R4-6::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 120.31 | P23:345:WERE:N345-345-80:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66928 | 109.55 | P23:345:WERE:N345-345-80:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 120.31 | P23:345:WERE:N345-345-80::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66928 | 109.55 | P23:345:WERE:N345-345-80::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 117.12 | PROXY_P4_345kV_POI_760921_0 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 117.14 | PROXY_P4_345kV_POI_760921_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66932 | 117.12 | PROXY_P4_345kV_POI_760921_2 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66722 | 120.98 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.65213 | 102.75 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | TDF Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 107.7 | P12:345:WERE:N345-LACY-345:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44039 | 115.54 | 541207 ARCHIE 5 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 114.75 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 114.75 | P12:345:WERE:N345-LACY-345:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 114.71 | P23:345:WERE:N345-345-80:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 114.71 | P23:345:WERE:N345-345-80::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44039 | 114.66 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43998 | 114.55 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCH:::HV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43998 | 114.55 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCHIE_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66726 | 112.94 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.40065 | 112.22 | P12:161:AECI:CLINTON-HOLDEN | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.40065 | 112.22 | P12:161:AECI:CLINTON-HOLDEN:::HV:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43021 | 111.34 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-195 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.03205 | 111.34 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-196 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.03205 | 111.34 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43519 | 110.29 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43519 | 110.29 | P23:345:GMO:SIBLEY-R3-8:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 110.26 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 110.26 | P23:345:KCPL-WERE:236LACYGNE-R4-6::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 107.68 | P23:345:WERE:N345-345-80:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43858 | 110.21 | 301342 5BUTLER 161 541208 NEVADA 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 110.12 | PROXY_P4_345kV_POI_760921_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 110.08 | PROXY_P4_345kV_POI_760921_0 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 110.08 | PROXY_P4_345kV_POI_760921_2 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43398 | 110.05 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.40079 | 109.28 | P12:161:AECI:CLINTON-HOLDEN | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 107.68 | P23:345:WERE:N345-345-80::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.40079 | 109.28 | P12:161:AECI:CLINTON-HOLDEN:::HV:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.66731 | 109.08 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44054 | 108.98 | 541207 ARCHIE 5 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43358 | 105.22 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43641 | 104.41 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 108.14 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43641 | 104.41 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 108.14 | P12:345:WERE:N345-LACY-345:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 108.12 | P23:345:WERE:N345-345-80:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 108.12 | P23:345:WERE:N345-345-80::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44054 | 108.03 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44013 | 107.96 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCH:::HV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.44013 | 107.96 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCHIE_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43641 | 104.41 | P23:345:GMO:SIBLEY-R3-8:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 104.15 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 104.15 | P23:345:KCPL-WERE:236LACYGNE-R4-6::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 104.03 | PROXY_P4_345kV_POI_760921_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 104 | P12:345:WERE:N345-LACY_345:: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 104 | P12:345:WERE:N345-LACY-345:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 104 | PROXY_P4_345kV_POI_760921_2 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43472 | 103.99 | PROXY_P4_345kV_POI_760921_0 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26WP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.43936 | 103.98 | 301342 5BUTLER 161 541208 NEVADA 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44115 | 101.19 | 541207 ARCHIE 5 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44115 | 100.6 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44071 | 100.53 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCHIE_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43035 | 104.72 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-195 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.03213 | 104.72 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-196 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.03213 | 104.72 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43873 | 103.8 | 301342 5BUTLER 161 541208 NEVADA 5 161 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43539 | 103.69 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43539 | 103.69 | P23:345:GMO:SIBLEY-R3-8:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 103.66 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 103.66 | P23:345:KCPL-WERE:236LACYGNE-R4-6::WERE VERSION:EHV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 103.53 | PROXY_P4_345kV_POI_760921_1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.44071 | 100.53 | P12:161:GMO:NEVADA-BUTLER-ADRIAN-ARCH:::HV: | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 103.5 | PROXY_P4_345kV_POI_760921_0 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 422 | 432 | 0.66415 | 100.05 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.43415 | 103.5 | PROXY_P4_345kV_POI_760921_2 | Cumulative Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.65214 | 102.79 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | TDF Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-108 | FROM->TO | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.65212 | 100.97 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | TDF Impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52756 | 117.91 | 515120 RUSSET-4 138 521044 RUSSETT4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52756 | 115.67 | P12:138:OKGE-SWPA-WFEC:BKRBKR250:::: | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52756 | 115.67 | P12:138:WFEC:BROWN_RUSSETT:::: | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52756 | 115.09 | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52753 | 105.33 | 515120 RUSSET-4 138 521044 RUSSETT4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52753 | 103.3 | P12:138:OKGE-SWPA-WFEC:BKRBKR250:::: | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52753 | 103.3 | P12:138:WFEC:BROWN_RUSSETT:::: | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.52753 | 102.78 | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.7173 | 123.08 | 515152 BROWNTP4 138 515155 BODLE 4 138 1 | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.7173 | 118.04 | 515152 BROWNTP4 138 515155 BODLE 4 138 1 | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.7173 | 113.72 | 515152 BROWNTP4 138 515155 BODLE 4 138 1 | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 1 | 103.28 | P12:138:OKGE:BKRBKR261:::: | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.72491 | 102.17 | P23:345:AEPW:PITTSBURG CB 3429A NBTB | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.72491 | 102.17 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 1 | 102.9 | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 1 | 102.32 | P12:138:OKGE:BKRBKR261:::: | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 1 | 102.25 | P12:138:OKGE:BKRBKR261:::: | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 1 | 101.92 | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 1 | 101.83 | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.71951 | 101.15 | P23:345:AEPW:PITTSBURG CB 3425A NBTB | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 | 04ALL | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 |  | 143 | 0.71951 | 101.15 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT | Cumulative Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 143 | 143 | 1 | 102.85 | P12:138:OKGE:BKRBKR261:::: | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 143 | 143 | 1 | 102.49 | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 143 | 143 | 0.71532 | 101.52 | 515152 BROWNTP4 138 515155 BODLE 4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 143 | 143 | 1 | 102.11 | P12:138:OKGE:BKRBKR261:::: | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 143 | 143 | 1 | 101.97 | P12:138:OKGE:BKRBKR261:::: | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 143 | 143 | 1 | 101.71 | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-232 | FROM->TO | 505602 S BROWN4 138 515157 BROWN 4 138 1 | 143 | 143 | 1 | 101.58 | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | TDF Impact | SPA Brown to Brown 138 kV Equipment Upgrade
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 113.25 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 113.25 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 113.25 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 113.25 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 113.25 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 113.25 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 113.25 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 113.25 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 113.25 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 113.25 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.27 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.27 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.26 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.26 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.26 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.26 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.24 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.24 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.27 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.27 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.24 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.24 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.27 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.26 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.26 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.24 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.27 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.26 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.26 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.24 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06367 | 100 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06367 | 100 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06367 | 100 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06367 | 100 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.27 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.26 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.26 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.24 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.27 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06111 | 109.24 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.27 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.24 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06367 | 100 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.06367 | 100 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.27 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0556 | 109.24 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05793 | 100 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05793 | 100 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05793 | 100 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05793 | 100 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 121.64 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 121.64 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 121.64 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 121.64 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 121.64 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 121.64 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 121.64 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 121.64 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 121.64 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 121.64 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 110.09 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 110.09 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 110.09 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 110.09 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 110.09 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 110.09 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 110.09 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 110.09 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 110.09 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 110.09 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05783 | 117.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.16 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.16 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.16 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.16 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 105.92 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 105.92 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06072 | 107.25 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06072 | 107.25 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06084 | 107.21 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06084 | 107.21 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06084 | 107.21 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06084 | 107.21 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05231 | 117.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06073 | 107 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06073 | 107 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 105.92 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 105.92 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 102.92 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 102.92 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.16 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.16 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 105.92 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 107.26 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06072 | 107.25 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06084 | 107.21 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06084 | 107.21 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06073 | 107 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.16 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.16 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 105.92 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.16 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.16 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 105.92 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 107.26 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 107.26 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 107.26 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09918 | 107.25 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0993 | 107.21 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0993 | 107.21 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09919 | 107 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06045 | 105.92 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.06068 | 102.92 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 107.26 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 107.26 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 107.26 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09918 | 107.25 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0993 | 107.21 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0993 | 107.21 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09919 | 107 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 105.92 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 102.92 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 106.17 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05471 | 105.92 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.09914 | 102.92 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-178 | TO->FROM | 514898 CIMARON4 138 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.03754 | 103.54 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-233 | TO->FROM | 514898 CIMARON4 138 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.06131 | 103.54 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-150 | TO->FROM | 514898 CIMARON4 138 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.06131 | 103.54 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-164 | TO->FROM | 514898 CIMARON4 138 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.03754 | 103.54 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-178 | FROM->TO | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.03754 | 107.46 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-233 | FROM->TO | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.06131 | 107.46 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-150 | FROM->TO | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.06131 | 107.46 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-164 | FROM->TO | 514901 CIMARON7 345 997999 CIMARON1 _1 138 1 | 478 | 478 | 0.03754 | 107.46 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-230 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 | 268 |  | 0.04888 | 103.75 | System Intact | TDF Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 | 268 |  | 0.05846 | 103.75 | System Intact | TDF Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 | 268 |  | 0.05846 | 103.75 | System Intact | TDF Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 | 268 |  | 0.05846 | 103.75 | System Intact | TDF Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 | 268 |  | 0.05846 | 103.75 | System Intact | TDF Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-230 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0549 | 109.45 | 514907 ARCADIA4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-230 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06786 | 109.01 | P12:138:OKGE:BKRBKR109:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-230 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0549 | 108.77 | P12:138:OKGE:BKRBKR109_1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-230 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0549 | 108.21 | 514842 CHTWOOD4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-230 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0549 | 107.89 | 514842 CHTWOOD4 138 515480 JONESSB4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-230 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06822 | 100.36 | P12:138:OKGE:BKRBKR109_2 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 109.45 | 514907 ARCADIA4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.10234 | 112.48 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.07168 | 109.01 | P12:138:OKGE:BKRBKR109:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.77 | P12:138:OKGE:BKRBKR109_1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.21 | 514842 CHTWOOD4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 107.89 | 514842 CHTWOOD4 138 515480 JONESSB4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 105.02 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.9 | P12:138:OKGE:BKRBKR106:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.82 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 109.45 | 514907 ARCADIA4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.10234 | 112.48 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 103.97 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.07168 | 109.01 | P12:138:OKGE:BKRBKR109:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.77 | P12:138:OKGE:BKRBKR109_1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.21 | 514842 CHTWOOD4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 107.89 | 514842 CHTWOOD4 138 515480 JONESSB4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 109.45 | 514907 ARCADIA4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06663 | 100.36 | P12:138:OKGE:BKRBKR109_2 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.10234 | 112.48 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 105.02 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.07168 | 109.01 | P12:138:OKGE:BKRBKR109:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.77 | P12:138:OKGE:BKRBKR109_1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.9 | P12:138:OKGE:BKRBKR106:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.82 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.21 | 514842 CHTWOOD4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 107.89 | 514842 CHTWOOD4 138 515480 JONESSB4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 103.97 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 105.02 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.9 | P12:138:OKGE:BKRBKR106:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.82 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06663 | 100.36 | P12:138:OKGE:BKRBKR109_2 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 103.97 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 109.45 | 514907 ARCADIA4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.10234 | 112.48 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.07168 | 109.01 | P12:138:OKGE:BKRBKR109:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.77 | P12:138:OKGE:BKRBKR109_1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 108.21 | 514842 CHTWOOD4 138 515465 LGARBER4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.0705 | 107.89 | 514842 CHTWOOD4 138 515480 JONESSB4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06663 | 100.36 | P12:138:OKGE:BKRBKR109_2 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 105.02 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.9 | P12:138:OKGE:BKRBKR106:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 104.82 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06777 | 103.97 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514906 JNSKAMO4 138 514907 ARCADIA4 138 1 |  | 308 | 0.06663 | 100.36 | P12:138:OKGE:BKRBKR109_2 | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 104.62 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 104.5 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 102.72 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-133 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 100.92 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 104.62 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 104.5 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 102.72 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 104.62 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-134 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 100.92 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 104.5 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 102.72 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-137 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 100.92 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 104.62 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 104.5 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 102.72 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-132 | FROM->TO | 514907 ARCADIA4 138 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 100.92 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 106.38 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 104.42 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-133 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 106.22 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-133 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 102.18 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 106.38 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 104.42 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-134 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 106.22 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 106.38 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-134 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 102.18 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 104.42 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-137 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 106.22 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-137 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 102.18 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.10096 | 106.38 | P13:138-345:OKGE:BKRBKR_3W023:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.09899 | 104.42 | P13:138-345:OKGE:BKRBKR_3W024:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 23SP | GEN-2017-132 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14209 | 106.22 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 | 04ALL | 1 | 26SP | GEN-2017-132 | FROM->TO | 514908 ARCADIA7 345 3WXFMR ARCADIA4 _1 138 1 |  | 448 | 0.14137 | 102.18 | P12:345:OKGE:BKRBKR143:::: | Cumulative Impact | Matthewson - Redbud 345 kV New Line
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-117 | FROM->TO | 514946 MIDWEST4 138 520917 FRNKLNS4 138 1 | 268 | 287 | 0.05402 | 104.46 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Park Community - Sunshine 138 kV
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-117 | FROM->TO | 514946 MIDWEST4 138 520917 FRNKLNS4 138 1 | 268 | 287 | 0.05402 | 104.46 | PROXY_P4_345kV_POI_514801_12 | TDF Impact | Multi - Park Community - Sunshine 138 kV
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-117 | FROM->TO | 514946 MIDWEST4 138 520917 FRNKLNS4 138 1 | 268 | 287 | 0.05402 | 104.19 | PROXY_P4_345kV_POI_514801_6 | TDF Impact | Multi - Park Community - Sunshine 138 kV
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-117 | FROM->TO | 514946 MIDWEST4 138 520917 FRNKLNS4 138 1 | 268 | 287 | 0.05402 | 103.97 | PROXY_P4_345kV_POI_514801_9 | TDF Impact | Multi - Park Community - Sunshine 138 kV
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-117 | FROM->TO | 514946 MIDWEST4 138 520917 FRNKLNS4 138 1 | 268 | 287 | 0.05402 | 100.31 | PROXY_P4_345kV_POI_514801_13 | TDF Impact | Multi - Park Community - Sunshine 138 kV
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26L | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03585 | 109.55 | System Intact | TDF Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 123.2 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 123.2 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.55 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 123.2 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 123.2 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.55 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 123.2 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 123.2 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.55 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 123.2 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 123.2 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.55 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 123.2 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 123.2 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.55 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0993 | 119.98 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0993 | 119.98 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09919 | 119.74 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09918 | 120.03 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 120.04 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 120.04 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 120.04 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 136.12 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 136.12 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06084 | 119.98 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06084 | 119.98 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06073 | 119.74 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06072 | 120.03 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 136.12 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 136.12 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06084 | 119.98 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06084 | 119.98 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06073 | 119.74 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06072 | 120.03 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 136.12 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 136.12 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06084 | 119.98 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06084 | 119.98 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06073 | 119.74 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06072 | 120.03 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 120.04 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 136.12 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 136.12 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05783 | 131.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0993 | 119.98 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0993 | 119.98 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09919 | 119.74 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09918 | 120.03 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 120.04 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 120.04 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 120.04 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 136.12 | P43:345:SPS:TUCO:NR05:SLG:EHV: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 136.12 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.53 | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.51 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05231 | 131.51 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 115.18 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 115.18 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 115.18 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.55 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.55 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 109.21 | PROXY_P4_345kV_POI_514801_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 109.21 | PROXY_P4_345kV_POI_514801_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 115.18 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06385 | 106.95 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06385 | 106.95 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 115.18 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06398 | 106.72 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06398 | 106.72 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06398 | 106.72 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06398 | 106.72 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06385 | 106.59 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06385 | 106.59 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-172 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 101.77 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-173 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 101.77 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06045 | 118.55 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06068 | 109.21 | PROXY_P4_345kV_POI_514801_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 106.98 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06385 | 106.95 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06398 | 106.72 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06398 | 106.72 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06385 | 106.59 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.55 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 109.21 | PROXY_P4_345kV_POI_514801_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.81 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05471 | 118.55 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.09914 | 109.21 | PROXY_P4_345kV_POI_514801_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 106.98 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 106.98 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 106.98 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10293 | 106.95 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10306 | 106.72 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10306 | 106.72 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-171 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.06381 | 101.77 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10293 | 106.59 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 106.98 | PROXY_P4_345kV_POI_514801_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 106.98 | P12:345:OKGE:BKRBKR24:::: | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 106.98 | PROXY_P4_345kV_POI_514901_4 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10293 | 106.95 | PROXY_P4_345kV_POI_514901_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10306 | 106.72 | PROXY_P4_345kV_POI_514901_2 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10306 | 106.72 | PROXY_P4_345kV_POI_514901_1 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10293 | 106.59 | PROXY_P4_345kV_POI_514901_3 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 101.77 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 04ALL | 1 | 23SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.10289 | 101.77 | PROXY_P4_345kV_POI_514801_0 | Cumulative Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03377 | 100.28 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-233 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03377 | 100.28 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03377 | 100.28 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-150 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03377 | 100.28 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2017-002 | 03ALL | 1 | 26L | GEN-2017-119 | FROM->TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.6859 | 107.59 | P23:345:WERE:SUMM_345-218:: | Cumulative Impact | Partly rebuild the Elm Creek to North Manhattan 230 kV line
Thermal | DISIS-2017-002 | 03ALL | 1 | 26L | GEN-2017-119 | FROM->TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.6859 | 107.59 | P23:345:WERE:SUMM-345-218:::EHV: | Cumulative Impact | Partly rebuild the Elm Creek to North Manhattan 230 kV line
Thermal | DISIS-2017-002 | 03ALL | 1 | 26L | GEN-2017-119 | FROM->TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.69104 | 106 | P12:345:WERE:SUMM-ELMC-345:::EHV: | Cumulative Impact | Partly rebuild the Elm Creek to North Manhattan 230 kV line
Thermal | DISIS-2017-002 | 03ALL | 1 | 26L | GEN-2017-119 | FROM->TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.69104 | 106 | P12:345:WERE:SUMM-ELMC_345:: | Cumulative Impact | Partly rebuild the Elm Creek to North Manhattan 230 kV line
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 311 | 334 | 0.6675 | 112.58 | System Intact | TDF impact | Terminal upgrades at Clinton (owned by AECI)
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05359 | 105.62 | 541225 PHILL 5 161 541313 HARRIS 161 1 | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05359 | 105.22 | P12:161:GMO:PLEASANTHILL-HARRISRD-GREENWOOD | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05359 | 105.22 | P12:161:GMO:PLEASANTHILL-HARRISRD-GREENWOOD_1 | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05359 | 105.22 | P12:161:GMO:PLEASANTHILL-HARRISRD-GREENWOOD:::HV: | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05369 | 104.96 | 541225 PHILL 5 161 541313 HARRIS 161 1 | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05359 | 104.58 | 541218 GRNWD 5 161 541313 HARRIS 161 1 | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05369 | 104.55 | P12:161:GMO:PLEASANTHILL-HARRISRD-GREENWOOD_1 | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05369 | 104.55 | P12:161:GMO:PLEASANTHILL-HARRISRD-GREENWOOD | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05369 | 104.55 | P12:161:GMO:PLEASANTHILL-HARRISRD-GREENWOOD:::HV: | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 541225 PHILL 5 161 541243 LKWINBG5 161 1 | 334 | 334 | 0.05369 | 103.91 | 541218 GRNWD 5 161 541313 HARRIS 161 1 | TDF Impact | Pleasant Hill to Lake Winnebago 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07733 | 125.02 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07733 | 125.02 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.079 | 111.89 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.079 | 111.89 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.11641 | 111.86 | P23:345:KCPL:NASHUA-R9-11:::EHV: | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.11641 | 111.86 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.11641 | 111.86 | P23:345:KCPL:NASHUA-R9-11:::EHV: | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.11641 | 111.86 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05907 | 103.33 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05907 | 103.33 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07948 | 104.44 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07948 | 104.44 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05548 | 132.22 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05548 | 132.22 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05548 | 135.37 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05548 | 135.37 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05548 | 124.8 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05548 | 124.8 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.0569 | 123.26 | P12:345:WERE:87TH-STRA_345:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.0569 | 123.26 | P12:345:WERE:87TH-STRA_345:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.0569 | 123.26 | P12:345:WERE:87TH-STRA-345:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.0569 | 123.26 | P12:345:WERE:87TH-STRA-345:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05714 | 123.12 | P23:345:WERE:87TH-345-BKRS:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05714 | 123.12 | P23:345:WERE:87TH-345-BKRS:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.0573 | 124.1 | PROXY_P4_345kV_POI_532772_6 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.0573 | 124.1 | PROXY_P4_345kV_POI_532772_6 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | P23:345:WERE:STRA_345-99:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | P23:345:WERE:STRA_345-99:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | P23:345:WERE:STRA-345-99:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | P23:345:WERE:STRA-345-99:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | P23:345:WERE:STRA-345-99::WERE VERSION:EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | P23:345:WERE:STRA-345-99::WERE VERSION:EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | PROXY_P4_345kV_POI_532772_5 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05737 | 124.21 | PROXY_P4_345kV_POI_532772_5 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05891 | 122.34 | P23:345:WERE:STRA_345-100:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05891 | 122.34 | P23:345:WERE:STRA_345-100:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05891 | 122.34 | P23:345:WERE:STRA-345-100:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05891 | 122.34 | P23:345:WERE:STRA-345-100:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05891 | 122.34 | PROXY_P4_345kV_POI_532772_0 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05891 | 122.34 | PROXY_P4_345kV_POI_532772_0 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06204 | 131.51 | 543028 NASHUA-5 161 543029 SHOLCRK5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06204 | 131.51 | 543028 NASHUA-5 161 543029 SHOLCRK5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06285 | 134.32 | PROXY_P4_345kV_POI_532772_9 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06285 | 134.32 | PROXY_P4_345kV_POI_532772_9 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 128.87 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 128.87 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 131.95 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 131.95 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07271 | 131.87 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07271 | 131.87 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07376 | 127.35 | 543028 NASHUA-5 161 543029 SHOLCRK5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07376 | 127.35 | 543028 NASHUA-5 161 543029 SHOLCRK5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07618 | 127.84 | PROXY_P4_345kV_POI_532772_9 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07618 | 127.84 | PROXY_P4_345kV_POI_532772_9 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.09114 | 151.24 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.09114 | 151.24 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.10467 | 138.74 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.10467 | 138.74 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.08116 | 128.73 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.08116 | 128.73 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06913 | 124.45 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06913 | 124.45 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06913 | 121.19 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06913 | 121.19 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 119.27 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 119.27 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.10582 | 129.23 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.10582 | 129.23 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07541 | 120.31 | 543028 NASHUA-5 161 543029 SHOLCRK5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07541 | 120.31 | 543028 NASHUA-5 161 543029 SHOLCRK5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06162 | 116.59 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06162 | 116.59 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | P23:345:WERE:STRA_345-99:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | P23:345:WERE:STRA_345-99:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | P23:345:WERE:STRA-345-99:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | P23:345:WERE:STRA-345-99:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | P23:345:WERE:STRA-345-99::WERE VERSION:EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | P23:345:WERE:STRA-345-99::WERE VERSION:EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | PROXY_P4_345kV_POI_532772_5 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06853 | 118.12 | PROXY_P4_345kV_POI_532772_5 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06845 | 118.02 | PROXY_P4_345kV_POI_532772_6 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06845 | 118.02 | PROXY_P4_345kV_POI_532772_6 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14013 | 136.27 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14013 | 136.27 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14013 | 136.27 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14013 | 136.27 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.08198 | 120.97 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.08198 | 120.97 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06789 | 117.26 | P12:345:WERE:87TH-STRA_345:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06789 | 117.26 | P12:345:WERE:87TH-STRA_345:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06789 | 117.26 | P12:345:WERE:87TH-STRA-345:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06789 | 117.26 | P12:345:WERE:87TH-STRA-345:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 116.72 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06767 | 116.72 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06789 | 116.7 | PROXY_P4_345kV_POI_532772_4 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06789 | 116.7 | PROXY_P4_345kV_POI_532772_4 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06819 | 116.74 | P23:345:WERE:87TH-345-BKRS:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06819 | 116.74 | P23:345:WERE:87TH-345-BKRS:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07655 | 116.5 | PROXY_P4_345kV_POI_532772_9 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.07655 | 116.5 | PROXY_P4_345kV_POI_532772_9 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06913 | 111.75 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06913 | 111.75 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.31 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.31 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.31 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1:::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.31 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1:::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.3 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.3 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.3 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06289 | 110.3 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU::: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | P23:345:WERE:STRA_345-99:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | P23:345:WERE:STRA_345-99:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | P23:345:WERE:STRA-345-99:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | P23:345:WERE:STRA-345-99:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | P23:345:WERE:STRA-345-99::WERE VERSION:EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | P23:345:WERE:STRA-345-99::WERE VERSION:EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | PROXY_P4_345kV_POI_532772_5 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06943 | 110.31 | PROXY_P4_345kV_POI_532772_5 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06935 | 110.24 | PROXY_P4_345kV_POI_532772_6 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06935 | 110.24 | PROXY_P4_345kV_POI_532772_6 | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14971 | 121.18 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14971 | 121.18 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14971 | 121.18 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.14971 | 121.18 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06883 | 109.7 | P12:345:WERE:87TH-STRA_345:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06883 | 109.7 | P12:345:WERE:87TH-STRA_345:: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06883 | 109.7 | P12:345:WERE:87TH-STRA-345:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06883 | 109.7 | P12:345:WERE:87TH-STRA-345:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05252 | 106.96 | System Intact | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.05252 | 106.96 | System Intact | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06162 | 104.51 | System Intact | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.06162 | 104.51 | System Intact | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.15107 | 110.16 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.15107 | 110.16 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-183 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.15107 | 110.16 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-184 | FROM->TO | 541230 RNRIDGE5 161 543028 NASHUA-5 161 1 | 223 | 223 | 0.15107 | 110.16 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 293 | 334 | 1 | 127.79 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 293 | 334 | 1 | 126.55 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
Thermal | DISIS-2017-002 | 03ALL | 1 | 23SP | GEN-2017-108 | FROM->TO | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 293 | 334 | 1 | 127.79 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal Upgrades at Archie 161kV
Thermal | DISIS-2017-002 | 03ALL | 1 | 26SP | GEN-2017-108 | FROM->TO | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 293 | 334 | 1 | 126.55 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Cumulative Impact | Terminal Upgrades at Archie 161kV
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-108 | FROM->TO | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 293 | 334 | 1 | 126.13 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-108 | FROM->TO | 542969 STILWEL5 161 761278 G17-108-TAP 161 1 | 293 | 334 | 1 | 126.06 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-196 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06067 | 103.69 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-196 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06283 | 103.52 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-196 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06068 | 100.84 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-196 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06282 | 100.77 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-195 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06067 | 103.69 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-195 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06283 | 103.52 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 23SP | GEN-2017-195 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06068 | 100.84 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 00NR | 1 | 26SP | GEN-2017-195 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06282 | 100.77 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-196 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06321 | 102.26 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-196 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.0607 | 100.71 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-195 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.06321 | 102.26 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 CF | 00NR | 1 | 23SP | GEN-2017-195 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 0.0607 | 100.71 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | TDF Impact | Craig to Lenexa 161 kV line 1 Rating Update
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-183 | FROM->TO | 543028 NASHUA-5 161 997413 NASHUA11 _1 161 11 | 650 | 715 | 0.21495 | 100.15 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Install a second 650 MVA TX at Nashua
Thermal | DISIS-2017-002 | 03ALL | 1 | 26WP | GEN-2017-184 | FROM->TO | 543028 NASHUA-5 161 997413 NASHUA11 _1 161 11 | 650 | 715 | 0.21495 | 100.15 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | Install a second 650 MVA TX at Nashua
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-214 | FROM->TO | 603023 MALLARD7 115 655655 E.RUTHVL-CP7 115 1 | 120 | 120 | 0.03295 | 110.1 | 655657 SW.MINOT-CP7 115 659155 LOGAN___-BE7 115 1 | TDF Impact | Millard to E.Ruth 115 kV line 1 Rating Update
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-215 | FROM->TO | 603023 MALLARD7 115 655655 E.RUTHVL-CP7 115 1 | 120 | 120 | 0.03295 | 110.1 | 655657 SW.MINOT-CP7 115 659155 LOGAN___-BE7 115 1 | TDF Impact | Millard to E.Ruth 115 kV line 1 Rating Update
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.11523 | 113.94 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1172 | 111.14 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1247 | 109.84 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12754 | 109.7 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.10864 | 108.2 | P11:014:NPPD:SHELDN2G:2:141::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.06661 | 113.94 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 108.23 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 107.93 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 107.93 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12644 | 106.65 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.11523 | 113.94 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05528 | 111.14 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.14585 | 102.99 | P42:345:NPPD:BKR-RW-3302::::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1172 | 111.14 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05021 | 109.84 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.04498 | 109.7 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.10864 | 100.21 | System Intact | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.06095 | 108.2 | P11:014:NPPD:SHELDN2G:2:141::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05147 | 108.23 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1247 | 109.84 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05147 | 107.93 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05147 | 107.93 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12754 | 109.7 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.10864 | 108.2 | P11:014:NPPD:SHELDN2G:2:141::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05145 | 106.65 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 108.23 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 107.93 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 107.93 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12644 | 106.65 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.04479 | 102.99 | P42:345:NPPD:BKR-RW-3302::::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.06095 | 100.21 | System Intact | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.14585 | 102.99 | P42:345:NPPD:BKR-RW-3302::::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.10864 | 100.21 | System Intact | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12291 | 110.48 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12324 | 109.16 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.13175 | 107.4 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1298 | 106.77 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.10013 | 105.01 | P11:014:NPPD:SHELDN1G:1:128::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1312 | 103.33 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1312 | 103.04 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1312 | 103.04 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.07429 | 110.48 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.06132 | 109.16 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12291 | 110.48 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.04919 | 107.4 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12324 | 109.16 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.05531 | 106.77 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.05244 | 105.01 | P11:014:NPPD:SHELDN1G:1:128::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.13175 | 107.4 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1298 | 106.77 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.10013 | 105.01 | P11:014:NPPD:SHELDN1G:1:128::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.05684 | 103.33 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.05684 | 103.04 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.05684 | 103.04 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1312 | 103.33 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1312 | 103.04 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1312 | 103.04 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-234 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.05683 | 114.05 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16169 | 114.05 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-234 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.0618 | 116.89 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-182 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16666 | 116.89 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.06863 | 114.05 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-144 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.0736 | 116.89 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16169 | 114.05 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-181 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16666 | 116.89 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-210 | FROM->TO | 640277 MOORE 3 345 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.12274 | 116.89 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.11523 | 106.49 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1172 | 104.01 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1247 | 103.05 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12754 | 102.96 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 101.65 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 101.42 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 101.42 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.10864 | 100.97 | P11:014:NPPD:SHELDN2G:2:141::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12644 | 100.2 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.06661 | 106.49 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05528 | 104.01 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.11523 | 106.49 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05021 | 103.05 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.04498 | 102.96 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05147 | 101.65 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05147 | 101.42 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05147 | 101.42 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.06095 | 100.97 | P11:014:NPPD:SHELDN2G:2:141::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1172 | 104.01 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.05145 | 100.2 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.1247 | 103.05 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12754 | 102.96 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 101.65 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 101.42 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12583 | 101.42 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.10864 | 100.97 | P11:014:NPPD:SHELDN2G:2:141::: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26WP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997023 MOORE T1 _1 115 1 | 336 | 336 | 0.12644 | 100.2 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12291 | 103.86 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12324 | 102.68 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.13175 | 101.3 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-182 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1298 | 100.73 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.07429 | 103.86 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.06132 | 102.68 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.04919 | 101.3 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-201 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.05531 | 100.73 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12291 | 103.86 | P13:115-345:LES:T141::NW68&HOLDREGE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.12324 | 102.68 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.13175 | 101.3 | P12:345:LES:L3516::NW68&HOLDREGE.MOORE.CKT1 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 00NR | 1 | 26SP | GEN-2017-181 | FROM->TO | 640278 SHELDON7 115 997025 MOORE T1 _1 115 1 | 336 | 336 | 0.1298 | 100.73 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-234 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.05683 | 110.28 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-234 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.0618 | 113.25 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-182 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16169 | 110.28 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-182 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16666 | 113.25 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-144 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.06863 | 110.28 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-144 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.0736 | 113.25 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26L | GEN-2017-181 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16169 | 110.28 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-181 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.16666 | 113.25 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 | 02ALL | 1 | 26WP | GEN-2017-210 | TO->FROM | 640278 SHELDON7 115 997027 MOORE T1 _1 115 1 | 336 | 336 | 0.12274 | 113.25 | P42:345:NPPD:BKR-RW-3302::::: | Cumulative Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 1 | 133.98 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 1 | 133.98 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 1 | 133.98 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 1 | 129.45 | PROXY_P4_345kV_POI_652532_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 121.11 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 121.11 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 121.11 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 121.11 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 121.11 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 120.3 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 118.55 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 118.55 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 118.55 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 118.55 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 118.55 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 118.5 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 114.62 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 114.62 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 114.62 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 113.65 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 113.65 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 113.65 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 110.78 | PROXY_P4_345kV_POI_652532_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 1 | 110.29 | PROXY_P4_345kV_POI_652532_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65438 | 104.26 | PROXY_P4_345kV_POI_640525_2 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65327 | 102.48 | PROXY_P4_345kV_POI_640525_3 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65351 | 101.98 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65438 | 101.9 | 640525 TOBIAS 3 345 761292 GEN-2017-181 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65438 | 101.52 | P11:345:WERE:WOLFU1_GEN:: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65438 | 101.52 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65446 | 101.45 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65446 | 101.45 | P23:345:WERE:WOLF_345-50:: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65788 | 101.32 | P12:230:UMZB:# 111 #:: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON:HV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.65863 | 101.23 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 652506 FTTHOMP3 345 996799 FT2 KU1B 230 1 | 250 | 313 | 0.42661 | 101.88 | PROXY_P4_345kV_POI_640510_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 652506 FTTHOMP3 345 996800 FT2 KU1A 230 1 | 250 | 313 | 0.42661 | 101.88 | PROXY_P4_345kV_POI_640510_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 652507 FTTHOMP4 230 996799 FT2 KU1B 230 1 | 250 | 313 | 0.42661 | 102.64 | PROXY_P4_345kV_POI_640510_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 652507 FTTHOMP4 230 996800 FT2 KU1A 230 1 | 250 | 313 | 0.42661 | 102.64 | PROXY_P4_345kV_POI_640510_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18818 | 121.44 | System Intact | TDF Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18849 | 115.96 | System Intact | TDF Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18839 | 113.67 | System Intact | TDF Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24211 | 137.61 | P12:161:WAPA:DENISON-EXIRA:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24211 | 137.61 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24211 | 137.5 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24211 | 137.5 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24222 | 137.28 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24222 | 137.28 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24259 | 137.11 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24259 | 137.11 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.2427 | 136.76 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.2427 | 136.76 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24314 | 136.12 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19069 | 122.02 | P23:345:MEC:RAUN 0270 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18154 | 120.13 | P13:161-69:MEC:AUTO-SINGLE:MONONA5:MONONA8:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18205 | 119.51 | P13:069:MEC:MONONA AC | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18331 | 119.17 | 635236 SALIX 8 69.0 659923 K10225A_-NI8 69.0 1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18331 | 119.15 | 659923 K10225A_-NI8 69.0 659981 K127WHTG-NI8 69.0 1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19023 | 119.27 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19023 | 119.27 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19023 | 119.27 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19023 | 119.27 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19023 | 119.27 | P22:345:OPPD:S3451-RAUN:::EHV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19023 | 119.27 | P23:345:OPPD:S3451-RAUN:::EHV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18331 | 118.12 | 659981 K127WHTG-NI8 69.0 659982 K118LSCR-NI8 69.0 1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18818 | 117.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24246 | 121.95 | P12:161:WAPA:DENISON-EXIRA:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24246 | 121.95 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24246 | 121.85 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24246 | 121.85 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24102 | 121.49 | P12:161:WAPA:DENISON-EXIRA:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24102 | 121.49 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24257 | 121.49 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24257 | 121.49 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24102 | 121.35 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24102 | 121.35 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24112 | 121.34 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24112 | 121.34 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18119 | 115.89 | P12:161:MEC:AUTO-SINGLE:QUICK5:OVRLND5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18119 | 115.89 | P21:161:MEC:AUTO-SINGLE:QUICK5:OVRLND5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24259 | 121.25 | P12:161:WAPA:DENISON-EXIRA:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24259 | 121.25 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24347 | 120.07 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18057 | 114.46 | P13:069:MEC:AVOCA 8T1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.24359 | 119.43 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18119 | 113.93 | P12:161:MEC:AUTO-SINGLE:QUICK5:AVOCA5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18119 | 113.93 | P21:161:MEC:AUTO-SINGLE:QUICK5:AVOCA5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.2421 | 118.61 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19112 | 113.83 | P23:345:MEC:RAUN 0270 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19709 | 114.01 | P12:161:WAPA-ALTW:AUTO-SINGLE:ANTATP5:ANITA5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19709 | 114.01 | P21:161:WAPA-ALTW:AUTO-SINGLE:ANTATP5:ANITA5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19713 | 113.98 | P12:161:WAUW:# 3102 #: TI IN MT. TI-TT-SH2 & TT-RY-HV | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19713 | 113.98 | P13:161-69:CIPCO:ANITA T1:IA-SW | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19713 | 113.95 | P12:161:WAUW:# 3088 #: HV IN MT. HV-RY-TT LINE FAULT | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18111 | 112.35 | P12:161:MEC:AUTO-SINGLE:QUICK5:OVRLND5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18111 | 112.35 | P21:161:MEC:AUTO-SINGLE:QUICK5:OVRLND5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18849 | 112.84 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19098 | 112.5 | P23:345:MEC:RAUN 0270 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18355 | 111.21 | 635236 SALIX 8 69.0 659923 K10225A_-NI8 69.0 1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18049 | 111.01 | P13:069:MEC:AVOCA 8T1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18355 | 111.19 | 659923 K10225A_-NI8 69.0 659981 K127WHTG-NI8 69.0 1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.21284 | 112.71 | 656247 TEMPLTON8 69.0 656267 MANNINGTAP 8 69.0 1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18176 | 110.66 | P13:161-69:MEC:AUTO-SINGLE:MONONA5:MONONA8:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18839 | 110.98 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18111 | 110.4 | P12:161:MEC:AUTO-SINGLE:QUICK5:AVOCA5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18111 | 110.4 | P21:161:MEC:AUTO-SINGLE:QUICK5:AVOCA5:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18829 | 110.24 | P23:345:MEC:CBEC 905 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.18839 | 110.1 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26SP | GEN-2017-222 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 72 | 80 | 0.19051 | 109.8 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | Cumulative Impact | Denison to Boyer 69kV Terminal Upgrade
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-175 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 120 | 120 | 0.12409 | 108.27 | 652526 UTICAJC4 230 655484 RASMUSN-ER4 230 1 | Cumulative Impact | Utica to Napa 115kV Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-175 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 120 | 120 | 0.12409 | 105.54 | 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 | Cumulative Impact | Utica to Napa 115kV Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26L | GEN-2017-175 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 120 | 120 | 0.14876 | 104.2 | 652398 VFODNES4 230 762237 G17-175TAP 230 1 | Cumulative Impact | Utica to Napa 115kV Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-175 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 120 | 120 | 0.08467 | 101.94 | 652510 FTRANDL7 115 655490 WHTSWAN-ER7 115 1 | Cumulative Impact | Utica to Napa 115kV Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-175 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 120 | 120 | 0.08467 | 100.6 | P12:115:UMZW:# 5566 #:: FR-WSW IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-WSW).:HV: | Cumulative Impact | Utica to Napa 115kV Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-175 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 120 | 120 | 0.08467 | 100.6 | P12:115:UMZ:# 5566 #: IN . PROPER N-1 (LINE) FOR 655490-652510-1 | Cumulative Impact | Utica to Napa 115kV Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 23SP | GEN-2017-175 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 120 | 120 | 0.08467 | 100.52 | 652525 TYNDALL7 115 655490 WHTSWAN-ER7 115 1 | Cumulative Impact | Utica to Napa 115kV Rating Update
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 1 | 134 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 1 | 134 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 1 | 134 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 1 | 128.98 | PROXY_P4_345kV_POI_652532_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 119.93 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 119.93 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 119.93 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 119.93 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 119.93 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 119.21 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 117.53 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 117.53 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 117.53 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 117.53 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 117.53 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 117.45 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 114.17 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 114.17 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 114.17 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 113.24 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 113.24 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 113.24 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 109.92 | PROXY_P4_345kV_POI_652532_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 23SP | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 842 | 842 | 1 | 109.4 | PROXY_P4_345kV_POI_652532_2 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65438 | 103.85 | PROXY_P4_345kV_POI_640525_2 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65327 | 102.23 | PROXY_P4_345kV_POI_640525_3 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65351 | 101.92 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65438 | 101.52 | 640525 TOBIAS 3 345 761292 GEN-2017-181 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65438 | 101.28 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65438 | 101.28 | P11:345:WERE:WOLFU1_GEN:: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65788 | 101.28 | P12:230:UMZB:# 111 #:: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON:HV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65446 | 101.21 | P23:345:WERE:WOLF_345-50:: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65446 | 101.21 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26L | GEN-2017-144 | FROM->TO | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.65756 | 100.94 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.22 | P12:115:UMZ:# 5503 #: PROPER N-1 (LINE) FOR 603023-652440-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.22 | P12:115:UMZ:# 5503 #: PROPER N-1 (LINE) FOR 603023-652440-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.19 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.19 | P12:115:UMZW:# 5553 #:: GA-MX IN ND. FAULT FOR TRANSMISSION CIRCUIT (GA-MX).:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.19 | P12:115:UMZW:# 156 #:: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.19 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.19 | P12:115:UMZW:# 5553 #:: GA-MX IN ND. FAULT FOR TRANSMISSION CIRCUIT (GA-MX).:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.19 | P12:115:UMZW:# 156 #:: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 100.93 | P21:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 100.93 | P12:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 100.93 | P21:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | FROM->TO | 659108 LOGAN___-BE4 230 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 100.93 | P12:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.99 | P12:115:UMZ:# 5503 #: PROPER N-1 (LINE) FOR 603023-652440-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.99 | P12:115:UMZ:# 5503 #: PROPER N-1 (LINE) FOR 603023-652440-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.96 | P12:115:UMZW:# 156 #:: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.96 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.96 | P12:115:UMZW:# 5553 #:: GA-MX IN ND. FAULT FOR TRANSMISSION CIRCUIT (GA-MX).:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.96 | P12:115:UMZW:# 156 #:: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.96 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27827 | 101.96 | P12:115:UMZW:# 5553 #:: GA-MX IN ND. FAULT FOR TRANSMISSION CIRCUIT (GA-MX).:HV: | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 101.62 | P21:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-214 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 101.62 | P12:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 101.62 | P21:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Thermal | DISIS-2017-002 | 01ALL | 1 | 26WP | GEN-2017-215 | TO->FROM | 659155 LOGAN___-BE7 115 996721 KW1A _1 115 1 | 200 | 203 | 0.27829 | 101.62 | P12:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1 | Cumulative Impact | Logan 230-115 kV Transformer Rating Update
Non-Converge | DISIS-2017-002 | 00NR | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 00NR | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 00NR | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 01ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 01ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 01ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 01ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 01NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 02ALL | 0 | 23SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66557 |  | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 | 02ALL | 0 | 23SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66557 |  | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 | 02ALL | 0 | 23SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66557 |  | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 | 02ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 02ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 02ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 02NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 03NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.04481 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.04481 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.04481 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.04481 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.04481 |  | P43:345:SPS:TUCO:NR05:SLG:EHV: | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.24579 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.24579 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.04481 |  | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-149 | " | Non-Converge |  |  | 0.04481 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.04481 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.04481 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.04481 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.04481 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.04481 |  | P43:345:SPS:TUCO:NR05:SLG:EHV: | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.24579 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.24579 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.04481 |  | 511456 O.K.U.-7 345 762216 G17-151TAP 345 1 | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-154 | " | Non-Converge |  |  | 0.04481 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-233 | " | Non-Converge |  |  | 0.05612 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26L | GEN-2017-233 | " | Non-Converge |  |  | 0.05612 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Build Tolk to Potter County 345 kV Circuit 1
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 04ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 04NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 05ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 05ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 05ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 05ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 05NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 23SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66557 |  | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 23SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66557 |  | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 23SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66557 |  | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66549 |  | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66549 |  | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26SP | GEN-2017-144 | " | Non-Converge |  |  | 0.66549 |  | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26WP | GEN-2017-144 | " | Non-Converge |  |  | 0.66246 |  | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26WP | GEN-2017-144 | " | Non-Converge |  |  | 0.66246 |  | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26WP | GEN-2017-144 | " | Non-Converge |  |  | 0.66246 |  | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.34562 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-181 | " | Non-Converge |  |  | 0.04863 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-182 | " | Non-Converge |  |  | 0.04863 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-234 | " | Non-Converge |  |  | 0.047 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.34562 |  | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-181 | " | Non-Converge |  |  | 0.04863 |  | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-182 | " | Non-Converge |  |  | 0.04863 |  | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-234 | " | Non-Converge |  |  | 0.047 |  | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.34562 |  | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-181 | " | Non-Converge |  |  | 0.04863 |  | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-182 | " | Non-Converge |  |  | 0.04863 |  | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-234 | " | Non-Converge |  |  | 0.047 |  | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.34562 |  | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-181 | " | Non-Converge |  |  | 0.04863 |  | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-182 | " | Non-Converge |  |  | 0.04863 |  | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-234 | " | Non-Converge |  |  | 0.047 |  | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.34562 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-181 | " | Non-Converge |  |  | 0.04863 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-182 | " | Non-Converge |  |  | 0.04863 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-234 | " | Non-Converge |  |  | 0.047 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.34562 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-181 | " | Non-Converge |  |  | 0.04863 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-182 | " | Non-Converge |  |  | 0.04863 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-234 | " | Non-Converge |  |  | 0.047 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.65438 |  | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.65438 |  | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converge | DISIS-2017-002 CF | 02ALL | 0 | 26L | GEN-2017-144 | " | Non-Converge |  |  | 0.65438 |  | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2017-002 | 00NR | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 01NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 02ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 02NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 03ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 03ALL | 0 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 03ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 | 03ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 03NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 04NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 05ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 05ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 05ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 05NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 03ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 03ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 03ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 00NR | 0 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 00NR | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 00NR | 0 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 01ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 01ALL | 0 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 01ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 01ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 01ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 01ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 01ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 01ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 01NR | 0 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 01NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 02ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 02NR | 0 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 02NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 03ALL | 0 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2017-002 CF | 03NR | 0 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 03NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 CF | 03ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2017-002 | 04ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | DISIS-2017-002 | 00NR | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 00NR | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 00NR | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 01ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 01ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 01ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 01ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 01NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 02ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 02ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 02ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 02ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 02NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 03ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 03ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 03ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 03NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 04ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 04ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 04ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 04NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 05ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 05ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 | 05ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 04ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 04ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 04ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 04NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 05ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 05ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 05ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 00ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 00ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 00ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 01ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 01ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 01ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 01ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 02ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 02ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 02ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 02ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 03ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 03ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 03ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 00NR | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 00NR | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 00NR | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 01NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 02NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2017-002 CF | 03NR | 2 | 26L | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT1 | 3 Phase fault on AURORA 7 115.00 (652474) 115 kV Bus a. Apply fault at the AURORA 7 115.00 (652474) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA 7 (652474) 115.0 kV to FLANDRU7 (652505) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT2 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT3 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT5 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT6 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT7 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT8 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT9 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT10 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT11 | 3 Phase fault on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT12 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT13 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT14 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT15 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT16 | 3 Phase fault on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.2. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT17 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT18 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT19 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT20 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT21 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT22 | 3 Phase fault on CHERRYC7 115.00 (603008) 115 kV Bus a. Apply fault at the CHERRYC7 115.00 (603008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT23 | 3 Phase fault on CHERRYC7 115.00 (603008) 115 kV Bus a. Apply fault at the CHERRYC7 115.00 (603008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT24 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT25 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT26 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN7 (603013) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT27 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN7 (603013) 115.0 kV to CHANRMB7 (603180) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT28 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT29 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT30 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT31 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT32 | 3 Phase fault on WSX FLS7 115.00 (603017) 115 kV Bus a. Apply fault at the WSX FLS7 115.00 (603017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSX FLS7 (603017) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT33 | 3 Phase fault on SOURIS 7 115.00 (603022) 115 kV Bus a. Apply fault at the SOURIS 7 115.00 (603022) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOURIS 7 (603022) 115.0 kV to MAGIC CITY 7 (603270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT34 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT35 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT36 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT37 | 3 Phase fault on MAGIC CITY 7115.00 (603270) 115 kV Bus a. Apply fault at the MAGIC CITY 7115.00 (603270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 7 (603270) 115.0 kV to VELVA TAP (605634) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT38 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT39 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT40 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT41 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT42 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT43 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT44 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT45 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #8 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT46 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN8 (605215) 69.0 kV to PIPESTN7 (603013) 115.0 kV Two Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT47 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN8 (605215) 69.0 kV to PIPESTN7 (603013) 115.0 kV Two Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT48 | 3 Phase fault on WSX FLS7 115.00 (603017) 115 kV Bus a. Apply fault at the WSX FLS7 115.00 (603017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSX FLS8 (605207) 69.0 kV to WSX FLS7 (603017) 115.0 kV Two Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT49 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT50 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT51 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT52 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT55 | 3 Phase fault on SPLITRK CAP7115.00 (603228) 115 kV Bus a. Apply fault at the SPLITRK CAP7115.00 (603228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLITRK CAP7 (603228) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT56 | 3 Phase fault on PROSE CAP7 115.00 (603265) 115 kV Bus a. Apply fault at the PROSE CAP7 115.00 (603265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PROSE CAP7 (603265) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT57 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT58 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT59 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT60 | 3 Phase fault on MINEHAH7 115.00 (603011) 115 kV Bus a. Apply fault at the MINEHAH7 115.00 (603011) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINEHAH7 (603011) 115.0 kV to LAWRENC7 (603012) 115.0 kV Transmission Circuit #1 b.2. MINEHAH7 (603011) 115.0 kV to LINCNCO7 (603014) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT61 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT62 | 3 Phase fault on GRANT 7 115.00 (603009) 115 kV Bus a. Apply fault at the GRANT 7 115.00 (603009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to GRANT 7 (603009) 115.0 kV Transmission Circuit #1 b.2. GRANT 7 (603009) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.3. GRANT (605011) 69.0 kV to GRANT 7 (603009) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT63 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT64 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT65 | 3 Phase fault on BUFFRID7 115.00 (603134) 115 kV Bus a. Apply fault at the BUFFRID7 115.00 (603134) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN7 (603013) 115.0 kV to BUFFRID7 (603134) 115.0 kV Transmission Circuit #1 b.2. BUFLO RDG 2 (605647) 34.5 kV to BUFFRID7 (603134) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT66 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT67 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT68 | 3 Phase fault on ADAMS 5 161.00 (635056) 161 kV Bus a. Apply fault at the ADAMS 5 161.00 (635056) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT70 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT71 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT72 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT73 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT74 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT75 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT76 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT77 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT78 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT79 | 3 Phase fault on MCKSBRG 5 161.00 (635645) 161 kV Bus a. Apply fault at the MCKSBRG 5 161.00 (635645) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCKSBRG 5 (635645) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT80 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT81 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT82 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT83 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT84 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT85 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT86 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT87 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT88 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT89 | 3 Phase fault on 5MARYVB2 161.00 (300097) 161 kV Bus a. Apply fault at the 5MARYVB2 161.00 (300097) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARYVB2 (300097) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT90 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT91 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT92 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT93 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT94 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT95 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT96 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT97 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT98 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT99 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT100 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT101 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT102 | 3 Phase fault on SOURIS 7 115.00 (603022) 115 kV Bus a. Apply fault at the SOURIS 7 115.00 (603022) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOURIS 7 (603022) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT103 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT104 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT105 | 3 Phase fault on E.RUTHVL-CP7115.00 (655655) 115 kV Bus a. Apply fault at the E.RUTHVL-CP7115.00 (655655) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 b.2. E.RUTHVL-CP7 (655655) 115.0 kV to E.RUTHVL-CP9 (655600) 41.6 kV Two Winding #1 b.3. E.RUTHVL-CP7 (655655) 115.0 kV to DUNNING -CP7 (655656) 115.0 kV Transmission Circuit #1 b.4. E.RUTHVL-CP7 (655655) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.5. E.RUTHVL-CP7 (655655) 115.0 kV to RUTHVILL-CP7 (655658) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT106 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT107 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT108 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT109 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT110 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT111 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT112 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT113 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT114 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT115 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT116 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT117 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 b.5. PICKERT8 (657923) 69.0 kV to PICKERT4 (657759) 230.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT118 | 3 Phase fault on PLEASANT LK7115.00 (652446) 115 kV Bus a. Apply fault at the PLEASANT LK7115.00 (652446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.2. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT119 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT120 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT121 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT122 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT123 | 3 Phase fault on MAPLETAP-LO7115.00 (659716) 115 kV Bus a. Apply fault at the MAPLETAP-LO7115.00 (659716) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL7 (652524) 115.0 kV to MAPLETAP-LO7 (659716) 115.0 kV Transmission Circuit #1 b.2. MAPLE ST-ER7 (655409) 115.0 kV to MAPLETAP-LO7 (659716) 115.0 kV Transmission Circuit #1 b.3. MAPLETAP-LO7 (659716) 115.0 kV to STATELIN-LO7 (659717) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT124 | 3 Phase fault on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENASTON-BE7 (659308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT125 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT126 | 3 Phase fault on ALLISNTP-LO869.000 (659702) 69 kV Bus a. Apply fault at the ALLISNTP-LO869.000 (659702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPRKTP-LO8 (659700) 69.0 kV to ALLISNTP-LO8 (659702) 69.0 kV Transmission Circuit #1 b.2. ALLISNTP-LO8 (659702) 69.0 kV to ALLISON -LO8 (659703) 69.0 kV Transmission Circuit #1 b.3. ALLISNTP-LO8 (659702) 69.0 kV to MAYCITY -LO8 (659704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT127 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT129 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT130 | 3 Phase fault on RUGBY TP-CP7115.00 (655665) 115 kV Bus a. Apply fault at the RUGBY TP-CP7115.00 (655665) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #z b.2. ROLETTE_-CP7 (655609) 115.0 kV to THORNE -CP7 (655649) 115.0 kV Transmission Circuit #1 b.3. ROLETTE_-CP7 (655609) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 b.4. RUGBY -CP7 (655654) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT131 | 3 Phase fault on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT132 | 3 Phase fault on ROYAL 8 69.000 (630010) 69 kV Bus a. Apply fault at the ROYAL 8 69.000 (630010) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROYAL 8 (630010) 69.0 kV to CORNLLTA8 (656433) 69.0 kV Transmission Circuit #1 b.2. ROYAL 8 (630010) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT133 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT134 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT135 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT136 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT137 | 3 Phase fault on TWIN CH8 69.000 (640388) 69 kV Bus a. Apply fault at the TWIN CH8 69.000 (640388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT138 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT139 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT140 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT141 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT142 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT143 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT144 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT145 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT146 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT147 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT148 | 3 Phase fault on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT149 | 3 Phase fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT150 | 3 Phase fault on MITCHELL 7115.00 (660004) 115 kV Bus a. Apply fault at the MITCHELL 7115.00 (660004) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MITCHELL 7 (660004) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT151 | 3 Phase fault on MITCHELL 7115.00 (660004) 115 kV Bus a. Apply fault at the MITCHELL 7115.00 (660004) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT152 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT153 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT154 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT155 | 3 Phase fault on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT156 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT157 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT158 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT159 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT160 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT161 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT162 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT163 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT164 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT165 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT166 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT167 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT168 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT169 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT170 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT171 | 3 Phase fault on PALERMO -MW7115.00 (655916) 115 kV Bus a. Apply fault at the PALERMO -MW7115.00 (655916) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT172 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT173 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT174 | 3 Phase fault on ROSEGLEN-CP7115.00 (655662) 115 kV Bus a. Apply fault at the ROSEGLEN-CP7115.00 (655662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLS.C-CP7 (655661) 115.0 kV to ROSEGLEN-CP7 (655662) 115.0 kV Transmission Circuit #1 b.2. ROSEGLEN-CP7 (655662) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.3. RAUB TAP-CP7 (655663) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.4. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT175 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT176 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT177 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT178 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT179 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT180 | 3 Phase fault on K424SANB-NI869.000 (659958) 69 kV Bus a. Apply fault at the K424SANB-NI869.000 (659958) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVERLYN8 (630028) 69.0 kV to SPENCER8 (652581) 69.0 kV Transmission Circuit #1 b.2. EVERLYN8 (630028) 69.0 kV to K409HRTM-NI8 (659960) 69.0 kV Transmission Circuit #1 b.3. SANBORNMUNI8 (658908) 69.0 kV to M5SANBOR-NI8 (659892) 69.0 kV Transmission Circuit #1 b.4. M5SANBOR-NI8 (659892) 69.0 kV to K424SANB-NI8 (659958) 69.0 kV Transmission Circuit #1 b.5. J2______-NI8 (659908) 69.0 kV to K424SANB-NI8 (659958) 69.0 kV Transmission Circuit #1 b.6. K424SANB-NI8 (659958) 69.0 kV to K417HART-NI8 (659959) 69.0 kV Transmission Circuit #1 b.7. K417HART-NI8 (659959) 69.0 kV to K409HRTM-NI8 (659960) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT181 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT182 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT183 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT184 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT185 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT186 | 3 Phase fault on GARRISN7 115 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV Load #BB b.2. GARRISN7 (652442) 115.0 kV Load #BW b.3. GARRISN7 (652442) 115.0 kV Load #R0 b.4. GARRISN7 (652442) 115.0 kV Load #W0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Base | GROUP1_LOCAL_P1_FAULT187 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT187 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. Issue also observed in the base case. | Reclosing was removed.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT188 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT189 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT190 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT191 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT193 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT194 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT195 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT196 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT197 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT198 | 3 Phase fault on CAROL S8 69.000 (635322) 69 kV Bus a. Apply fault at the CAROL S8 69.000 (635322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROL S8 (635322) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT199 | 3 Phase fault on TEMPLTN8 69.000 (635325) 69 kV Bus a. Apply fault at the TEMPLTN8 69.000 (635325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTN8 (635325) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT200 | 3 Phase fault on MIDAMER8 69.000 (635373) 69 kV Bus a. Apply fault at the MIDAMER8 69.000 (635373) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDAMER8 (635373) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT201 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT202 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT203 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT204 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT205 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT206 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT207 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT208 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT209 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT210 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT211 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT212 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT213 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT214 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT215 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT216 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT217 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT218 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT219 | 3 Phase fault on SIOUXFL8 69.000 (652235) 69 kV Bus a. Apply fault at the SIOUXFL8 69.000 (652235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL8 (652235) 69.0 kV to SW101-ER8 (655011) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT220 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT221 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT222 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Base | GROUP1_LOCAL_P1_FAULT223 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed and clearing time was reduced to 5 cycles.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT223 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. Issue also observed in the base case. | Reclosing was removed and clearing time was reduced to 5 cycles.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT224 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT225 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT226 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT227 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT228 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT229 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT230 | 3 Phase fault on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT231 | 3 Phase fault on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT232 | 3 Phase fault on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT233 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT234 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV to MANNING-ER7 (655478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT235 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT236 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV to HOLLAND -LO7 (659733) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT237 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT238 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT239 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT240 | 3 Phase fault on SIOUXFL7 115.00 (652524) 115 kV Bus a. Apply fault at the SIOUXFL7 115.00 (652524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL7 (652524) 115.0 kV to SW1145-ER7 (655377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT241 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT242 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT243 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT244 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT245 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT246 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT247 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT248 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT249 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT250 | 3 Phase fault on SPENCER8 69.000 (652581) 69 kV Bus a. Apply fault at the SPENCER8 69.000 (652581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER8 (652581) 69.0 kV to SPNCRSJCT8 (656555) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT251 | 3 Phase fault on SPENCER8 69.000 (652581) 69 kV Bus a. Apply fault at the SPENCER8 69.000 (652581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER8 (652581) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT252 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT253 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT254 | 3 Phase fault on LETCHER7 115.00 (652609) 115 kV Bus a. Apply fault at the LETCHER7 115.00 (652609) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT255 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to FREEMAN-ER7 (655418) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT256 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT257 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT258 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT259 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT260 | 3 Phase fault on MOS-CNTN-ER869.000 (655142) 69 kV Bus a. Apply fault at the MOS-CNTN-ER869.000 (655142) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CNTN-ER8 (655142) 69.0 kV to TEA-ER8 (655322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT261 | 3 Phase fault on MOS-PARK-ER869.000 (655143) 69 kV Bus a. Apply fault at the MOS-PARK-ER869.000 (655143) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-PARK-ER8 (655143) 69.0 kV to PARKER-ER8 (655192) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT262 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT263 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT264 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT265 | 3 Phase fault on SW1145-ER7 115.00 (655377) 115 kV Bus a. Apply fault at the SW1145-ER7 115.00 (655377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW1145-ER7 (655377) 115.0 kV to SW167 -ER7 (655413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT266 | 3 Phase fault on HRRISBRG-ER7115.00 (655404) 115 kV Bus a. Apply fault at the HRRISBRG-ER7115.00 (655404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HRRISBRG-ER7 (655404) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT267 | 3 Phase fault on SXFCHCLR-ER7115.00 (655408) 115 kV Bus a. Apply fault at the SXFCHCLR-ER7115.00 (655408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT268 | 3 Phase fault on BUCKSNRT-ER7115.00 (655441) 115 kV Bus a. Apply fault at the BUCKSNRT-ER7115.00 (655441) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT269 | 3 Phase fault on BUCKSNRT-ER7115.00 (655441) 115 kV Bus a. Apply fault at the BUCKSNRT-ER7115.00 (655441) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT270 | 3 Phase fault on DELAPRE-ER7 115.00 (655444) 115 kV Bus a. Apply fault at the DELAPRE-ER7 115.00 (655444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT271 | 3 Phase fault on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT272 | 3 Phase fault on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT273 | 3 Phase fault on VFODNES-ER7 115.00 (655468) 115 kV Bus a. Apply fault at the VFODNES-ER7 115.00 (655468) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT274 | 3 Phase fault on BERTHOLD-CP7115.00 (655641) 115 kV Bus a. Apply fault at the BERTHOLD-CP7115.00 (655641) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT275 | 3 Phase fault on BERTHOLD-CP7115.00 (655641) 115 kV Bus a. Apply fault at the BERTHOLD-CP7115.00 (655641) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT276 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT277 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT278 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT279 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT280 | 3 Phase fault on PARSHALL-MW7115.00 (655908) 115 kV Bus a. Apply fault at the PARSHALL-MW7115.00 (655908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSHALL-MW7 (655908) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT281 | 3 Phase fault on STANLEY -MW7115.00 (655917) 115 kV Bus a. Apply fault at the STANLEY -MW7115.00 (655917) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANLEY -MW7 (655917) 115.0 kV to LOSTWD_T-MW7 (655950) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT282 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV to BLAISDEL-MW7 (655949) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT283 | 3 Phase fault on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Base | GROUP1_LOCAL_P1_FAULT284 | 3 Phase fault on CAROLTON8 69.000 (656233) 69 kV Bus a. Apply fault at the CAROLTON8 69.000 (656233) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTON8 (656233) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Violation of the damping factor criteria was observed at COONRPDS (656237) | Reduce clearing time to 3.5 cycles
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT284 | 3 Phase fault on CAROLTON8 69.000 (656233) 69 kV Bus a. Apply fault at the CAROLTON8 69.000 (656233) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTON8 (656233) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Violation of the damping factor criteria was observed at COONRPDS (656237). The issue was also present in the base case. | Reduce clearing time to 3.5 cycles
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT285 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT286 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT287 | 3 Phase fault on INDUSTRI8 69.000 (656493) 69 kV Bus a. Apply fault at the INDUSTRI8 69.000 (656493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDUSTRI8 (656493) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT288 | 3 Phase fault on SPNCRSJCT8 69.000 (656555) 69 kV Bus a. Apply fault at the SPNCRSJCT8 69.000 (656555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNCRSJCT8 (656555) 69.0 kV to SPENCERW8 (656609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT289 | 3 Phase fault on SPNCRSJCT8 69.000 (656555) 69 kV Bus a. Apply fault at the SPNCRSJCT8 69.000 (656555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNCRSJCT8 (656555) 69.0 kV to SPENCERS8 (656611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT290 | 3 Phase fault on WISDMJCT8 69.000 (656571) 69 kV Bus a. Apply fault at the WISDMJCT8 69.000 (656571) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WISDMJCT8 (656571) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT291 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT292 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT293 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT294 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT295 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT296 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT297 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT298 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT299 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT300 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT301 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT302 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Base | GROUP1_LOCAL_P1_FAULT303 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT303 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. Issue also observed in the base case. | Reclosing was removed.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT304 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT305 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT306 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT307 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT308 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT309 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT310 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Base | GROUP1_LOCAL_P1_FAULT311 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed and clearing time was reduced to 5 cycles.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT311 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. Issue also observed in the base case. | Reclosing was removed and clearing time was reduced to 5 cycles.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT312 | 3 Phase fault on K126MEC -NI869.000 (659852) 69 kV Bus a. Apply fault at the K126MEC -NI869.000 (659852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K126MEC -NI8 (659852) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT313 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT314 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT315 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT316 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT317 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT318 | 3 Phase fault on K308EARL-NI869.000 (659856) 69 kV Bus a. Apply fault at the K308EARL-NI869.000 (659856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K308EARL-NI8 (659856) 69.0 kV to K321MEC -NI8 (659857) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT319 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT320 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT321 | 3 Phase fault on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT322 | 3 Phase fault on K319EWOL-NI869.000 (659867) 69 kV Bus a. Apply fault at the K319EWOL-NI869.000 (659867) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K319EWOL-NI8 (659867) 69.0 kV to L9 MANNI-NI8 (659868) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT323 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT324 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT325 | 3 Phase fault on K326OTTE-NI869.000 (659886) 69 kV Bus a. Apply fault at the K326OTTE-NI869.000 (659886) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K326OTTE-NI8 (659886) 69.0 kV to K333SCHL-NI8 (659887) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT326 | 3 Phase fault on K333SCHL-NI869.000 (659887) 69 kV Bus a. Apply fault at the K333SCHL-NI869.000 (659887) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K333SCHL-NI8 (659887) 69.0 kV to K337ARTH-NI8 (659888) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT327 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT328 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT329 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT330 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT331 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT332 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT333 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT334 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT335 | 3 Phase fault on K105UTE_-NI869.000 (659998) 69 kV Bus a. Apply fault at the K105UTE_-NI869.000 (659998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K105UTE_-NI8 (659998) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Base | GROUP1_LOCAL_P1_FAULT336 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT336 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. Issue also observed in the base case. | Reclosing was removed.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT337 | 3 Phase fault on MAGIC CITY 4230.00 (602052) 230 kV Bus a. Apply fault at the MAGIC CITY 4230.00 (602052) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to MAGIC CITY 7 (603270) 115.0 kV to MAGIC CTY T9 (605787) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT338 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT339 | 3 Phase fault on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV to RUGBY T (620179) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT340 | 3 Phase fault on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV to RUGBY T2 (620479) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT341 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT342 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSONG (640164) 69.0 kV to EMERSON7 (640163) 115.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT343 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT344 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT345 | 3 Phase fault on S.SIOUXCITY7115.00 (640424) 115 kV Bus a. Apply fault at the S.SIOUXCITY7115.00 (640424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.SIOUXCITY8 (640425) 69.0 kV to S.SIOUXCITY7 (640424) 115.0 kV to S.SIOUXCYT19 (643170) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT346 | 3 Phase fault on SIOUXFL7 115.00 (652524) 115 kV Bus a. Apply fault at the SIOUXFL7 115.00 (652524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL8 (652235) 69.0 kV to SIOUXFL7 (652524) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT347 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT348 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT349 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT350 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT351 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT352 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV to BERSFRD8 (652254) 69.0 kV to BERSFR19 (652255) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT353 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV to FLANDRU8 (652229) 69.0 kV to FLANDR19 (652227) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT354 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT355 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT356 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT357 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to HANLON1-ER8 (655494) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT358 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to HANLON2-ER8 (655495) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT359 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to HANLON-ER7 (655493) 115.0 kV to HANLON 9 (652592) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT360 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT361 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT362 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT363 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT364 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT366 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT367 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT368 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT369 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT370 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT371 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT372 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT373 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT374 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT375 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT376 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT377 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT378 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT379 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT380 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT381 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT382 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT383 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT384 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT385 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT386 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT387 | 3 Phase fault on BDV 4230.00 (672603) 230 kV Bus a. Apply fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT388 | 3 Phase fault on FALLS 7 115.00 (603225) 115 kV Bus a. Apply fault at the FALLS 7 115.00 (603225) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FALLS 7 (603225) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT389 | 3 Phase fault on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT390 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT391 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT392 | 3 Phase fault on WISDOM G 69.000 (656573) 69 kV Bus a. Apply fault at the WISDOM G 69.000 (656573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WISDOM G (656573) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT393 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P1_FAULT394 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT3 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT4 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT5 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT6 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT7 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT8 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT9 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT10 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT11 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT12 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT13 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT14 | 3 Phase fault on CNTSHNT3 345.00 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 345.00 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT15 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reduce acceleration factor to 0.1.
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT16 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT17 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT18 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT19 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT20 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT21 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT22 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT23 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT24 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT25 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT26 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT27 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT28 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT29 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT30 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT31 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT32 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT33 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT34 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT35 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT36 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT37 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT38 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT39 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT40 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT41 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT42 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT43 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P1_FAULT44 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT1 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT2 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT3 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.6. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT4 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT5 | Single Phase Fault with Stuck Breaker on SOURIS 7 115.00 (603022) 115 kV Bus a. Apply Fault at the SOURIS 7 115.00 (603022) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOURIS 7 (603022) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 b.2. SOURIS 7 (603022) 115.0 kV to MAGIC CITY 7 (603270) 115.0 kV Transmission Circuit #1 b.3. MAGIC CITY 7 (603270) 115.0 kV to VELVA TAP (605634) 115.0 kV Transmission Circuit #1 b.4. VELVA TAP (605634) 115.0 kV to VELVA FDR2 (605633) 34.5 kV Two Winding #1 b.5. VELVA TAP (605634) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT6 | Single Phase Fault with Stuck Breaker on MALLARD7 115.00 (603023) 115 kV Bus a. Apply Fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOURIS 7 (603022) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 b.2. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.3. MALLARD7 (603023) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.4. MALLARD7 (603023) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 b.5. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 b.6. MALLARD1-CP9 (655603) 41.6 kV to MALLARD7 (603023) 115.0 kV Two Winding #1 b.7. MALLARD2-CP9 (655604) 41.6 kV to MALLARD7 (603023) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT7 | Single Phase Fault with Stuck Breaker on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply Fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. PIPESTN7 (603013) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.3. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT8 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 b.4. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT9 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.4. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT10 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT11 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT12 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT13 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (635226) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (635226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT14 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT15 | Single Phase Fault with Stuck Breaker on LEMARS S 5 161.00 (635261) 161 kV Bus a. Apply Fault at the LEMARS S 5 161.00 (635261) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.4. LEMARS S 5 (635261) 161.0 kV to LEMARS S 8 (635262) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT16 | Single Phase Fault with Stuck Breaker on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply Fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.4. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.5. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT17 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT18 | Single Phase Fault with Stuck Breaker on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply Fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.4. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT19 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT20 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT21 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT22 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT23 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT24 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.5. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.7. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.8. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.9. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.10. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT25 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT26 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT27 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT28 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.2. SIOUXFL8 (652235) 69.0 kV to SIOUXFL7 (652524) 115.0 kV Two Winding #1 b.3. SIOUXFL8 (652235) 69.0 kV to SW101-ER8 (655011) 69.0 kV Transmission Circuit #1 b.4. FLANDRU7 (652505) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.5. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT29 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERSFRD7 (652502) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.2. BRANDON-ER7 (655400) 115.0 kV to ROWENA-ER7 (655401) 115.0 kV Transmission Circuit #1 b.3. BRANDON-ER7 (655400) 115.0 kV to SW1116 -ER7 (655414) 115.0 kV Transmission Circuit #1 b.4. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT30 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT31 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT32 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT33 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT34 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT35 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT36 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT37 | Single Phase Fault with Stuck Breaker on HANLON 4 230.00 (652513) 230 kV Bus a. Apply Fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to HANLON1-ER8 (655494) 69.0 kV Two Winding #1 b.3. HANLON 4 (652513) 230.0 kV to HANLON2-ER8 (655495) 69.0 kV Two Winding #1 b.4. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.5. SW124-ER8 (655019) 69.0 kV to HANLON1-ER8 (655494) 69.0 kV Transmission Circuit #1 b.6. SW130-ER8 (655020) 69.0 kV to HANLON1-ER8 (655494) 69.0 kV Transmission Circuit #1 b.7. SW159-ER8 (655026) 69.0 kV to HANLON1-ER8 (655494) 69.0 kV Transmission Circuit #1 b.8. HANLON1-ER8 (655494) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #z b.9. HANLON 4 (652513) 230.0 kV to HANLON-ER7 (655493) 115.0 kV to HANLON 9 (652592) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT38 | Single Phase Fault with Stuck Breaker on HANLON 4 230.00 (652513) 230 kV Bus a. Apply Fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to HANLON1-ER8 (655494) 69.0 kV Two Winding #1 b.3. HANLON 4 (652513) 230.0 kV to HANLON2-ER8 (655495) 69.0 kV Two Winding #1 b.4. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.5. SW145-ER8 (655023) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #1 b.6. SW1142-ER8 (655166) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #1 b.7. MOS-LKV2-ER8 (655226) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #1 b.8. HANLON1-ER8 (655494) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #z b.9. HANLON 4 (652513) 230.0 kV to HANLON-ER7 (655493) 115.0 kV to HANLON 9 (652592) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT39 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT40 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT41 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT42 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT43 | Single Phase Fault with Stuck Breaker on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply Fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT44 | Single Phase Fault with Stuck Breaker on GU CTR 5 161.00 (631072) 161 kV Bus a. Apply Fault at the GU CTR 5 161.00 (631072) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.5. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.6. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.7. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.8. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.9. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. SCRANTN5 (631071) 161.0 kV to SCRANTN9 (629111) 34.5 kV Two Winding #1 b.11. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.12. SCRANTN5 (631071) 161.0 kV to GR JCT 5 (631074) 161.0 kV Transmission Circuit #1 b.13. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT45 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT46 | Single Phase Fault with Stuck Breaker on ONEILL 7 115.00 (640305) 115 kV Bus a. Apply Fault at the ONEILL 7 115.00 (640305) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 b.2. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.3. ONEILL 7 (640305) 115.0 kV to EAGLECREEK 7 (640465) 115.0 kV Transmission Circuit #1 b.4. ONEILL 7 (640305) 115.0 kV to ONEILL 8 (640306) 69.0 kV to ONEILL T1 9 (643117) 13.8 kV Three Winding #1 b.5. ONEILL 7 (640305) 115.0 kV to ONEILL 8 (640306) 69.0 kV to ONEILL T2 9 (643118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT47 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT48 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT49 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT50 | Single Phase Fault with Stuck Breaker on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply Fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. GAVINS 7 (652511) 115.0 kV to GAVINS1G (652575) 13.2 kV Two Winding #1 b.4. GAVINS 7 (652511) 115.0 kV to GAVINS2G (652576) 13.2 kV Two Winding #1 b.5. GAVINS 7 (652511) 115.0 kV to GAVINS3G (652577) 13.2 kV Two Winding #1 b.6. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 b.7. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT51 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.6. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT52 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT53 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT54 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT55 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERSFRD7 (652502) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.2. SIOUXFL7 (652524) 115.0 kV to SW1145-ER7 (655377) 115.0 kV Transmission Circuit #1 b.3. SIOUXFL7 (652524) 115.0 kV to MAPLETAP-LO7 (659716) 115.0 kV Transmission Circuit #1 b.4. BRANDON-ER7 (655400) 115.0 kV to ROWENA-ER7 (655401) 115.0 kV Transmission Circuit #1 b.5. BRANDON-ER7 (655400) 115.0 kV to SW1116 -ER7 (655414) 115.0 kV Transmission Circuit #1 b.6. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT56 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.2. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.3. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.4. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 b.5. VFODNES-ER7 (655468) 115.0 kV to VFODNES4 (652398) 230.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT57 | Single Phase Fault with Stuck Breaker on MITCHELL 7115.00 (660004) 115 kV Bus a. Apply Fault at the MITCHELL 7115.00 (660004) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANT 7 (603009) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.2. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.3. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit #1 b.4. MITCHELL 7 (660004) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 b.5. MIT TRANSMSN (660200) 34.5 kV to MITCHELL 7 (660004) 115.0 kV Two Winding #1 b.6. MIT TRANSMSN (660200) 34.5 kV to MITCHELL 7 (660004) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT58 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT59 | Single Phase Fault with Stuck Breaker on TRIPP JCT 7115.00 (660005) 115 kV Bus a. Apply Fault at the TRIPP JCT 7115.00 (660005) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.2. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit #1 b.3. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.4. TRIPP JCT 7 (660005) 115.0 kV to SCHROEDER 7 (660018) 115.0 kV Transmission Circuit #1 b.5. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding #1 b.6. TRIPP JCT (660221) 34.5 kV to TRIPP JCT 7 (660005) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT60 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT61 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT62 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT63 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT64 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT65 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT66 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT67 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT68 | Single Phase Fault with Stuck Breaker on PLEASANT LK7115.00 (652446) 115 kV Bus a. Apply Fault at the PLEASANT LK7115.00 (652446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 8 (652317) 69.0 kV to LEEDS 7 (652447) 115.0 kV Two Winding #1 b.2. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.3. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT70 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.4. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.5. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT71 | Single Phase Fault with Stuck Breaker on MTVERN 7 115.00 (652518) 115 kV Bus a. Apply Fault at the MTVERN 7 115.00 (652518) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. MTVERNS8 (652251) 69.0 kV to MTVERN 7 (652518) 115.0 kV Two Winding #1 b.4. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.6. MTVERN 7 (652518) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.7. MT VERNON 8 (660252) 69.0 kV to MTVERN 7 (652518) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT72 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT73 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT74 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT75 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT76 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT77 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT78 | Single Phase Fault with Stuck Breaker on SD.PW1__-BE934.500 (659327) 34.5 kV Bus a. Apply Fault at the SD.PW1__-BE934.500 (659327) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT79 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.5. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT80 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding #1 b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT81 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT82 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to VFODNES4 (652398) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding #1 b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT83 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to VFODNES4 (652398) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT84 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT85 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT86 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. EXIRA 5 (652603) 161.0 kV to EXIRA 2G (658001) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT87 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT88 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT89 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.3. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.8. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT90 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT91 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT92 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 b.7. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT93 | Single Phase Fault with Stuck Breaker on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply Fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.5. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.6. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.7. YNK JCT (660100) 34.5 kV to YANKTON JCT7 (660006) 115.0 kV Two Winding #1 b.8. YNK JCT (660100) 34.5 kV to YANKTON JCT7 (660006) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT94 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT95 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT96 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT97 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT98 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT99 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT100 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT101 | Single Phase Fault with Stuck Breaker on NAPA JCT 7115.00 (660026) 115 kV Bus a. Apply Fault at the NAPA JCT 7115.00 (660026) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.2. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.3. NAPA JCT 7 (660026) 115.0 kV to YANKTONEAST7 (660036) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT102 | Single Phase Fault with Stuck Breaker on BOTINU.W-CP7115.00 (655650) 115 kV Bus a. Apply Fault at the BOTINU.W-CP7115.00 (655650) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOTINU.W-CP7 (655650) 115.0 kV to DUNNING -CP7 (655656) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT103 | Single Phase Fault with Stuck Breaker on DUNNING -CP7115.00 (655656) 115 kV Bus a. Apply Fault at the DUNNING -CP7115.00 (655656) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 b.2. E.RUTHVL-CP7 (655655) 115.0 kV to E.RUTHVL-CP9 (655600) 41.6 kV Two Winding #1 b.3. E.RUTHVL-CP7 (655655) 115.0 kV to DUNNING -CP7 (655656) 115.0 kV Transmission Circuit #1 b.4. E.RUTHVL-CP7 (655655) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.5. E.RUTHVL-CP7 (655655) 115.0 kV to RUTHVILL-CP7 (655658) 115.0 kV Transmission Circuit #1 b.6. DUNNING -CP7 (655656) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT104 | Single Phase Fault with Stuck Breaker on DUNNING -CP7115.00 (655656) 115 kV Bus a. Apply Fault at the DUNNING -CP7115.00 (655656) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNNING -CP7 (655656) 115.0 kV to DUNNING2-CP8 (655678) 60.0 kV Two Winding #1 b.2. DUNNING -CP7 (655656) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT105 | Single Phase Fault with Stuck Breaker on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply Fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.2. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.3. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 b.4. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT106 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT107 | Single Phase Fault with Stuck Breaker on PALERMO -MW7115.00 (655916) 115 kV Bus a. Apply Fault at the PALERMO -MW7115.00 (655916) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.4. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT108 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.4. BLAISDEL-BE7 (659144) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT109 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 b.2. LGN.KW1A-BE9 (659208) 13.8 kV to LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT110 | Single Phase Fault with Stuck Breaker on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply Fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LGN.KW1A-BE9 (659208) 13.8 kV to LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV Three Winding #1 b.2. LOGAN___-BE7 (659155) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT111 | Single Phase Fault with Stuck Breaker on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply Fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.2. E.RUTHVL-CP7 (655655) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.3. SW.MINOT-CP7 (655657) 115.0 kV to SW.MNOT1-CP9 (655605) 41.6 kV Two Winding #1 b.4. SW.MINOT-CP7 (655657) 115.0 kV to SW.MNOT2-CP9 (655606) 41.6 kV Two Winding #2 b.5. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT112 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT113 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. BROOKS 5 (635037) 161.0 kV to ADAMS 5 (635056) 161.0 kV Transmission Circuit #1 b.5. ADAMS 5 (635056) 161.0 kV to ADAMS B1 9 (635057) 34.5 kV Two Winding #1 b.6. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.7. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT114 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT115 | Single Phase Fault with Stuck Breaker on AGATE -CP7115.00 (655616) 115 kV Bus a. Apply Fault at the AGATE -CP7115.00 (655616) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.2. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.3. LEEDS 7 (652447) 115.0 kV to AGATE -CP7 (655616) 115.0 kV Transmission Circuit #1 b.4. ROLLA___-CP7 (655614) 115.0 kV to AGATE -CP7 (655616) 115.0 kV Transmission Circuit #1 b.5. AGATE -CP7 (655616) 115.0 kV to AGATE -CP8 (655617) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT116 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFALLS-ER7 (655439) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit #z b.2. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit #1 b.3. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.4. SUNDOWN-ER7 (655445) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit #1 b.5. VFODNES1-ER9 (655470) 12.5 kV to VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT117 | Single Phase Fault with Stuck Breaker on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply Fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to WALLLK-ER7 (655447) 115.0 kV Transmission Circuit #1 b.2. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.3. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit #1 b.4. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit #1 b.5. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT118 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT119 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT120 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT121 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT122 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT123 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT124 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT125 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT126 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT127 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT128 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT129 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT130 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT131 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT132 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT133 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT134 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT135 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (655690) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (655690) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to Load #BW b.7. GARRISN7 (652442) 115.0 kV to Load #R0 b.8. GARRISN7 (652442) 115.0 kV to Load #W0 b.9. GARRISN7 (652442) 115.0 kV to Load #BB | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT136 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT137 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT138 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT139 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT140 | Single Phase Fault with Stuck Breaker on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply Fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.2. RUGBY 9 (652324) 41.8 kV to RUGBY 7 (652452) 115.0 kV Two Winding #1 b.3. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.4. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.5. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.6. RUGBY 7 (652452) 115.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Transmission Circuit #1 b.7. RUGBY 7 (652452) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #z b.8. ROLETTE_-CP7 (655609) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 b.9. RUGBY -CP7 (655654) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT141 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT142 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT143 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT144 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT145 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT146 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT147 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT148 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT149 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT150 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT151 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT152 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH8 (635224) 69.0 kV to PLYMOTH5 (635223) 161.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 b.2. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT153 | Single Phase Fault with Stuck Breaker on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply Fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT154 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT155 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT156 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT157 | Single Phase Fault with Stuck Breaker on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY8 (652574) 69.0 kV to SIOUXCY5 (652566) 161.0 kV Two Winding #1 b.2. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT158 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. DENISON8 (652583) 69.0 kV to DENISON4 (652567) 230.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT159 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to UTICAJC4 (652526) 230.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT160 | Single Phase Fault with Stuck Breaker on MOS-PARK-ER869.000 (655143) 69 kV Bus a. Apply Fault at the MOS-PARK-ER869.000 (655143) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-PARK-ER8 (655143) 69.0 kV to MOS-HRLM-ER8 (655105) 69.0 kV Transmission Circuit #1 b.2. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT161 | Single Phase Fault with Stuck Breaker on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply Fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA -MW7 (655944) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.2. PLAZA -MW7 (655944) 115.0 kV to PARSHALL-MW7 (655908) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT162 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT163 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT164 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. J6BOYER_-NI8 (659912) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT165 | Single Phase Fault with Stuck Breaker on J12_____-NI869.000 (659918) 69 kV Bus a. Apply Fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J12_____-NI8 (659918) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. J12_____-NI8 (659918) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT166 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT167 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT168 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 b.2. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT169 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT170 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT171 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT172 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT173 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY2 (652552) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT174 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT175 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT176 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT177 | Single Phase Fault with Stuck Breaker on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply Fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to PLEASANT LK7 (652446) 115.0 kV Transmission Circuit #1 b.2. RUGBY 7 (652452) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT178 | Single Phase Fault with Stuck Breaker on BONESTL7 115.00 (652475) 115 kV Bus a. Apply Fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT179 | Single Phase Fault with Stuck Breaker on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply Fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT180 | Single Phase Fault with Stuck Breaker on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply Fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 b.2. SW.MINOT-CP7 (655657) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT181 | Single Phase Fault with Stuck Breaker on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply Fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT182 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT183 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT184 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT185 | Single Phase Fault with Stuck Breaker on DENSOUMAIN8 69.000 (658031) 69 kV Bus a. Apply Fault at the DENSOUMAIN8 69.000 (658031) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENSOUMAIN8 (658031) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENSOUMAIN8 (658031) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT186 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT187 | Single Phase Fault with Stuck Breaker on TOYNE8 69.000 (656249) 69 kV Bus a. Apply Fault at the TOYNE8 69.000 (656249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOYNE8 (656249) 69.0 kV to TEMPLTON8 (656247) 69.0 kV Transmission Circuit #1 b.2. TOYNE8 (656249) 69.0 kV to CAROL S8 (635322) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT188 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT189 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT190 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL7 (652524) 115.0 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 b.2. SIOUXFL7 (652524) 115.0 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT191 | Single Phase Fault with Stuck Breaker on SPENCER8 69.000 (652581) 69 kV Bus a. Apply Fault at the SPENCER8 69.000 (652581) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER8 (652581) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 b.2. SPENCER8 (652581) 69.0 kV to EVERLYN8 (630028) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT192 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT193 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to PLYMOTH5 (635223) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT194 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT195 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT196 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT197 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT198 | Single Phase Fault with Stuck Breaker on UTICAJC7 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT199 | Single Phase Fault with Stuck Breaker on RASMUSN-ER8 (655485) 69 kV Bus a. Apply Fault at the RASMUSN-ER8 (655485) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RASMUSN-ER8 (655485) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT200 | Single Phase Fault with Stuck Breaker on VFODNES4 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT201 | Single Phase Fault with Stuck Breaker on SIOUXFL4 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT202 | Single Phase Fault with Stuck Breaker on SIOUXFL7 (652524) 115 kV Bus a. Apply Fault at the SIOUXFL7 (652524) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL7 (652524) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT203 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT204 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT205 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT206 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT207 | Single Phase Fault with Stuck Breaker on SW.MINOT-CP7 (655657) 115 kV Bus a. Apply Fault at the SW.MINOT-CP7 (655657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT208 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT209 | Single Phase Fault with Stuck Breaker on DENISON8 (652583) 69 kV Bus a. Apply Fault at the DENISON8 (652583) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT210 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI8 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI8 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT211 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT212 | Single Phase Fault with Stuck Breaker on SIOUXCY5 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT213 | Single Phase Fault with Stuck Breaker on PLYMOTH5 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT214 | Single Phase Fault with Stuck Breaker on SPENCER5 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT215 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT216 | Single Phase Fault with Stuck Breaker on SIOUXCY2 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_LOCAL_P4_FAULT217 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT1 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT2 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT3 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT5 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT6 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT7 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT8 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT9 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT10 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT11 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT12 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT13 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT14 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT15 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT16 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT17 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT18 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT19 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT20 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT21 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT22 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT23 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT24 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT25 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT26 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT27 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT28 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT29 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT30 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT31 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT32 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT33 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT34 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT35 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT36 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT37 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT38 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT39 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT40 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to HRDLKGEN (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT41 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT42 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT43 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT44 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT45 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT46 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT47 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT48 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT49 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT50 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT51 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT52 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT53 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT54 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT55 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT56 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT57 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT58 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT59 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT60 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT61 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT62 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT63 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT64 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT65 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT66 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT67 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT68 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT70 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT71 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT72 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT73 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT74 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT75 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT76 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT77 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT78 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT79 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT80 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT81 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT82 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT83 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT84 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT85 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT86 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT87 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT88 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT89 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT90 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT91 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT92 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT93 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT94 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT95 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT96 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT97 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT98 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT99 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT100 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT101 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT102 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT103 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT104 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT105 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT106 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT107 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT108 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT109 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT110 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT111 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT112 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT113 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT114 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 b.2. FORMAN 4 (620363) 230.0 kV to HANKSON4 (620327) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT115 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT116 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT117 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT118 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT119 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT120 | Single Phase Fault with Stuck Breaker on G82RPHT1 230.00 (667085) 230 kV Bus a. Apply Fault at the G82RPHT1 230.00 (667085) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G82RPHT1 (667085) 230.0 kV to GLENBOR4 (667052) 230.0 kV Transmission Circuit #1 b.2. G82RPHT1 (667085) 230.0 kV to PEACE GARD 5 (602057) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT121 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT122 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT123 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT124 | Single Phase Fault with Stuck Breaker on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply Fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z b.2. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT125 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT126 | Single Phase Fault with Stuck Breaker on BSSOUTH4 230.00 (620322) 230 kV Bus a. Apply Fault at the BSSOUTH4 230.00 (620322) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #2 b.2. BSSOUTH4 (620322) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT127 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT128 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT129 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT130 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 b.2. WHITE 7 (652538) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT131 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.2. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT132 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT133 | Single Phase Fault with Stuck Breaker on J748POI (87487) 345 kV Bus a. Apply Fault at the J748POI (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT134 | Single Phase Fault with Stuck Breaker on PEACE GARD 5 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT135 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT136 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT137 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT138 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT139 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT140 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT141 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT142 | Single Phase Fault with Stuck Breaker on FORMAN 4 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT143 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT144 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT145 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT146 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT147 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT148 | Single Phase Fault with Stuck Breaker on G82RPHT1 (667085) 230 kV Bus a. Apply Fault at the G82RPHT1 (667085) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G82RPHT1 (667085) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT149 | Single Phase Fault with Stuck Breaker on DEUEL CO 3 (620480) 345 kV Bus a. Apply Fault at the DEUEL CO 3 (620480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEUEL CO 3 (620480) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT150 | Single Phase Fault with Stuck Breaker on ASTORIA 3 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT151 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT152 | Single Phase Fault with Stuck Breaker on DEERCREK-BE3 (659286) 345 kV Bus a. Apply Fault at the DEERCREK-BE3 (659286) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCREK-BE3 (659286) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT153 | Single Phase Fault with Stuck Breaker on BDV 4 (672603) 230 kV Bus a. Apply Fault at the BDV 4 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT154 | Single Phase Fault with Stuck Breaker on SPLT RK7 (603016) 115 kV Bus a. Apply Fault at the SPLT RK7 (603016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT155 | Single Phase Fault with Stuck Breaker on BUFFALO7 (620258) 115 kV Bus a. Apply Fault at the BUFFALO7 (620258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT156 | Single Phase Fault with Stuck Breaker on FORMN 7 (620263) 115 kV Bus a. Apply Fault at the FORMN 7 (620263) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMN 7 (620263) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT157 | Single Phase Fault with Stuck Breaker on BSSOUTH4 (620322) 230 kV Bus a. Apply Fault at the BSSOUTH4 (620322) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT158 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT159 | Single Phase Fault with Stuck Breaker on FARGO 7 (652436) 115 kV Bus a. Apply Fault at the FARGO 7 (652436) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT160 | Single Phase Fault with Stuck Breaker on NUNDRWD7 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT161 | Single Phase Fault with Stuck Breaker on WHITE 7 (652538) 115 kV Bus a. Apply Fault at the WHITE 7 (652538) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT162 | Single Phase Fault with Stuck Breaker on BLAIR-ER8 (655466) 69 kV Bus a. Apply Fault at the BLAIR-ER8 (655466) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER8 (655466) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT163 | Single Phase Fault with Stuck Breaker on PRAIRIE4 (657755) 230 kV Bus a. Apply Fault at the PRAIRIE4 (657755) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25S | Transfer | GROUP1_REGIONAL_P4_FAULT164 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT1 | 3 Phase fault on AURORA 7 115.00 (652474) 115 kV Bus a. Apply fault at the AURORA 7 115.00 (652474) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA 7 (652474) 115.0 kV to FLANDRU7 (652505) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT2 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT3 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT5 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT6 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT7 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT8 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT9 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT10 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT11 | 3 Phase fault on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT12 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT13 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT14 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT15 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT16 | 3 Phase fault on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.2. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT17 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT18 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT19 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT20 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT21 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT22 | 3 Phase fault on CHERRYC7 115.00 (603008) 115 kV Bus a. Apply fault at the CHERRYC7 115.00 (603008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT23 | 3 Phase fault on CHERRYC7 115.00 (603008) 115 kV Bus a. Apply fault at the CHERRYC7 115.00 (603008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT24 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT25 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT26 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN7 (603013) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT27 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN7 (603013) 115.0 kV to CHANRMB7 (603180) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT28 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT29 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT30 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT31 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT32 | 3 Phase fault on WSX FLS7 115.00 (603017) 115 kV Bus a. Apply fault at the WSX FLS7 115.00 (603017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSX FLS7 (603017) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT33 | 3 Phase fault on SOURIS 7 115.00 (603022) 115 kV Bus a. Apply fault at the SOURIS 7 115.00 (603022) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOURIS 7 (603022) 115.0 kV to MAGIC CITY 7 (603270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT34 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT35 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT36 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT37 | 3 Phase fault on MAGIC CITY 7115.00 (603270) 115 kV Bus a. Apply fault at the MAGIC CITY 7115.00 (603270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 7 (603270) 115.0 kV to VELVA TAP (605634) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT38 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT39 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT40 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT41 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT42 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Base | GROUP1_LOCAL_P1_FAULT43 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON 4G (608894), BISON 6G (608896), and BISON1BG (608897). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT43 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON 4G (608894), BISON 6G (608896), and BISON1BG (608897). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT44 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT45 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #8 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT46 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN8 (605215) 69.0 kV to PIPESTN7 (603013) 115.0 kV Two Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT47 | 3 Phase fault on PIPESTN7 115.00 (603013) 115 kV Bus a. Apply fault at the PIPESTN7 115.00 (603013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN8 (605215) 69.0 kV to PIPESTN7 (603013) 115.0 kV Two Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT48 | 3 Phase fault on WSX FLS7 115.00 (603017) 115 kV Bus a. Apply fault at the WSX FLS7 115.00 (603017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSX FLS8 (605207) 69.0 kV to WSX FLS7 (603017) 115.0 kV Two Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT49 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT50 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT51 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT52 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT55 | 3 Phase fault on SPLITRK CAP7115.00 (603228) 115 kV Bus a. Apply fault at the SPLITRK CAP7115.00 (603228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLITRK CAP7 (603228) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT56 | 3 Phase fault on PROSE CAP7 115.00 (603265) 115 kV Bus a. Apply fault at the PROSE CAP7 115.00 (603265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PROSE CAP7 (603265) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT57 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Base | GROUP1_LOCAL_P1_FAULT58 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON 4G (608894), BISON 6G (608896), and BISON1BG (608897). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT58 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON 4G (608894), BISON 6G (608896), and BISON1BG (608897). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT59 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT60 | 3 Phase fault on MINEHAH7 115.00 (603011) 115 kV Bus a. Apply fault at the MINEHAH7 115.00 (603011) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINEHAH7 (603011) 115.0 kV to LAWRENC7 (603012) 115.0 kV Transmission Circuit #1 b.2. MINEHAH7 (603011) 115.0 kV to LINCNCO7 (603014) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT61 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT62 | 3 Phase fault on GRANT 7 115.00 (603009) 115 kV Bus a. Apply fault at the GRANT 7 115.00 (603009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to GRANT 7 (603009) 115.0 kV Transmission Circuit #1 b.2. GRANT 7 (603009) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.3. GRANT (605011) 69.0 kV to GRANT 7 (603009) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT63 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT64 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT65 | 3 Phase fault on BUFFRID7 115.00 (603134) 115 kV Bus a. Apply fault at the BUFFRID7 115.00 (603134) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPESTN7 (603013) 115.0 kV to BUFFRID7 (603134) 115.0 kV Transmission Circuit #1 b.2. BUFLO RDG 2 (605647) 34.5 kV to BUFFRID7 (603134) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT66 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT67 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT68 | 3 Phase fault on ADAMS 5 161.00 (635056) 161 kV Bus a. Apply fault at the ADAMS 5 161.00 (635056) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT70 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips CARROLL W1 (635316), CARROLL W2 (635317), INTRPD W1 (635352), INTRPD W2 (635354), POMEROY W1 (636027), POMEROY W2 (636033), CENTURY W1 (636238), and CENTURY W2 (636239). | Protections were disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT71 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT72 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT73 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT74 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT75 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT76 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT77 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT78 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT79 | 3 Phase fault on MCKSBRG 5 161.00 (635645) 161 kV Bus a. Apply fault at the MCKSBRG 5 161.00 (635645) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCKSBRG 5 (635645) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT80 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT81 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT82 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT83 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT84 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT85 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT86 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT87 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT88 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT89 | 3 Phase fault on 5MARYVB2 161.00 (300097) 161 kV Bus a. Apply fault at the 5MARYVB2 161.00 (300097) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARYVB2 (300097) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT90 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT91 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT92 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT93 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT94 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT95 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT96 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT97 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT98 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT99 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT100 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT101 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT102 | 3 Phase fault on SOURIS 7 115.00 (603022) 115 kV Bus a. Apply fault at the SOURIS 7 115.00 (603022) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOURIS 7 (603022) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT103 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT104 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT105 | 3 Phase fault on E.RUTHVL-CP7115.00 (655655) 115 kV Bus a. Apply fault at the E.RUTHVL-CP7115.00 (655655) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 b.2. E.RUTHVL-CP7 (655655) 115.0 kV to E.RUTHVL-CP9 (655600) 41.6 kV Two Winding #1 b.3. E.RUTHVL-CP7 (655655) 115.0 kV to DUNNING -CP7 (655656) 115.0 kV Transmission Circuit #1 b.4. E.RUTHVL-CP7 (655655) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.5. E.RUTHVL-CP7 (655655) 115.0 kV to RUTHVILL-CP7 (655658) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT106 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT107 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT108 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT109 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT110 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT111 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT112 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT113 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT114 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT115 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT116 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT117 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 b.5. PICKERT8 (657923) 69.0 kV to PICKERT4 (657759) 230.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT118 | 3 Phase fault on PLEASANT LK7115.00 (652446) 115 kV Bus a. Apply fault at the PLEASANT LK7115.00 (652446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.2. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT119 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT120 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT121 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT122 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT123 | 3 Phase fault on MAPLETAP-LO7115.00 (659716) 115 kV Bus a. Apply fault at the MAPLETAP-LO7115.00 (659716) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL7 (652524) 115.0 kV to MAPLETAP-LO7 (659716) 115.0 kV Transmission Circuit #1 b.2. MAPLE ST-ER7 (655409) 115.0 kV to MAPLETAP-LO7 (659716) 115.0 kV Transmission Circuit #1 b.3. MAPLETAP-LO7 (659716) 115.0 kV to STATELIN-LO7 (659717) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT124 | 3 Phase fault on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENASTON-BE7 (659308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT125 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT126 | 3 Phase fault on ALLISNTP-LO869.000 (659702) 69 kV Bus a. Apply fault at the ALLISNTP-LO869.000 (659702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPRKTP-LO8 (659700) 69.0 kV to ALLISNTP-LO8 (659702) 69.0 kV Transmission Circuit #1 b.2. ALLISNTP-LO8 (659702) 69.0 kV to ALLISON -LO8 (659703) 69.0 kV Transmission Circuit #1 b.3. ALLISNTP-LO8 (659702) 69.0 kV to MAYCITY -LO8 (659704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT127 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT129 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT130 | 3 Phase fault on RUGBY TP-CP7115.00 (655665) 115 kV Bus a. Apply fault at the RUGBY TP-CP7115.00 (655665) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #z b.2. ROLETTE_-CP7 (655609) 115.0 kV to THORNE -CP7 (655649) 115.0 kV Transmission Circuit #1 b.3. ROLETTE_-CP7 (655609) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 b.4. RUGBY -CP7 (655654) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT131 | 3 Phase fault on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT132 | 3 Phase fault on ROYAL 8 69.000 (630010) 69 kV Bus a. Apply fault at the ROYAL 8 69.000 (630010) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROYAL 8 (630010) 69.0 kV to CORNLLTA8 (656433) 69.0 kV Transmission Circuit #1 b.2. ROYAL 8 (630010) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT133 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT134 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT135 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT136 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT137 | 3 Phase fault on TWIN CH8 69.000 (640388) 69 kV Bus a. Apply fault at the TWIN CH8 69.000 (640388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT138 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT139 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT140 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT141 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT142 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT143 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT144 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw units (541546, 541549 and 541550). | Protection at Outlaw was disabled with no impact on system stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT145 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT146 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection was disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT147 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT148 | 3 Phase fault on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT149 | 3 Phase fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT150 | 3 Phase fault on MITCHELL 7115.00 (660004) 115 kV Bus a. Apply fault at the MITCHELL 7115.00 (660004) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MITCHELL 7 (660004) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT151 | 3 Phase fault on MITCHELL 7115.00 (660004) 115 kV Bus a. Apply fault at the MITCHELL 7115.00 (660004) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT152 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT153 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips CARROLL W1 (635316), CARROLL W2 (635317), INTRPD W1 (635352), INTRPD W2 (635354), POMEROY W1 (636027), POMEROY W2 (636033), CENTURY W1 (636238), and CENTURY W2 (636239). | Protections were disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT154 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT155 | 3 Phase fault on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT156 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT157 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT158 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT159 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT160 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT161 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT162 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT163 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT164 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT165 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips CARROLL W1 (635316), CARROLL W2 (635317), INTRPD W1 (635352), INTRPD W2 (635354), POMEROY W1 (636027), POMEROY W2 (636033), CENTURY W1 (636238), and CENTURY W2 (636239). | Protections were disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT166 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT167 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT168 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT169 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT170 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT171 | 3 Phase fault on PALERMO -MW7115.00 (655916) 115 kV Bus a. Apply fault at the PALERMO -MW7115.00 (655916) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT172 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT173 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT174 | 3 Phase fault on ROSEGLEN-CP7115.00 (655662) 115 kV Bus a. Apply fault at the ROSEGLEN-CP7115.00 (655662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLS.C-CP7 (655661) 115.0 kV to ROSEGLEN-CP7 (655662) 115.0 kV Transmission Circuit #1 b.2. ROSEGLEN-CP7 (655662) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.3. RAUB TAP-CP7 (655663) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.4. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT175 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT176 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT177 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT178 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT179 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT180 | 3 Phase fault on K424SANB-NI869.000 (659958) 69 kV Bus a. Apply fault at the K424SANB-NI869.000 (659958) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVERLYN8 (630028) 69.0 kV to SPENCER8 (652581) 69.0 kV Transmission Circuit #1 b.2. EVERLYN8 (630028) 69.0 kV to K409HRTM-NI8 (659960) 69.0 kV Transmission Circuit #1 b.3. SANBORNMUNI8 (658908) 69.0 kV to M5SANBOR-NI8 (659892) 69.0 kV Transmission Circuit #1 b.4. M5SANBOR-NI8 (659892) 69.0 kV to K424SANB-NI8 (659958) 69.0 kV Transmission Circuit #1 b.5. J2______-NI8 (659908) 69.0 kV to K424SANB-NI8 (659958) 69.0 kV Transmission Circuit #1 b.6. K424SANB-NI8 (659958) 69.0 kV to K417HART-NI8 (659959) 69.0 kV Transmission Circuit #1 b.7. K417HART-NI8 (659959) 69.0 kV to K409HRTM-NI8 (659960) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT181 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT182 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT183 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT184 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT185 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT186 | 3 Phase fault on GARRISN7 115 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV Load #BB b.2. GARRISN7 (652442) 115.0 kV Load #BW b.3. GARRISN7 (652442) 115.0 kV Load #R0 b.4. GARRISN7 (652442) 115.0 kV Load #W0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT187 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protections were disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT188 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT189 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT190 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT191 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT193 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT194 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT195 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT196 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT197 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT198 | 3 Phase fault on CAROL S8 69.000 (635322) 69 kV Bus a. Apply fault at the CAROL S8 69.000 (635322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROL S8 (635322) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT199 | 3 Phase fault on TEMPLTN8 69.000 (635325) 69 kV Bus a. Apply fault at the TEMPLTN8 69.000 (635325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTN8 (635325) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT200 | 3 Phase fault on MIDAMER8 69.000 (635373) 69 kV Bus a. Apply fault at the MIDAMER8 69.000 (635373) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDAMER8 (635373) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT201 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT202 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT203 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT204 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT205 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT206 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT207 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT208 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT209 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT210 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT211 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT212 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT213 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT214 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT215 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT216 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT217 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT218 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT219 | 3 Phase fault on SIOUXFL8 69.000 (652235) 69 kV Bus a. Apply fault at the SIOUXFL8 69.000 (652235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL8 (652235) 69.0 kV to SW101-ER8 (655011) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT220 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT221 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT222 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT223 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT224 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT225 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT226 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT227 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT228 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON 4G (608894), BISON 6G (608896), and BISON1BG (608897). | Protections were disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT229 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON 4G (608894), BISON 6G (608896), and BISON1BG (608897). | Protections were disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT230 | 3 Phase fault on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT231 | 3 Phase fault on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT232 | 3 Phase fault on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT233 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT234 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV to MANNING-ER7 (655478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT235 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT236 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV to HOLLAND -LO7 (659733) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT237 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT238 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT239 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT240 | 3 Phase fault on SIOUXFL7 115.00 (652524) 115 kV Bus a. Apply fault at the SIOUXFL7 115.00 (652524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL7 (652524) 115.0 kV to SW1145-ER7 (655377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT241 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT242 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT243 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT244 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT245 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT246 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT247 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT248 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT249 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT250 | 3 Phase fault on SPENCER8 69.000 (652581) 69 kV Bus a. Apply fault at the SPENCER8 69.000 (652581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER8 (652581) 69.0 kV to SPNCRSJCT8 (656555) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT251 | 3 Phase fault on SPENCER8 69.000 (652581) 69 kV Bus a. Apply fault at the SPENCER8 69.000 (652581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER8 (652581) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT252 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT253 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT254 | 3 Phase fault on LETCHER7 115.00 (652609) 115 kV Bus a. Apply fault at the LETCHER7 115.00 (652609) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT255 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to FREEMAN-ER7 (655418) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT256 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT257 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT258 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT259 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT260 | 3 Phase fault on MOS-CNTN-ER869.000 (655142) 69 kV Bus a. Apply fault at the MOS-CNTN-ER869.000 (655142) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CNTN-ER8 (655142) 69.0 kV to TEA-ER8 (655322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT261 | 3 Phase fault on MOS-PARK-ER869.000 (655143) 69 kV Bus a. Apply fault at the MOS-PARK-ER869.000 (655143) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-PARK-ER8 (655143) 69.0 kV to PARKER-ER8 (655192) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT262 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT263 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT264 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT265 | 3 Phase fault on SW1145-ER7 115.00 (655377) 115 kV Bus a. Apply fault at the SW1145-ER7 115.00 (655377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW1145-ER7 (655377) 115.0 kV to SW167 -ER7 (655413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT266 | 3 Phase fault on HRRISBRG-ER7115.00 (655404) 115 kV Bus a. Apply fault at the HRRISBRG-ER7115.00 (655404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HRRISBRG-ER7 (655404) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT267 | 3 Phase fault on SXFCHCLR-ER7115.00 (655408) 115 kV Bus a. Apply fault at the SXFCHCLR-ER7115.00 (655408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT268 | 3 Phase fault on BUCKSNRT-ER7115.00 (655441) 115 kV Bus a. Apply fault at the BUCKSNRT-ER7115.00 (655441) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT269 | 3 Phase fault on BUCKSNRT-ER7115.00 (655441) 115 kV Bus a. Apply fault at the BUCKSNRT-ER7115.00 (655441) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT270 | 3 Phase fault on DELAPRE-ER7 115.00 (655444) 115 kV Bus a. Apply fault at the DELAPRE-ER7 115.00 (655444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT271 | 3 Phase fault on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT272 | 3 Phase fault on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT273 | 3 Phase fault on VFODNES-ER7 115.00 (655468) 115 kV Bus a. Apply fault at the VFODNES-ER7 115.00 (655468) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT274 | 3 Phase fault on BERTHOLD-CP7115.00 (655641) 115 kV Bus a. Apply fault at the BERTHOLD-CP7115.00 (655641) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT275 | 3 Phase fault on BERTHOLD-CP7115.00 (655641) 115 kV Bus a. Apply fault at the BERTHOLD-CP7115.00 (655641) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT276 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT277 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT278 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT279 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT280 | 3 Phase fault on PARSHALL-MW7115.00 (655908) 115 kV Bus a. Apply fault at the PARSHALL-MW7115.00 (655908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSHALL-MW7 (655908) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT281 | 3 Phase fault on STANLEY -MW7115.00 (655917) 115 kV Bus a. Apply fault at the STANLEY -MW7115.00 (655917) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANLEY -MW7 (655917) 115.0 kV to LOSTWD_T-MW7 (655950) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT282 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV to BLAISDEL-MW7 (655949) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT283 | 3 Phase fault on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Base | GROUP1_LOCAL_P1_FAULT284 | 3 Phase fault on CAROLTON8 69.000 (656233) 69 kV Bus a. Apply fault at the CAROLTON8 69.000 (656233) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTON8 (656233) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Violation of the damping factor criteria was observed at COONRPDS (656237) | Reduce clearing time to 3.5 cycles
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT284 | 3 Phase fault on CAROLTON8 69.000 (656233) 69 kV Bus a. Apply fault at the CAROLTON8 69.000 (656233) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTON8 (656233) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Violation of the damping factor criteria was observed at COONRPDS (656237). Issue is also observed in the base case. | Reduce clearing time to 3.5 cycles
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT285 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT286 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT287 | 3 Phase fault on INDUSTRI8 69.000 (656493) 69 kV Bus a. Apply fault at the INDUSTRI8 69.000 (656493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDUSTRI8 (656493) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT288 | 3 Phase fault on SPNCRSJCT8 69.000 (656555) 69 kV Bus a. Apply fault at the SPNCRSJCT8 69.000 (656555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNCRSJCT8 (656555) 69.0 kV to SPENCERW8 (656609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT289 | 3 Phase fault on SPNCRSJCT8 69.000 (656555) 69 kV Bus a. Apply fault at the SPNCRSJCT8 69.000 (656555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNCRSJCT8 (656555) 69.0 kV to SPENCERS8 (656611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT290 | 3 Phase fault on WISDMJCT8 69.000 (656571) 69 kV Bus a. Apply fault at the WISDMJCT8 69.000 (656571) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WISDMJCT8 (656571) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT291 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT292 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT293 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT294 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT295 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT296 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT297 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT298 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT299 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT300 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT301 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT302 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Base | GROUP1_LOCAL_P1_FAULT303 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT303 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT304 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT305 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT306 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT307 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT308 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT309 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT310 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT311 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT312 | 3 Phase fault on K126MEC -NI869.000 (659852) 69 kV Bus a. Apply fault at the K126MEC -NI869.000 (659852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K126MEC -NI8 (659852) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT313 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT314 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT315 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT316 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT317 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT318 | 3 Phase fault on K308EARL-NI869.000 (659856) 69 kV Bus a. Apply fault at the K308EARL-NI869.000 (659856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K308EARL-NI8 (659856) 69.0 kV to K321MEC -NI8 (659857) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT319 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT320 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT321 | 3 Phase fault on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT322 | 3 Phase fault on K319EWOL-NI869.000 (659867) 69 kV Bus a. Apply fault at the K319EWOL-NI869.000 (659867) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K319EWOL-NI8 (659867) 69.0 kV to L9 MANNI-NI8 (659868) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT323 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT324 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT325 | 3 Phase fault on K326OTTE-NI869.000 (659886) 69 kV Bus a. Apply fault at the K326OTTE-NI869.000 (659886) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K326OTTE-NI8 (659886) 69.0 kV to K333SCHL-NI8 (659887) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT326 | 3 Phase fault on K333SCHL-NI869.000 (659887) 69 kV Bus a. Apply fault at the K333SCHL-NI869.000 (659887) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K333SCHL-NI8 (659887) 69.0 kV to K337ARTH-NI8 (659888) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT327 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT328 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT329 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT330 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT331 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT332 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT333 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT334 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT335 | 3 Phase fault on K105UTE_-NI869.000 (659998) 69 kV Bus a. Apply fault at the K105UTE_-NI869.000 (659998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K105UTE_-NI8 (659998) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Base | GROUP1_LOCAL_P1_FAULT336 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT336 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protections were disabled with no impact to stability. Reclosing was removed due to simulation crashes.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT337 | 3 Phase fault on MAGIC CITY 4230.00 (602052) 230 kV Bus a. Apply fault at the MAGIC CITY 4230.00 (602052) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to MAGIC CITY 7 (603270) 115.0 kV to MAGIC CTY T9 (605787) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT338 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT339 | 3 Phase fault on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV to RUGBY T (620179) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT340 | 3 Phase fault on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV to RUGBY T2 (620479) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT341 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT342 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSONG (640164) 69.0 kV to EMERSON7 (640163) 115.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT343 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT344 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT345 | 3 Phase fault on S.SIOUXCITY7115.00 (640424) 115 kV Bus a. Apply fault at the S.SIOUXCITY7115.00 (640424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.SIOUXCITY8 (640425) 69.0 kV to S.SIOUXCITY7 (640424) 115.0 kV to S.SIOUXCYT19 (643170) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT346 | 3 Phase fault on SIOUXFL7 115.00 (652524) 115 kV Bus a. Apply fault at the SIOUXFL7 115.00 (652524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL8 (652235) 69.0 kV to SIOUXFL7 (652524) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT347 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT348 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT349 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT350 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT351 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON 4G (608894), BISON 6G (608896), and BISON1BG (608897). | Protections were disabled with no impact to stability.
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT352 | 3 Phase fault on BERSFRD7 115.00 (652502) 115 kV Bus a. Apply fault at the BERSFRD7 115.00 (652502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERSFRD7 (652502) 115.0 kV to BERSFRD8 (652254) 69.0 kV to BERSFR19 (652255) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT353 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV to FLANDRU8 (652229) 69.0 kV to FLANDR19 (652227) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT354 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT355 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT356 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT357 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to HANLON1-ER8 (655494) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT358 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to HANLON2-ER8 (655495) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT359 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to HANLON-ER7 (655493) 115.0 kV to HANLON 9 (652592) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT360 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT361 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT362 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT363 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT364 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT366 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT367 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT368 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT369 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT370 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT371 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT372 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT373 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT374 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT375 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT376 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT377 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT378 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT379 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT380 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT381 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT382 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT383 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT384 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT385 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT386 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT387 | 3 Phase fault on BDV 4230.00 (672603) 230 kV Bus a. Apply fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT388 | 3 Phase fault on FALLS 7 115.00 (603225) 115 kV Bus a. Apply fault at the FALLS 7 115.00 (603225) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FALLS 7 (603225) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT389 | 3 Phase fault on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUGBY 7 (652452) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT390 | 3 Phase fault on FLANDRU7 115.00 (652505) 115 kV Bus a. Apply fault at the FLANDRU7 115.00 (652505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLANDRU7 (652505) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT391 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT392 | 3 Phase fault on WISDOM G 69.000 (656573) 69 kV Bus a. Apply fault at the WISDOM G 69.000 (656573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WISDOM G (656573) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT393 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations observed in the power output of GARISN5G (652461) and GARISN4G (652460). | Operational measures fixing the voltages setpoint at GARISN4G and GARISN5G
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P1_FAULT394 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT3 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT4 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT5 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT6 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT7 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT8 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT9 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT10 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT11 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT12 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT13 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT14 | 3 Phase fault on CNTSHNT3 345.00 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 345.00 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT15 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT16 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT17 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT18 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT19 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT20 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT21 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT22 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT23 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT24 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT25 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT26 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT27 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT28 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT29 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT30 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT31 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT32 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT33 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT34 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT35 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT36 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT37 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT38 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT39 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT40 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT41 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT42 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT43 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P1_FAULT44 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT1 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT2 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT3 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.6. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT4 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT5 | Single Phase Fault with Stuck Breaker on SOURIS 7 115.00 (603022) 115 kV Bus a. Apply Fault at the SOURIS 7 115.00 (603022) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOURIS 7 (603022) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 b.2. SOURIS 7 (603022) 115.0 kV to MAGIC CITY 7 (603270) 115.0 kV Transmission Circuit #1 b.3. MAGIC CITY 7 (603270) 115.0 kV to VELVA TAP (605634) 115.0 kV Transmission Circuit #1 b.4. VELVA TAP (605634) 115.0 kV to VELVA FDR2 (605633) 34.5 kV Two Winding #1 b.5. VELVA TAP (605634) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT6 | Single Phase Fault with Stuck Breaker on MALLARD7 115.00 (603023) 115 kV Bus a. Apply Fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOURIS 7 (603022) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 b.2. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.3. MALLARD7 (603023) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.4. MALLARD7 (603023) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 b.5. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 b.6. MALLARD1-CP9 (655603) 41.6 kV to MALLARD7 (603023) 115.0 kV Two Winding #1 b.7. MALLARD2-CP9 (655604) 41.6 kV to MALLARD7 (603023) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT7 | Single Phase Fault with Stuck Breaker on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply Fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. PIPESTN7 (603013) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.3. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT8 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 b.4. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT9 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.4. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT10 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT11 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT12 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT13 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (635226) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (635226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT14 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT15 | Single Phase Fault with Stuck Breaker on LEMARS S 5 161.00 (635261) 161 kV Bus a. Apply Fault at the LEMARS S 5 161.00 (635261) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.4. LEMARS S 5 (635261) 161.0 kV to LEMARS S 8 (635262) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT16 | Single Phase Fault with Stuck Breaker on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply Fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.4. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.5. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT17 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT18 | Single Phase Fault with Stuck Breaker on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply Fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.4. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT19 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT20 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT21 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT22 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT23 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT24 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.5. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.7. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.8. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.9. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.10. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT25 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT26 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT27 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT28 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.2. SIOUXFL8 (652235) 69.0 kV to SIOUXFL7 (652524) 115.0 kV Two Winding #1 b.3. SIOUXFL8 (652235) 69.0 kV to SW101-ER8 (655011) 69.0 kV Transmission Circuit #1 b.4. FLANDRU7 (652505) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.5. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT29 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERSFRD7 (652502) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.2. BRANDON-ER7 (655400) 115.0 kV to ROWENA-ER7 (655401) 115.0 kV Transmission Circuit #1 b.3. BRANDON-ER7 (655400) 115.0 kV to SW1116 -ER7 (655414) 115.0 kV Transmission Circuit #1 b.4. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT30 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT31 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT32 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT33 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT34 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT35 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT36 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT37 | Single Phase Fault with Stuck Breaker on HANLON 4 230.00 (652513) 230 kV Bus a. Apply Fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to HANLON1-ER8 (655494) 69.0 kV Two Winding #1 b.3. HANLON 4 (652513) 230.0 kV to HANLON2-ER8 (655495) 69.0 kV Two Winding #1 b.4. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.5. SW124-ER8 (655019) 69.0 kV to HANLON1-ER8 (655494) 69.0 kV Transmission Circuit #1 b.6. SW130-ER8 (655020) 69.0 kV to HANLON1-ER8 (655494) 69.0 kV Transmission Circuit #1 b.7. SW159-ER8 (655026) 69.0 kV to HANLON1-ER8 (655494) 69.0 kV Transmission Circuit #1 b.8. HANLON1-ER8 (655494) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #z b.9. HANLON 4 (652513) 230.0 kV to HANLON-ER7 (655493) 115.0 kV to HANLON 9 (652592) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT38 | Single Phase Fault with Stuck Breaker on HANLON 4 230.00 (652513) 230 kV Bus a. Apply Fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to HANLON1-ER8 (655494) 69.0 kV Two Winding #1 b.3. HANLON 4 (652513) 230.0 kV to HANLON2-ER8 (655495) 69.0 kV Two Winding #1 b.4. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.5. SW145-ER8 (655023) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #1 b.6. SW1142-ER8 (655166) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #1 b.7. MOS-LKV2-ER8 (655226) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #1 b.8. HANLON1-ER8 (655494) 69.0 kV to HANLON2-ER8 (655495) 69.0 kV Transmission Circuit #z b.9. HANLON 4 (652513) 230.0 kV to HANLON-ER7 (655493) 115.0 kV to HANLON 9 (652592) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT39 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT40 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT41 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT42 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT43 | Single Phase Fault with Stuck Breaker on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply Fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT44 | Single Phase Fault with Stuck Breaker on GU CTR 5 161.00 (631072) 161 kV Bus a. Apply Fault at the GU CTR 5 161.00 (631072) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.5. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.6. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.7. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.8. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.9. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. SCRANTN5 (631071) 161.0 kV to SCRANTN9 (629111) 34.5 kV Two Winding #1 b.11. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.12. SCRANTN5 (631071) 161.0 kV to GR JCT 5 (631074) 161.0 kV Transmission Circuit #1 b.13. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT45 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT46 | Single Phase Fault with Stuck Breaker on ONEILL 7 115.00 (640305) 115 kV Bus a. Apply Fault at the ONEILL 7 115.00 (640305) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 b.2. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.3. ONEILL 7 (640305) 115.0 kV to EAGLECREEK 7 (640465) 115.0 kV Transmission Circuit #1 b.4. ONEILL 7 (640305) 115.0 kV to ONEILL 8 (640306) 69.0 kV to ONEILL T1 9 (643117) 13.8 kV Three Winding #1 b.5. ONEILL 7 (640305) 115.0 kV to ONEILL 8 (640306) 69.0 kV to ONEILL T2 9 (643118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT47 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT48 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT49 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT50 | Single Phase Fault with Stuck Breaker on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply Fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. GAVINS 7 (652511) 115.0 kV to GAVINS1G (652575) 13.2 kV Two Winding #1 b.4. GAVINS 7 (652511) 115.0 kV to GAVINS2G (652576) 13.2 kV Two Winding #1 b.5. GAVINS 7 (652511) 115.0 kV to GAVINS3G (652577) 13.2 kV Two Winding #1 b.6. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 b.7. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT51 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.6. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT52 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT53 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT54 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT55 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERSFRD7 (652502) 115.0 kV to SIOUXFL7 (652524) 115.0 kV Transmission Circuit #1 b.2. SIOUXFL7 (652524) 115.0 kV to SW1145-ER7 (655377) 115.0 kV Transmission Circuit #1 b.3. SIOUXFL7 (652524) 115.0 kV to MAPLETAP-LO7 (659716) 115.0 kV Transmission Circuit #1 b.4. BRANDON-ER7 (655400) 115.0 kV to ROWENA-ER7 (655401) 115.0 kV Transmission Circuit #1 b.5. BRANDON-ER7 (655400) 115.0 kV to SW1116 -ER7 (655414) 115.0 kV Transmission Circuit #1 b.6. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT56 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.2. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.3. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.4. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 b.5. VFODNES-ER7 (655468) 115.0 kV to VFODNES4 (652398) 230.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT57 | Single Phase Fault with Stuck Breaker on MITCHELL 7115.00 (660004) 115 kV Bus a. Apply Fault at the MITCHELL 7115.00 (660004) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANT 7 (603009) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.2. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.3. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit #1 b.4. MITCHELL 7 (660004) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 b.5. MIT TRANSMSN (660200) 34.5 kV to MITCHELL 7 (660004) 115.0 kV Two Winding #1 b.6. MIT TRANSMSN (660200) 34.5 kV to MITCHELL 7 (660004) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT58 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT59 | Single Phase Fault with Stuck Breaker on TRIPP JCT 7115.00 (660005) 115 kV Bus a. Apply Fault at the TRIPP JCT 7115.00 (660005) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.2. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit #1 b.3. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.4. TRIPP JCT 7 (660005) 115.0 kV to SCHROEDER 7 (660018) 115.0 kV Transmission Circuit #1 b.5. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding #1 b.6. TRIPP JCT (660221) 34.5 kV to TRIPP JCT 7 (660005) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT60 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT61 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT62 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT63 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT64 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT65 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT66 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT67 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT68 | Single Phase Fault with Stuck Breaker on PLEASANT LK7115.00 (652446) 115 kV Bus a. Apply Fault at the PLEASANT LK7115.00 (652446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 8 (652317) 69.0 kV to LEEDS 7 (652447) 115.0 kV Two Winding #1 b.2. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.3. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT70 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.4. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.5. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT71 | Single Phase Fault with Stuck Breaker on MTVERN 7 115.00 (652518) 115 kV Bus a. Apply Fault at the MTVERN 7 115.00 (652518) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. MTVERNS8 (652251) 69.0 kV to MTVERN 7 (652518) 115.0 kV Two Winding #1 b.4. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.6. MTVERN 7 (652518) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.7. MT VERNON 8 (660252) 69.0 kV to MTVERN 7 (652518) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT72 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT73 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT74 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT75 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT76 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT77 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT78 | Single Phase Fault with Stuck Breaker on SD.PW1__-BE934.500 (659327) 34.5 kV Bus a. Apply Fault at the SD.PW1__-BE934.500 (659327) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT79 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.5. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT80 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding #1 b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT81 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT82 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to VFODNES4 (652398) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding #1 b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT83 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-175TAP (762237) 230.0 kV to VFODNES4 (652398) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT84 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT85 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT86 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. EXIRA 5 (652603) 161.0 kV to EXIRA 2G (658001) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT87 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT88 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT89 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.3. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.8. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT90 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT91 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT92 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 b.7. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT93 | Single Phase Fault with Stuck Breaker on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply Fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.5. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.6. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.7. YNK JCT (660100) 34.5 kV to YANKTON JCT7 (660006) 115.0 kV Two Winding #1 b.8. YNK JCT (660100) 34.5 kV to YANKTON JCT7 (660006) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT94 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT95 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT96 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT97 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT98 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT99 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT100 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT101 | Single Phase Fault with Stuck Breaker on NAPA JCT 7115.00 (660026) 115 kV Bus a. Apply Fault at the NAPA JCT 7115.00 (660026) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.2. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.3. NAPA JCT 7 (660026) 115.0 kV to YANKTONEAST7 (660036) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT102 | Single Phase Fault with Stuck Breaker on BOTINU.W-CP7115.00 (655650) 115 kV Bus a. Apply Fault at the BOTINU.W-CP7115.00 (655650) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOTINU.W-CP7 (655650) 115.0 kV to DUNNING -CP7 (655656) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT103 | Single Phase Fault with Stuck Breaker on DUNNING -CP7115.00 (655656) 115 kV Bus a. Apply Fault at the DUNNING -CP7115.00 (655656) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 b.2. E.RUTHVL-CP7 (655655) 115.0 kV to E.RUTHVL-CP9 (655600) 41.6 kV Two Winding #1 b.3. E.RUTHVL-CP7 (655655) 115.0 kV to DUNNING -CP7 (655656) 115.0 kV Transmission Circuit #1 b.4. E.RUTHVL-CP7 (655655) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.5. E.RUTHVL-CP7 (655655) 115.0 kV to RUTHVILL-CP7 (655658) 115.0 kV Transmission Circuit #1 b.6. DUNNING -CP7 (655656) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT104 | Single Phase Fault with Stuck Breaker on DUNNING -CP7115.00 (655656) 115 kV Bus a. Apply Fault at the DUNNING -CP7115.00 (655656) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNNING -CP7 (655656) 115.0 kV to DUNNING2-CP8 (655678) 60.0 kV Two Winding #1 b.2. DUNNING -CP7 (655656) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT105 | Single Phase Fault with Stuck Breaker on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply Fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.2. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.3. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 b.4. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT106 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT107 | Single Phase Fault with Stuck Breaker on PALERMO -MW7115.00 (655916) 115 kV Bus a. Apply Fault at the PALERMO -MW7115.00 (655916) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.4. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT108 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.4. BLAISDEL-BE7 (659144) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT109 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 b.2. LGN.KW1A-BE9 (659208) 13.8 kV to LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT110 | Single Phase Fault with Stuck Breaker on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply Fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LGN.KW1A-BE9 (659208) 13.8 kV to LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV Three Winding #1 b.2. LOGAN___-BE7 (659155) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT111 | Single Phase Fault with Stuck Breaker on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply Fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.2. E.RUTHVL-CP7 (655655) 115.0 kV to SW.MINOT-CP7 (655657) 115.0 kV Transmission Circuit #1 b.3. SW.MINOT-CP7 (655657) 115.0 kV to SW.MNOT1-CP9 (655605) 41.6 kV Two Winding #1 b.4. SW.MINOT-CP7 (655657) 115.0 kV to SW.MNOT2-CP9 (655606) 41.6 kV Two Winding #2 b.5. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT112 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT113 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. BROOKS 5 (635037) 161.0 kV to ADAMS 5 (635056) 161.0 kV Transmission Circuit #1 b.5. ADAMS 5 (635056) 161.0 kV to ADAMS B1 9 (635057) 34.5 kV Two Winding #1 b.6. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.7. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT114 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT115 | Single Phase Fault with Stuck Breaker on AGATE -CP7115.00 (655616) 115 kV Bus a. Apply Fault at the AGATE -CP7115.00 (655616) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.2. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.3. LEEDS 7 (652447) 115.0 kV to AGATE -CP7 (655616) 115.0 kV Transmission Circuit #1 b.4. ROLLA___-CP7 (655614) 115.0 kV to AGATE -CP7 (655616) 115.0 kV Transmission Circuit #1 b.5. AGATE -CP7 (655616) 115.0 kV to AGATE -CP8 (655617) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT116 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFALLS-ER7 (655439) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit #z b.2. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit #1 b.3. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.4. SUNDOWN-ER7 (655445) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit #1 b.5. VFODNES1-ER9 (655470) 12.5 kV to VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT117 | Single Phase Fault with Stuck Breaker on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply Fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to WALLLK-ER7 (655447) 115.0 kV Transmission Circuit #1 b.2. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 b.3. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit #1 b.4. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit #1 b.5. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT118 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT119 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT120 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT121 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT122 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT123 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT124 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT125 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT126 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT127 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT128 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT129 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT130 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT131 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT132 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT133 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT134 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT135 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (655690) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (655690) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to Load #BW b.7. GARRISN7 (652442) 115.0 kV to Load #R0 b.8. GARRISN7 (652442) 115.0 kV to Load #W0 b.9. GARRISN7 (652442) 115.0 kV to Load #BB | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT136 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT137 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT138 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT139 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT140 | Single Phase Fault with Stuck Breaker on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply Fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.2. RUGBY 9 (652324) 41.8 kV to RUGBY 7 (652452) 115.0 kV Two Winding #1 b.3. PLEASANT LK7 (652446) 115.0 kV to LEEDS 7 (652447) 115.0 kV Transmission Circuit #1 b.4. PLEASANT LK7 (652446) 115.0 kV to RUGBY 7 (652452) 115.0 kV Transmission Circuit #1 b.5. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.6. RUGBY 7 (652452) 115.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Transmission Circuit #1 b.7. RUGBY 7 (652452) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #z b.8. ROLETTE_-CP7 (655609) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 b.9. RUGBY -CP7 (655654) 115.0 kV to RUGBY TP-CP7 (655665) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT141 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT142 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT143 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT144 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT145 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT146 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT147 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT148 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT149 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT150 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT151 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT152 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH8 (635224) 69.0 kV to PLYMOTH5 (635223) 161.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 b.2. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT153 | Single Phase Fault with Stuck Breaker on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply Fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT154 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT155 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT156 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT157 | Single Phase Fault with Stuck Breaker on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY8 (652574) 69.0 kV to SIOUXCY5 (652566) 161.0 kV Two Winding #1 b.2. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT158 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. DENISON8 (652583) 69.0 kV to DENISON4 (652567) 230.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT159 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to UTICAJC4 (652526) 230.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT160 | Single Phase Fault with Stuck Breaker on MOS-PARK-ER869.000 (655143) 69 kV Bus a. Apply Fault at the MOS-PARK-ER869.000 (655143) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-PARK-ER8 (655143) 69.0 kV to MOS-HRLM-ER8 (655105) 69.0 kV Transmission Circuit #1 b.2. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT161 | Single Phase Fault with Stuck Breaker on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply Fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA -MW7 (655944) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.2. PLAZA -MW7 (655944) 115.0 kV to PARSHALL-MW7 (655908) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT162 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT163 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT164 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. J6BOYER_-NI8 (659912) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT165 | Single Phase Fault with Stuck Breaker on J12_____-NI869.000 (659918) 69 kV Bus a. Apply Fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J12_____-NI8 (659918) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. J12_____-NI8 (659918) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT166 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT167 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT168 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 b.2. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT169 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT170 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT171 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT172 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT173 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY2 (652552) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT174 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT175 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT176 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT177 | Single Phase Fault with Stuck Breaker on RUGBY 7 115.00 (652452) 115 kV Bus a. Apply Fault at the RUGBY 7 115.00 (652452) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to PLEASANT LK7 (652446) 115.0 kV Transmission Circuit #1 b.2. RUGBY 7 (652452) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT178 | Single Phase Fault with Stuck Breaker on BONESTL7 115.00 (652475) 115 kV Bus a. Apply Fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT179 | Single Phase Fault with Stuck Breaker on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply Fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT180 | Single Phase Fault with Stuck Breaker on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply Fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 b.2. SW.MINOT-CP7 (655657) 115.0 kV to E.RUTHVL-CP7 (655655) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT181 | Single Phase Fault with Stuck Breaker on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply Fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT182 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT183 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT184 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT185 | Single Phase Fault with Stuck Breaker on DENSOUMAIN8 69.000 (658031) 69 kV Bus a. Apply Fault at the DENSOUMAIN8 69.000 (658031) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENSOUMAIN8 (658031) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENSOUMAIN8 (658031) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT186 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT187 | Single Phase Fault with Stuck Breaker on TOYNE8 69.000 (656249) 69 kV Bus a. Apply Fault at the TOYNE8 69.000 (656249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOYNE8 (656249) 69.0 kV to TEMPLTON8 (656247) 69.0 kV Transmission Circuit #1 b.2. TOYNE8 (656249) 69.0 kV to CAROL S8 (635322) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT188 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT189 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT190 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL7 (652524) 115.0 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 b.2. SIOUXFL7 (652524) 115.0 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT191 | Single Phase Fault with Stuck Breaker on SPENCER8 69.000 (652581) 69 kV Bus a. Apply Fault at the SPENCER8 69.000 (652581) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER8 (652581) 69.0 kV to WISDOM G (656573) 69.0 kV Transmission Circuit #1 b.2. SPENCER8 (652581) 69.0 kV to EVERLYN8 (630028) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT192 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT193 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to PLYMOTH5 (635223) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT194 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT195 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT196 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT197 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT198 | Single Phase Fault with Stuck Breaker on UTICAJC7 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT199 | Single Phase Fault with Stuck Breaker on RASMUSN-ER8 (655485) 69 kV Bus a. Apply Fault at the RASMUSN-ER8 (655485) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RASMUSN-ER8 (655485) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT200 | Single Phase Fault with Stuck Breaker on VFODNES4 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT201 | Single Phase Fault with Stuck Breaker on SIOUXFL4 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT202 | Single Phase Fault with Stuck Breaker on SIOUXFL7 (652524) 115 kV Bus a. Apply Fault at the SIOUXFL7 (652524) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL7 (652524) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT203 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT204 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT205 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT206 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT207 | Single Phase Fault with Stuck Breaker on SW.MINOT-CP7 (655657) 115 kV Bus a. Apply Fault at the SW.MINOT-CP7 (655657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT208 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT209 | Single Phase Fault with Stuck Breaker on DENISON8 (652583) 69 kV Bus a. Apply Fault at the DENISON8 (652583) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT210 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI8 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI8 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT211 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT212 | Single Phase Fault with Stuck Breaker on SIOUXCY5 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT213 | Single Phase Fault with Stuck Breaker on PLYMOTH5 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT214 | Single Phase Fault with Stuck Breaker on SPENCER5 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT215 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT216 | Single Phase Fault with Stuck Breaker on SIOUXCY2 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_LOCAL_P4_FAULT217 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT1 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT2 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT3 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT5 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT6 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT7 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT8 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT9 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT10 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT11 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT12 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT13 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT14 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT15 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT16 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT17 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT18 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT19 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT20 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT21 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT22 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT23 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT24 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT25 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT26 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT27 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT28 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT29 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT30 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT31 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT32 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT33 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT34 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT35 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT36 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT37 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT38 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT39 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT40 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to HRDLKGEN (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT41 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT42 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT43 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT44 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT45 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT46 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT47 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT48 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT49 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT50 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT51 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT52 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT53 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT54 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT55 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT56 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT57 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT58 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT59 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT60 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT61 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT62 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT63 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT64 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT65 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT66 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT67 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT68 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT70 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT71 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT72 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT73 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT74 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT75 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT76 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT77 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT78 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT79 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT80 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT81 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT82 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT83 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT84 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT85 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT86 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT87 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT88 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT89 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT90 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT91 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT92 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT93 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT94 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT95 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT96 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT97 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT98 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT99 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT100 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT101 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT102 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT103 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT104 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT105 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT106 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT107 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT108 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT109 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT110 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT111 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT112 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT113 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT114 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 b.2. FORMAN 4 (620363) 230.0 kV to HANKSON4 (620327) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT115 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT116 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT117 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT118 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT119 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT120 | Single Phase Fault with Stuck Breaker on G82RPHT1 230.00 (667085) 230 kV Bus a. Apply Fault at the G82RPHT1 230.00 (667085) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G82RPHT1 (667085) 230.0 kV to GLENBOR4 (667052) 230.0 kV Transmission Circuit #1 b.2. G82RPHT1 (667085) 230.0 kV to PEACE GARD 5 (602057) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT121 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT122 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT123 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT124 | Single Phase Fault with Stuck Breaker on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply Fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z b.2. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT125 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT126 | Single Phase Fault with Stuck Breaker on BSSOUTH4 230.00 (620322) 230 kV Bus a. Apply Fault at the BSSOUTH4 230.00 (620322) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #2 b.2. BSSOUTH4 (620322) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT127 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT128 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT129 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT130 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 b.2. WHITE 7 (652538) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT131 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.2. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT132 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT133 | Single Phase Fault with Stuck Breaker on J748POI (87487) 345 kV Bus a. Apply Fault at the J748POI (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT134 | Single Phase Fault with Stuck Breaker on PEACE GARD 5 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT135 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT136 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT137 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT138 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT139 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT140 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT141 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT142 | Single Phase Fault with Stuck Breaker on FORMAN 4 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT143 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT144 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT145 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT146 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT147 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT148 | Single Phase Fault with Stuck Breaker on G82RPHT1 (667085) 230 kV Bus a. Apply Fault at the G82RPHT1 (667085) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G82RPHT1 (667085) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT149 | Single Phase Fault with Stuck Breaker on DEUEL CO 3 (620480) 345 kV Bus a. Apply Fault at the DEUEL CO 3 (620480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEUEL CO 3 (620480) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT150 | Single Phase Fault with Stuck Breaker on ASTORIA 3 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT151 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT152 | Single Phase Fault with Stuck Breaker on DEERCREK-BE3 (659286) 345 kV Bus a. Apply Fault at the DEERCREK-BE3 (659286) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCREK-BE3 (659286) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT153 | Single Phase Fault with Stuck Breaker on BDV 4 (672603) 230 kV Bus a. Apply Fault at the BDV 4 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT154 | Single Phase Fault with Stuck Breaker on SPLT RK7 (603016) 115 kV Bus a. Apply Fault at the SPLT RK7 (603016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT155 | Single Phase Fault with Stuck Breaker on BUFFALO7 (620258) 115 kV Bus a. Apply Fault at the BUFFALO7 (620258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT156 | Single Phase Fault with Stuck Breaker on FORMN 7 (620263) 115 kV Bus a. Apply Fault at the FORMN 7 (620263) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMN 7 (620263) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT157 | Single Phase Fault with Stuck Breaker on BSSOUTH4 (620322) 230 kV Bus a. Apply Fault at the BSSOUTH4 (620322) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT158 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT159 | Single Phase Fault with Stuck Breaker on FARGO 7 (652436) 115 kV Bus a. Apply Fault at the FARGO 7 (652436) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT160 | Single Phase Fault with Stuck Breaker on NUNDRWD7 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT161 | Single Phase Fault with Stuck Breaker on WHITE 7 (652538) 115 kV Bus a. Apply Fault at the WHITE 7 (652538) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT162 | Single Phase Fault with Stuck Breaker on BLAIR-ER8 (655466) 69 kV Bus a. Apply Fault at the BLAIR-ER8 (655466) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER8 (655466) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT163 | Single Phase Fault with Stuck Breaker on PRAIRIE4 (657755) 230 kV Bus a. Apply Fault at the PRAIRIE4 (657755) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2017-002 | 25W | Transfer | GROUP1_REGIONAL_P4_FAULT164 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault1 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault2 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault3 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault4 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault5 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault6 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault7 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault8 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault9 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault10 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault11 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault12 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault13 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault14 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault15 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault16 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault17 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault18 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault19 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault20 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault21 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault22 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault23 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault24 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault25 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault26 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault28 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault29 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault30 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault31 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault32 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault33 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault34 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault35 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault36 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault37 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault38 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault39 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault40 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault42 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault44 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault45 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault46 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault47 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault48 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault49 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault50 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault51 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault52 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault53 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault54 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault55 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault56 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault57 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault59 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault60 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault61 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault62 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault64 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault65 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault66 | 3 Phase fault on MANAWA 5 161.00 (635010) 161 kV Bus a. Apply fault at the MANAWA 5 161.00 (635010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault67 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault68 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault69 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault70 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault71 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault72 | 3 Phase fault on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault73 | 3 Phase fault on NW56&MORTN7 115.00 (650207) 115 kV Bus a. Apply fault at the NW56&MORTN7 115.00 (650207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault74 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault75 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault76 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault77 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault78 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault79 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault80 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault81 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault82 | 3 Phase fault on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.LIB 7 (640353) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault83 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault84 | 3 Phase fault on SUB-C 7 115.00 (642070) 115 kV Bus a. Apply fault at the SUB-C 7 115.00 (642070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-C 7 (642070) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault85 | 3 Phase fault on SUB-B 7 115.00 (642069) 115 kV Bus a. Apply fault at the SUB-B 7 115.00 (642069) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-B 7 (642069) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault86 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault87 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault88 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault89 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault90 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault91 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault92 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault93 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault94 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault95 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault96 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault97 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault98 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault99 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault100 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault101 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault102 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault103 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault104 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault105 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault106 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault107 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault108 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault109 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault110 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault111 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault112 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault113 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault114 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault115 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault116 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault117 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault118 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault119 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault120 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault121 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault122 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault123 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault124 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault125 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault126 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault127 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault128 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault129 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault130 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault131 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault132 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault133 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault134 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault135 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault136 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault137 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault138 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault139 | 3 Phase fault on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault140 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault141 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault142 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault143 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault144 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault145 | 3 Phase fault on BELDEN 8 69.000 (640081) 69 kV Bus a. Apply fault at the BELDEN 8 69.000 (640081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault146 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault147 | 3 Phase fault on BROKENBG 69.000 (640090) 69 kV Bus a. Apply fault at the BROKENBG 69.000 (640090) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault148 | 3 Phase fault on CALAWAY8 69.000 (640099) 69 kV Bus a. Apply fault at the CALAWAY8 69.000 (640099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY8 (640099) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault149 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault150 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault151 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault152 | 3 Phase fault on CREITON8 69.000 (640150) 69 kV Bus a. Apply fault at the CREITON8 69.000 (640150) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault153 | 3 Phase fault on GENEVA 8 69.000 (640179) 69 kV Bus a. Apply fault at the GENEVA 8 69.000 (640179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault154 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault155 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault156 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault157 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault158 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault159 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault160 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault161 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault162 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault163 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault164 | 3 Phase fault on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETERSBRG.N7 (640444) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault165 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault166 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault167 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault168 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault169 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault170 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault171 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault172 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault173 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault174 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault175 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault176 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault177 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault178 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault179 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault180 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault181 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault182 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault183 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault184 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault185 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault186 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault187 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault188 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault189 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault190 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault191 | 3 Phase fault on S1250 5 161 (646250) 161 kV Bus a. Apply fault at the S1250 5 161 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault192 | 3 Phase fault on S1211 5 161 (646211) 161 kV Bus a. Apply fault at the S1211 5 161 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault193 | 3 Phase fault on S1299 5 161 (646299) 161 kV Bus a. Apply fault at the S1299 5 161 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault194 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault195 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault196 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault197 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault198 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault199 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault200 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault201 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault202 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault203 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault204 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault205 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault206 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault207 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault208 | 3 Phase fault on S1256 5 161.0 (646256) 161 kV Bus a. Apply fault at the S1256 5 161.0 (646256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault209 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault210 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault211 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault212 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault213 | 3 Phase fault on S1367 5 161.0 (646367) 161 kV Bus a. Apply fault at the S1367 5 161.0 (646367) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault214 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault215 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault216 | 3 Phase fault on S901 8 69.000 (647901) 69 kV Bus a. Apply fault at the S901 8 69.000 (647901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault217 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault218 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault219 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault220 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault221 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault222 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault223 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault224 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault225 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault226 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault227 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault228 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault229 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault230 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault231 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault232 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault233 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault234 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault235 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault236 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault237 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault238 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault239 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault240 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault241 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault242 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault243 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault244 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault245 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault246 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault247 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault248 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault249 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault250 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault251 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault252 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault253 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault254 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault255 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault256 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault257 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault258 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault259 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault260 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault261 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault262 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault263 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault264 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault265 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault266 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault267 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault270 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault271 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault272 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault273 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault274 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault275 | 3 Phase fault on CBLUFFS8 69.000 (635002) 69 kV Bus a. Apply fault at the CBLUFFS8 69.000 (635002) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault276 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB703 8 (635006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault277 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB704 8 (635007) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault278 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to HONEYCK8 (635080) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault280 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault281 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault282 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault283 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault286 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault287 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to SC WTRWRKS 8 (635242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault288 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to DIVISON8 (635246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault289 | 3 Phase fault on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault290 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to SLOAN 8 (635237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault291 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault292 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10215A_-NI8 (659922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault293 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10225A_-NI8 (659923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault294 | 3 Phase fault on STSTEEL8 69.000 (635240) 69 kV Bus a. Apply fault at the STSTEEL8 69.000 (635240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STSTEEL8 (635240) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault295 | 3 Phase fault on SC WEST8 69.000 (635241) 69 kV Bus a. Apply fault at the SC WEST8 69.000 (635241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SC WEST8 (635241) 69.0 kV to SC WTRWRKS 8 (635242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault296 | 3 Phase fault on DIVISON8 69.000 (635246) 69 kV Bus a. Apply fault at the DIVISON8 69.000 (635246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIVISON8 (635246) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault297 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault298 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to LAWTON8 (635249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault299 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to MAPLTN 8 (635302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault300 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to SMITHLD8 (635303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault301 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to DANBURY8 (635304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault302 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault303 | 3 Phase fault on DANBURY8 69.000 (635304) 69 kV Bus a. Apply fault at the DANBURY8 69.000 (635304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANBURY8 (635304) 69.0 kV to MAPCO 8 (635305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault305 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault306 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault307 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault308 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault309 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault310 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault311 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault312 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault313 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault314 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault315 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault316 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault317 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault318 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault319 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault320 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault321 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault322 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault323 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault324 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault325 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault326 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault327 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault328 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault329 | 3 Phase fault on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault330 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault331 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault332 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault333 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault334 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault335 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault336 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault337 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault338 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault339 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault340 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault341 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault342 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault343 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault344 | 3 Phase fault on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault345 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault346 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault347 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault348 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault349 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault350 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault351 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault352 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault353 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault354 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault355 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault356 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault357 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault358 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault359 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault360 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault361 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault362 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault363 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault364 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault365 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault366 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault367 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault368 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault369 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault370 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault371 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault372 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault373 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault374 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault375 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault376 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault377 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault378 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault379 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault380 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault381 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault382 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault383 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault384 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault385 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault386 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault387 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault388 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault389 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault390 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault391 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault392 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault393 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault394 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault395 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault396 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault397 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault398 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault399 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault400 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault401 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault402 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault403 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault404 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault405 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault406 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault407 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault408 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault409 | 3 Phase fault on ORD 7 115.00 (640308) 115 kV Bus a. Apply fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORD 7 (640308) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault410 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault411 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault412 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault413 | 3 Phase fault on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.LIB 7 (640353) 115.0 kV to ST.PAUL7 (640355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault414 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault415 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault416 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault417 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault418 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault419 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault420 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault421 | 3 Phase fault on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHERRYC3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault422 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault423 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault424 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault425 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault426 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault427 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault428 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault429 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault430 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault431 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault432 | 3 Phase fault on K10215A_-NI869.000 (659922) 69 kV Bus a. Apply fault at the K10215A_-NI869.000 (659922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10215A_-NI8 (659922) 69.0 kV to K144LWTN-NI8 (659979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault433 | 3 Phase fault on K10225A_-NI869.000 (659923) 69 kV Bus a. Apply fault at the K10225A_-NI869.000 (659923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10225A_-NI8 (659923) 69.0 kV to K127WHTG-NI8 (659981) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault434 | 3 Phase fault on K136MAPL-NI869.000 (659989) 69 kV Bus a. Apply fault at the K136MAPL-NI869.000 (659989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K136MAPL-NI8 (659989) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault435 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault436 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault437 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault438 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 8 (640085) 69.0 kV to BLMFLD 7 (640084) 115.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault439 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault440 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault441 | 3 Phase fault on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY8 (640099) 69.0 kV to CALAWAY7 (640098) 115.0 kV to CALLAWAY T19 (643027) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault442 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault443 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault444 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSONG (640164) 69.0 kV to EMERSON7 (640163) 115.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault445 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV to GENEVA 7 (640178) 115.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault446 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R8 (640207) 69.0 kV to GUIDE R7 (640206) 115.0 kV to GUIDEROCKT19 (643073) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault447 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN8 (640213) 69.0 kV to HARTGTN7 (640212) 115.0 kV to HARTINGTNT19 (643074) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault448 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault449 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault450 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault451 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault452 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault453 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault454 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault455 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 8 (640373) 69.0 kV to SUTTON 7 (640372) 115.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault456 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault457 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault458 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT8 (640415) 69.0 kV to CARLJCT7 (640105) 115.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault459 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault460 | 3 Phase fault on YORK SW7 115.00 (640413) 115 kV Bus a. Apply fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK.SW T2 8 (640447) 69.0 kV to YORK SW7 (640413) 115.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault461 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault462 | 3 Phase fault on ORD 7 115.00 (640308) 115 kV Bus a. Apply fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORD 8 (640475) 69.0 kV to ORD 7 (640308) 115.0 kV to ORD T2 9 (643179) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault463 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault464 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault465 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault466 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault467 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault468 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault469 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault470 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault471 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault472 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault473 | 3 Phase fault on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault474 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault475 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault476 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P1_Fault477 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault3 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault4 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault5 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault6 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault7 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault8 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault9 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault10 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault11 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault12 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault14 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault16 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault18 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault19 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault21 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault22 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault23 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault24 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault25 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault26 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault27 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault28 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault29 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault30 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault31 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault32 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault33 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault35 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault36 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault37 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault38 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault40 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault41 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault42 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault43 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault44 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault45 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault46 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault47 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault48 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P1_Fault49 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault1 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault2 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault3 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault4 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault5 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault6 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault7 | Single Phase Fault with Stuck Breaker on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 b.2. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault8 | Single Phase Fault with Stuck Breaker on BUNGE 5 161.00 (635031) 161 kV Bus a. Apply Fault at the BUNGE 5 161.00 (635031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 b.3. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 b.4. BUNGE 5 (635031) 161.0 kV to HASTING5 (635032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault9 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. SUB701 5 (635003) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault10 | Single Phase Fault with Stuck Breaker on OVRLND 5 161.00 (635015) 161 kV Bus a. Apply Fault at the OVRLND 5 161.00 (635015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault11 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault12 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault13 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault14 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault15 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault16 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault17 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault18 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault19 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault20 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (635226) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (635226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault21 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault22 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault23 | Single Phase Fault with Stuck Breaker on CRWFRD 5 161.00 (635330) 161 kV Bus a. Apply Fault at the CRWFRD 5 161.00 (635330) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.2. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.3. CRWFRD 5 (635330) 161.0 kV to NEWHRVST 9 (635331) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault24 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault25 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault26 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault27 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault28 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault29 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault30 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault31 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault32 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault33 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault34 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault35 | Single Phase Fault with Stuck Breaker on SUB-D 7 115.00 (642071) 115 kV Bus a. Apply Fault at the SUB-D 7 115.00 (642071) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DONIPHAN_7 (640159) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault36 | Single Phase Fault with Stuck Breaker on SUB-E 7 115.0 (642072) 115 kV Bus a. Apply Fault at the SUB-E 7 115.0 (642072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.2. SUB-E 7 (642072) 115.0 kV to Load #F0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault37 | Single Phase Fault with Stuck Breaker on SUB-F 7 115.0 (642073) 115 kV Bus a. Apply Fault at the SUB-F 7 115.0 (642073) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 b.2. SUB-F 7 (642073) 115.0 kV to Load #F0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault38 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to EGY CTRG (641086) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault39 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.6. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.7. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault40 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault41 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault42 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault43 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault44 | Single Phase Fault with Stuck Breaker on AINSWND7 115.00 (640050) 115 kV Bus a. Apply Fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWND.PLTD (640025) 34.5 kV Two Winding #1 b.2. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.3. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault45 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.4. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.5. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T1 9 (643004) 13.8 kV Three Winding #1 b.6. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T2 9 (643005) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault46 | Single Phase Fault with Stuck Breaker on AURORA_7 115.00 (640063) 115 kV Bus a. Apply Fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. AURORA_7 (640063) 115.0 kV to AURORA 9 (640064) 34.5 kV to AURORA T1 9 (643008) 13.8 kV Three Winding #1 b.4. AURORA_7 (640063) 115.0 kV to AURORA_8 (640416) 69.0 kV to AURORA T2 9 (643009) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault47 | Single Phase Fault with Stuck Breaker on BEEMER 7 115.00 (640078) 115 kV Bus a. Apply Fault at the BEEMER 7 115.00 (640078) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.3. BEEMER 7 (640078) 115.0 kV to BEEMER G (640079) 34.5 kV to BEEMER T1 9 (643015) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault48 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault49 | Single Phase Fault with Stuck Breaker on BROKENB7 115.00 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 b.2. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 b.3. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.4. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 b.5. BROKENB7 (640089) 115.0 kV to BROKENBG (640090) 69.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 b.6. BROKENB7 (640089) 115.0 kV to BROKENBG (640090) 69.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault50 | Single Phase Fault with Stuck Breaker on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply Fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 b.2. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 b.3. CALAWAY7 (640098) 115.0 kV to CALAWAY8 (640099) 69.0 kV to CALLAWAY T19 (643027) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault51 | Single Phase Fault with Stuck Breaker on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply Fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.3. CARLJCT7 (640105) 115.0 kV to CARLJCT9 (640106) 34.5 kV to CARLTNJCTT19 (643030) 13.8 kV Three Winding #1 b.4. CARLJCT7 (640105) 115.0 kV to CARLJCT8 (640415) 69.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault52 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.3. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT19 (643032) 13.8 kV Three Winding #1 b.4. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT29 (643033) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault53 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault54 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.2. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.3. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T1 9 (643046) 4.2 kV Three Winding #1 b.4. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T2 9 (643047) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault55 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault56 | Single Phase Fault with Stuck Breaker on EMERSON7 115.00 (640163) 115 kV Bus a. Apply Fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.3. EMERSON7 (640163) 115.0 kV to EMERSONG (640164) 69.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault57 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.3. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.4. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.5. GENEVA 7 (640178) 115.0 kV to GENEVA 8 (640179) 69.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault58 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T1 9 (643064) 13.8 kV Three Winding #1 b.4. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T2 9 (643065) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault59 | Single Phase Fault with Stuck Breaker on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.3. HEBRN N7 (640218) 115.0 kV to HEBRON G (640012) 13.8 kV Two Winding #1 b.4. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 b.5. HEBRON G (640012) Machine #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault60 | Single Phase Fault with Stuck Breaker on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.2. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.3. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. LOUPCTY7 (640259) 115.0 kV to LOUPCTY9 (640260) 34.5 kV to LOUP CITYT19 (643095) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault61 | Single Phase Fault with Stuck Breaker on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply Fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 b.2. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault62 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.4. MCCOOL 7 (640272) 115.0 kV to MCCOOL 8 (640273) 69.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault63 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault64 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault65 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault66 | Single Phase Fault with Stuck Breaker on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply Fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.2. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 b.3. N.LOUP 7 (640284) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.4. N.LOUP 7 (640284) 115.0 kV to N.LOUP 9 (640285) 34.5 kV to NORTHLOUPT19 (643105) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault67 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.3. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.4. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.5. OAKLAND7 (640300) 115.0 kV to OAKLAND9 (640301) 34.5 kV to OAKLAND T1 9 (643114) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault68 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.4. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.5. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.6. PAULINE7 (640313) 115.0 kV to PAULINE8 (640314) 69.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault69 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.3. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T19 (643139) 13.8 kV Three Winding #1 b.4. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T29 (643169) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault70 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault71 | Single Phase Fault with Stuck Breaker on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply Fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.2. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.3. SUTTON 7 (640372) 115.0 kV to SUTTON 8 (640373) 69.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault72 | Single Phase Fault with Stuck Breaker on TEKAMAH7 115.00 (640378) 115 kV Bus a. Apply Fault at the TEKAMAH7 115.00 (640378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH9 (640379) 34.5 kV to TEKAMAH T2 9 (643152) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault73 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.3. THEDFRD7 (640381) 115.0 kV to THEDFRD9 (640382) 34.5 kV to THEDFORD T19 (643153) 13.8 kV Three Winding #1 b.4. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault74 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.4. YORK 7 (640411) 115.0 kV to YORK 9 (640412) 34.5 kV to YORK T1 9 (643166) 13.8 kV Three Winding #1 b.5. YORK 7 (640411) 115.0 kV to YORK 8 (640443) 69.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault75 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. YORK SW7 (640413) 115.0 kV to YORK SW9 (640414) 34.5 kV to YORK.SW T1 9 (643168) 13.8 kV Three Winding #1 b.4. YORK SW7 (640413) 115.0 kV to YORK.SW T2 8 (640447) 69.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault76 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault77 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault78 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault79 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to BEATRCE7 (640076) 115.0 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.4. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.7. BEATRCE9 (640077) 34.5 kV to Load #NW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault80 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to BEATRCE7 (640076) 115.0 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 b.4. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE9 (640077) 34.5 kV to Load #NW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault81 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault82 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault83 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault84 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.4. HOSKINS9 (640229) 34.5 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.7. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.8. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.9. HOSKINS9 (640229) 34.5 kV to Load #N2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault85 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 b.4. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.8. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.9. HOSKINS9 (640229) 34.5 kV to Load #N2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault86 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault87 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.2. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.3. PETERSBRG.N7 (640444) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault88 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.7. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault89 | Single Phase Fault with Stuck Breaker on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply Fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. ELKRDG.PLT D (640419) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.4. CROFTN.PLT D (640423) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.5. BLMFLD 7 (640084) 115.0 kV to BLMFLD 8 (640085) 69.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault90 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to COLMBS1G (640006) 13.8 kV Two Winding #1 b.2. COLMBUS7 (640136) 115.0 kV to COLMBS2G (640007) 13.8 kV Two Winding #1 b.3. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.5. COLMBUS9 (640137) 34.5 kV to COLMBUS7 (640136) 115.0 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.9. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.10. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.11. COLMBUS7 (640136) 115.0 kV to Switched Shunt Device # b.12. COLMBUS9 (640137) 34.5 kV to Load #N0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault91 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.6. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault92 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.5. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.6. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.7. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.8. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault93 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG9 (640225) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.5. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.10. HOLDREG7 (640224) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault94 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault95 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.3. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.4. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault96 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to Load #O0 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault97 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1210 5 (646210) 161.0 kV to Load #O0 b.3. S1217 5 (646217) 161.0 kV to Load #O0 b.4. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.5. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.7. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault98 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault99 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault100 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault101 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault102 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault103 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault104 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault105 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault106 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault107 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault108 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault109 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault110 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault111 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault112 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault113 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault114 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault115 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault116 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault117 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault118 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault119 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault120 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211T39 (645127) 13.8 kV to Load #S4 b.2. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault121 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault122 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault123 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.4. NO4 AUX9 (645124) 2.4 kV to Load #S1 b.5. S1299 5 (646299) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault124 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.4. NO5 AUX9 (645125) 4.2 kV to Load #S1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault125 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 b.3. S1211T39 (645127) 13.8 kV to Load #S4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault126 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1216 5 (646216) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault127 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1216 5 (646216) 161.0 kV to Load #O0 b.8. S1217 5 (646217) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault128 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1216 5 (646216) 161.0 kV to Load #O0 b.8. S1210 5 (646210) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault129 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1217 5 (646217) 161.0 kV to Load #O0 b.8. S1210 5 (646210) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault130 | Single Phase Fault with Stuck Breaker on S1220 5 161.00 (646220) 161 kV Bus a. Apply Fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault131 | Single Phase Fault with Stuck Breaker on S1222 5 161.00 (646222) 161 kV Bus a. Apply Fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault132 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault133 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault134 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault135 | Single Phase Fault with Stuck Breaker on S1229 5 161.00 (646229) 161 kV Bus a. Apply Fault at the S1229 5 161.00 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault136 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault137 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault138 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault139 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault140 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault141 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault142 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load #O0 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault143 | Single Phase Fault with Stuck Breaker on S1250 5 161.0 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.0 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault144 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1341 5 (646341) 161.0 kV to Load #O0 b.2. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault145 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault146 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault147 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault148 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault149 | Single Phase Fault with Stuck Breaker on S1286 5 161.00 (646286) 161 kV Bus a. Apply Fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault150 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault151 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault152 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault153 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault154 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault155 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault156 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault157 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault158 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault159 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.4. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.5. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault160 | Single Phase Fault with Stuck Breaker on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply Fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. GAVINS 7 (652511) 115.0 kV to GAVINS1G (652575) 13.2 kV Two Winding #1 b.4. GAVINS 7 (652511) 115.0 kV to GAVINS2G (652576) 13.2 kV Two Winding #1 b.5. GAVINS 7 (652511) 115.0 kV to GAVINS3G (652577) 13.2 kV Two Winding #1 b.6. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 b.7. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault161 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault162 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault163 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault164 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault165 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault166 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault167 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault168 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault169 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.0 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.0 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault170 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault171 | Single Phase Fault with Stuck Breaker on 6815TP98 69.000 (647017) 69 kV Bus a. Apply Fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.8. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault172 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.4. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.5. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault173 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault174 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault175 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault176 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault178 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault179 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault180 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault181 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault182 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault183 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault184 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault185 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault186 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault187 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault188 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault189 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault190 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault191 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault192 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault193 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault194 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault195 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault196 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault197 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault198 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault199 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault200 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault201 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault203 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault204 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to EGYCTR2G (641089) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault205 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault206 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault207 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault209 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault210 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault211 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault212 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault213 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault214 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault215 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault216 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault217 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault218 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault219 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault220 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault221 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault222 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault223 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault224 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault225 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault226 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault227 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault228 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault229 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault230 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault231 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault232 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault233 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault234 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault235 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault236 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault237 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault238 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault239 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault240 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault241 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault242 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault243 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault244 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault245 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.3. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.4. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.5. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.6. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault246 | Single Phase Fault with Stuck Breaker on S985 8 69.000 (647985) 69 kV Bus a. Apply Fault at the S985 8 69.000 (647985) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.3. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault247 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault248 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.9. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault249 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault250 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault251 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault252 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault253 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault254 | Single Phase Fault with Stuck Breaker on S923 8 69.000 (647923) 69 kV Bus a. Apply Fault at the S923 8 69.000 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault255 | Single Phase Fault with Stuck Breaker on S924 8 69.000 (647924) 69 kV Bus a. Apply Fault at the S924 8 69.000 (647924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault256 | Single Phase Fault with Stuck Breaker on S928 8 69.000 (647928) 69 kV Bus a. Apply Fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault257 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.6. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault258 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault259 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault260 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault261 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault262 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault263 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault264 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault265 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault266 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault267 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault268 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault269 | Single Phase Fault with Stuck Breaker on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply Fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.2. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault270 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault271 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault272 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault273 | Single Phase Fault with Stuck Breaker on ORD 7 115.00 (640308) 115 kV Bus a. Apply Fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 b.2. ORD 7 (640308) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault274 | Single Phase Fault with Stuck Breaker on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. ST.LIB 7 (640353) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault275 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 b.2. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault276 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERRYC3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. CHERRYC3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault277 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault278 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault279 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault280 | Single Phase Fault with Stuck Breaker on ROSEMONT 7115.00 (640583) 115 kV Bus a. Apply Fault at the ROSEMONT 7115.00 (640583) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEMONT 7 (640583) 115.0 kV to GUIDE R7 (640206) 115.0 kV Transmission Circuit #1 b.2. ROSEMONT 7 (640583) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault281 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault282 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault283 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault284 | Single Phase Fault with Stuck Breaker on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #2 b.2. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault285 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault286 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault287 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault288 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault289 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault290 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault291 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault292 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to HILDRTH7 (640222) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault293 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.2. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault294 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault295 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault296 | Single Phase Fault with Stuck Breaker on HASTCTY7 115.00 (641088) 115 kV Bus a. Apply Fault at the HASTCTY7 115.00 (641088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTCTY7 (641088) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. HASTCTY7 (641088) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault297 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S3456 3 (645456) 345.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault298 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault299 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault300 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault301 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY2 (652552) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault303 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault304 | Single Phase Fault with Stuck Breaker on BROKENB7 115.00 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 b.2. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault305 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault306 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault307 | Single Phase Fault with Stuck Breaker on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.2. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault308 | Single Phase Fault with Stuck Breaker on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply Fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.LOUP 7 (640284) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.2. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault309 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault310 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault311 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault312 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault313 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault314 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault315 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault316 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARD AVE 3 (635219) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault317 | Single Phase Fault with Stuck Breaker on KNOX 8 69.000 (635243) 69 kV Bus a. Apply Fault at the KNOX 8 69.000 (635243) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOX 8 (635243) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 b.2. KNOX 8 (635243) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault318 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLND 3 (635400) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. HIGHLND 3 (635400) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault319 | Single Phase Fault with Stuck Breaker on MUDDY CREEK7115.00 (640455) 115 kV Bus a. Apply Fault at the MUDDY CREEK7115.00 (640455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUDDY CREEK7 (640455) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 b.2. MUDDY CREEK7 (640455) 115.0 kV to BROKENB7 (640089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault320 | Single Phase Fault with Stuck Breaker on S.SIOUXCITY7115.00 (640424) 115 kV Bus a. Apply Fault at the S.SIOUXCITY7115.00 (640424) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault321 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault322 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault323 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault324 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault325 | Single Phase Fault with Stuck Breaker on GRPR2 3 345.00 (648520) 345 kV Bus a. Apply Fault at the GRPR2 3 345.00 (648520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR2 3 (648520) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 b.2. GRPR2 3 (648520) 345.0 kV to GRPR21X9 (648521) 34.5 kV to GRPR21Y9 (648522) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault326 | Single Phase Fault with Stuck Breaker on GRPR_DMY_BUS345.00 (648527) 345 kV Bus a. Apply Fault at the GRPR_DMY_BUS345.00 (648527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 b.2. GRPR_DMY_BUS (648527) 345.0 kV to GRPR12X9 (648517) 34.5 kV to GRPR12Y9 (648518) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault327 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault328 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault329 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault330 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault331 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault332 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault333 | Single Phase Fault with Stuck Breaker on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply Fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to BELDEN 7 (640080) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault334 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault335 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault336 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault337 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL4 (640330) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault338 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault339 | Single Phase Fault with Stuck Breaker on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply Fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault340 | Single Phase Fault with Stuck Breaker on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply Fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. SUTTON 7 (640372) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault341 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault342 | Single Phase Fault with Stuck Breaker on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply Fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.2. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault343 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK SW7 (640413) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. YORK SW7 (640413) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault344 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault345 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault346 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING4 (640214) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault347 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault348 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S906 S 8 (647906) 69.0 kV to S904 8 (647904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault349 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault350 | Single Phase Fault with Stuck Breaker on S910 8 69.000 (647910) 69 kV Bus a. Apply Fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 b.2. S910 8 (647910) 69.0 kV to JCT205 8 (647105) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault351 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault352 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault353 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to PLYMOTH5 (635223) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault354 | Single Phase Fault with Stuck Breaker on OAKLAND7 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault355 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault356 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault357 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault358 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault359 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault360 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault361 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault362 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault363 | Single Phase Fault with Stuck Breaker on MONOLITH 7 (640591) 115 kV Bus a. Apply Fault at the MONOLITH 7 (640591) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault364 | Single Phase Fault with Stuck Breaker on TOBIAS 3 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault365 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault366 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault367 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault368 | Single Phase Fault with Stuck Breaker on MCCOOL 3 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault369 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault370 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault371 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault372 | Single Phase Fault with Stuck Breaker on HILDRTH7 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault374 | Single Phase Fault with Stuck Breaker on S910 8 (647910) 69 kV Bus a. Apply Fault at the S910 8 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault375 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault376 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault377 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault378 | Single Phase Fault with Stuck Breaker on NORFOLK7 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault379 | Single Phase Fault with Stuck Breaker on BELDEN 7 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault380 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault381 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault382 | Single Phase Fault with Stuck Breaker on ORD 7 (640308) 115 kV Bus a. Apply Fault at the ORD 7 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault383 | Single Phase Fault with Stuck Breaker on BROKENB7 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault384 | Single Phase Fault with Stuck Breaker on LOUPCTY7 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault385 | Single Phase Fault with Stuck Breaker on ST.LIB 7 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault386 | Single Phase Fault with Stuck Breaker on ALBION 7 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_LOCAL_P4_Fault387 | Single Phase Fault with Stuck Breaker on GENOA 7 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault1 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault2 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault3 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault4 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault5 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault6 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault7 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault8 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault9 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault10 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault11 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault12 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault13 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault14 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault15 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault16 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault17 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault18 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault19 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault20 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault21 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault22 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault23 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault24 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault25 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault26 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault27 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault28 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault29 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault30 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault31 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault32 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault33 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault34 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault35 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault36 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault37 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault38 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault39 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault40 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault41 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault42 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault43 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault44 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault45 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault46 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault47 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault48 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault49 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault50 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault51 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault52 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault53 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault54 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault55 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault56 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault57 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault58 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault59 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault60 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault61 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault62 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault63 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault64 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault65 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault66 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault67 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault68 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault69 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault70 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault71 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault72 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault73 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault74 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault75 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault76 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault77 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault79 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault80 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault81 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault82 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault83 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault84 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault85 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault86 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault87 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault88 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault89 | Single Phase Fault with Stuck Breaker on STHLND 3 345.00 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 345.00 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. STHLND 3 (635016) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault90 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault91 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault92 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault93 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault94 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault95 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault96 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault98 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault99 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault100 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault102 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault103 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault104 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault105 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault106 | Single Phase Fault with Stuck Breaker on G17-183-TAP (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault107 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault108 | Single Phase Fault with Stuck Breaker on STHLND 3 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault109 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault110 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault111 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips FRMR CTY W1 (635020) | Protection disabled with no impact on stability.
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault114 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault115 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault116 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault117 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault118 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault119 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault120 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault121 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault122 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault123 | Single Phase Fault with Stuck Breaker on S1280 5 (646280) 161 kV Bus a. Apply Fault at the S1280 5 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault124 | Single Phase Fault with Stuck Breaker on N.PLATT4 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.PLATT4 (640286) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault125 | Single Phase Fault with Stuck Breaker on BEVERLY7 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault126 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault127 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault128 | Single Phase Fault with Stuck Breaker on IDA CO 3 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault129 | Single Phase Fault with Stuck Breaker on 7FAIRPT (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25S | Transfer | GROUP2_REGIONAL_P4_Fault130 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault1 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault2 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault3 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault4 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault5 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault6 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault7 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault8 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault9 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault10 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault11 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault12 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault13 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault14 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault15 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault16 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault17 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault18 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault19 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault20 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault21 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault22 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault23 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault24 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault25 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault26 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault28 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault29 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault30 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault31 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault32 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault33 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault34 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault35 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault36 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault37 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault38 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault39 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault40 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault42 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault44 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault45 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault46 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault47 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault48 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault49 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault50 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault51 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault52 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault53 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault54 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault55 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault56 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault57 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault59 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault60 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault61 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault62 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault64 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault65 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault66 | 3 Phase fault on MANAWA 5 161.00 (635010) 161 kV Bus a. Apply fault at the MANAWA 5 161.00 (635010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault67 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault68 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault69 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault70 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault71 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault72 | 3 Phase fault on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault73 | 3 Phase fault on NW56&MORTN7 115.00 (650207) 115 kV Bus a. Apply fault at the NW56&MORTN7 115.00 (650207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault74 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault75 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault76 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault77 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault78 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault79 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault80 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault81 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault82 | 3 Phase fault on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.LIB 7 (640353) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault83 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault84 | 3 Phase fault on SUB-C 7 115.00 (642070) 115 kV Bus a. Apply fault at the SUB-C 7 115.00 (642070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-C 7 (642070) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault85 | 3 Phase fault on SUB-B 7 115.00 (642069) 115 kV Bus a. Apply fault at the SUB-B 7 115.00 (642069) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-B 7 (642069) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault86 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault87 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault88 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault89 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault90 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault91 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault92 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault93 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault94 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault95 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault96 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault97 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault98 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault99 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault100 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault101 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault102 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault103 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault104 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault105 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault106 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault107 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault108 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault109 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault110 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault111 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault112 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault113 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault114 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault115 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault116 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault117 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault118 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault119 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault120 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault121 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault122 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault123 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault124 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault125 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault126 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault127 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault128 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault129 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault130 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault131 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault132 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault133 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault134 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault135 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault136 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault137 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault138 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault139 | 3 Phase fault on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault140 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault141 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault142 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault143 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault144 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault145 | 3 Phase fault on BELDEN 8 69.000 (640081) 69 kV Bus a. Apply fault at the BELDEN 8 69.000 (640081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault146 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault147 | 3 Phase fault on BROKENBG 69.000 (640090) 69 kV Bus a. Apply fault at the BROKENBG 69.000 (640090) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault148 | 3 Phase fault on CALAWAY8 69.000 (640099) 69 kV Bus a. Apply fault at the CALAWAY8 69.000 (640099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY8 (640099) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault149 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault150 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault151 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault152 | 3 Phase fault on CREITON8 69.000 (640150) 69 kV Bus a. Apply fault at the CREITON8 69.000 (640150) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault153 | 3 Phase fault on GENEVA 8 69.000 (640179) 69 kV Bus a. Apply fault at the GENEVA 8 69.000 (640179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault154 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault155 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault156 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault157 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault158 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault159 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault160 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault161 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault162 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault163 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault164 | 3 Phase fault on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETERSBRG.N7 (640444) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault165 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault166 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault167 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault168 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault169 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault170 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault171 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault172 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault173 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault174 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault175 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault176 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault177 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault178 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault179 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault180 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault181 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault182 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault183 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault184 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault185 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault186 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault187 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault188 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault189 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault190 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault191 | 3 Phase fault on S1250 5 161 (646250) 161 kV Bus a. Apply fault at the S1250 5 161 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault192 | 3 Phase fault on S1211 5 161 (646211) 161 kV Bus a. Apply fault at the S1211 5 161 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault193 | 3 Phase fault on S1299 5 161 (646299) 161 kV Bus a. Apply fault at the S1299 5 161 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault194 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault195 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault196 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault197 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault198 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault199 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault200 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault201 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault202 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault203 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault204 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault205 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault206 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault207 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault208 | 3 Phase fault on S1256 5 161.0 (646256) 161 kV Bus a. Apply fault at the S1256 5 161.0 (646256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault209 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault210 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault211 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault212 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault213 | 3 Phase fault on S1367 5 161.0 (646367) 161 kV Bus a. Apply fault at the S1367 5 161.0 (646367) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault214 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault215 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault216 | 3 Phase fault on S901 8 69.000 (647901) 69 kV Bus a. Apply fault at the S901 8 69.000 (647901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault217 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault218 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault219 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault220 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault221 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault222 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault223 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault224 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault225 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault226 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault227 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault228 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault229 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault230 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault231 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault232 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault233 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault234 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault235 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault236 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault237 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault238 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault239 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault240 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault241 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault242 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault243 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault244 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault245 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault246 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault247 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault248 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault249 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault250 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault251 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault252 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault253 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault254 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault255 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault256 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault257 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault258 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault259 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault260 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault261 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault262 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault263 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault264 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault265 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault266 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault267 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault270 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault271 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault272 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault273 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault274 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault275 | 3 Phase fault on CBLUFFS8 69.000 (635002) 69 kV Bus a. Apply fault at the CBLUFFS8 69.000 (635002) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault276 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB703 8 (635006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault277 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB704 8 (635007) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault278 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to HONEYCK8 (635080) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault280 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault281 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault282 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault283 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault286 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault287 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to SC WTRWRKS 8 (635242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault288 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to DIVISON8 (635246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault289 | 3 Phase fault on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault290 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to SLOAN 8 (635237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault291 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault292 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10215A_-NI8 (659922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault293 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10225A_-NI8 (659923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault294 | 3 Phase fault on STSTEEL8 69.000 (635240) 69 kV Bus a. Apply fault at the STSTEEL8 69.000 (635240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STSTEEL8 (635240) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault295 | 3 Phase fault on SC WEST8 69.000 (635241) 69 kV Bus a. Apply fault at the SC WEST8 69.000 (635241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SC WEST8 (635241) 69.0 kV to SC WTRWRKS 8 (635242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault296 | 3 Phase fault on DIVISON8 69.000 (635246) 69 kV Bus a. Apply fault at the DIVISON8 69.000 (635246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIVISON8 (635246) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault297 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault298 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to LAWTON8 (635249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault299 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to MAPLTN 8 (635302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault300 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to SMITHLD8 (635303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault301 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to DANBURY8 (635304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault302 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault303 | 3 Phase fault on DANBURY8 69.000 (635304) 69 kV Bus a. Apply fault at the DANBURY8 69.000 (635304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANBURY8 (635304) 69.0 kV to MAPCO 8 (635305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault305 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault306 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault307 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault308 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault309 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault310 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault311 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault312 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault313 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault314 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault315 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault316 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault317 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault318 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault319 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault320 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault321 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault322 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault323 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault324 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault325 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault326 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault327 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault328 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault329 | 3 Phase fault on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault330 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault331 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault332 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault333 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault334 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault335 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault336 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault337 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault338 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault339 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault340 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault341 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault342 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault343 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault344 | 3 Phase fault on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault345 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault346 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault347 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault348 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault349 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault350 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault351 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault352 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault353 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault354 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault355 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault356 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault357 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault358 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault359 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault360 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault361 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault362 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault363 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault364 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault365 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault366 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault367 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault368 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault369 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault370 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault371 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault372 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault373 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault374 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault375 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault376 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault377 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault378 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault379 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault380 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault381 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault382 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault383 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault384 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault385 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault386 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault387 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault388 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault389 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault390 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault391 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault392 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault393 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault394 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault395 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault396 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault397 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault398 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault399 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault400 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault401 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault402 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault403 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault404 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault405 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault406 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault407 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault408 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault409 | 3 Phase fault on ORD 7 115.00 (640308) 115 kV Bus a. Apply fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORD 7 (640308) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault410 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault411 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault412 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault413 | 3 Phase fault on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.LIB 7 (640353) 115.0 kV to ST.PAUL7 (640355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault414 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault415 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault416 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault417 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault418 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault419 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault420 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault421 | 3 Phase fault on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHERRYC3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault422 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault423 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault424 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault425 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault426 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault427 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault428 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault429 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault430 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault431 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault432 | 3 Phase fault on K10215A_-NI869.000 (659922) 69 kV Bus a. Apply fault at the K10215A_-NI869.000 (659922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10215A_-NI8 (659922) 69.0 kV to K144LWTN-NI8 (659979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault433 | 3 Phase fault on K10225A_-NI869.000 (659923) 69 kV Bus a. Apply fault at the K10225A_-NI869.000 (659923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10225A_-NI8 (659923) 69.0 kV to K127WHTG-NI8 (659981) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault434 | 3 Phase fault on K136MAPL-NI869.000 (659989) 69 kV Bus a. Apply fault at the K136MAPL-NI869.000 (659989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K136MAPL-NI8 (659989) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault435 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault436 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault437 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault438 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 8 (640085) 69.0 kV to BLMFLD 7 (640084) 115.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault439 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault440 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault441 | 3 Phase fault on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY8 (640099) 69.0 kV to CALAWAY7 (640098) 115.0 kV to CALLAWAY T19 (643027) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault442 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault443 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault444 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSONG (640164) 69.0 kV to EMERSON7 (640163) 115.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault445 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV to GENEVA 7 (640178) 115.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault446 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R8 (640207) 69.0 kV to GUIDE R7 (640206) 115.0 kV to GUIDEROCKT19 (643073) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault447 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN8 (640213) 69.0 kV to HARTGTN7 (640212) 115.0 kV to HARTINGTNT19 (643074) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault448 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault449 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault450 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault451 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault452 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault453 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault454 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault455 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 8 (640373) 69.0 kV to SUTTON 7 (640372) 115.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault456 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault457 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault458 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT8 (640415) 69.0 kV to CARLJCT7 (640105) 115.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault459 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault460 | 3 Phase fault on YORK SW7 115.00 (640413) 115 kV Bus a. Apply fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK.SW T2 8 (640447) 69.0 kV to YORK SW7 (640413) 115.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault461 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault462 | 3 Phase fault on ORD 7 115.00 (640308) 115 kV Bus a. Apply fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORD 8 (640475) 69.0 kV to ORD 7 (640308) 115.0 kV to ORD T2 9 (643179) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault463 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault464 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault465 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault466 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault467 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault468 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault469 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault470 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault471 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault472 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault473 | 3 Phase fault on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault474 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault475 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault476 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P1_Fault477 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault3 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault4 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault5 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault6 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault7 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault8 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault9 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault10 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault11 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault12 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault14 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault16 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault18 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault19 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault21 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault22 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault23 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault24 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault25 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault26 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault27 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault28 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault29 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault30 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault31 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault32 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault33 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault35 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault36 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault37 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault38 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault40 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault41 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault42 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault43 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault44 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault45 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault46 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault47 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault48 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P1_Fault49 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault1 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault2 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault3 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault4 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault5 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault6 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault7 | Single Phase Fault with Stuck Breaker on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 b.2. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault8 | Single Phase Fault with Stuck Breaker on BUNGE 5 161.00 (635031) 161 kV Bus a. Apply Fault at the BUNGE 5 161.00 (635031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 b.3. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 b.4. BUNGE 5 (635031) 161.0 kV to HASTING5 (635032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault9 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. SUB701 5 (635003) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault10 | Single Phase Fault with Stuck Breaker on OVRLND 5 161.00 (635015) 161 kV Bus a. Apply Fault at the OVRLND 5 161.00 (635015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault11 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault12 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault13 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault14 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault15 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault16 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault17 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault18 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault19 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault20 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (635226) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (635226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault21 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault22 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault23 | Single Phase Fault with Stuck Breaker on CRWFRD 5 161.00 (635330) 161 kV Bus a. Apply Fault at the CRWFRD 5 161.00 (635330) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.2. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.3. CRWFRD 5 (635330) 161.0 kV to NEWHRVST 9 (635331) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault24 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault25 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault26 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault27 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault28 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault29 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault30 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault31 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault32 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault33 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault34 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault35 | Single Phase Fault with Stuck Breaker on SUB-D 7 115.00 (642071) 115 kV Bus a. Apply Fault at the SUB-D 7 115.00 (642071) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DONIPHAN_7 (640159) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault36 | Single Phase Fault with Stuck Breaker on SUB-E 7 115.0 (642072) 115 kV Bus a. Apply Fault at the SUB-E 7 115.0 (642072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.2. SUB-E 7 (642072) 115.0 kV to Load #F0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault37 | Single Phase Fault with Stuck Breaker on SUB-F 7 115.0 (642073) 115 kV Bus a. Apply Fault at the SUB-F 7 115.0 (642073) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 b.2. SUB-F 7 (642073) 115.0 kV to Load #F0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault38 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to EGY CTRG (641086) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault39 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.6. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.7. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault40 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault41 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault42 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault43 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault44 | Single Phase Fault with Stuck Breaker on AINSWND7 115.00 (640050) 115 kV Bus a. Apply Fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWND.PLTD (640025) 34.5 kV Two Winding #1 b.2. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.3. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault45 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.4. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.5. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T1 9 (643004) 13.8 kV Three Winding #1 b.6. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T2 9 (643005) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault46 | Single Phase Fault with Stuck Breaker on AURORA_7 115.00 (640063) 115 kV Bus a. Apply Fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. AURORA_7 (640063) 115.0 kV to AURORA 9 (640064) 34.5 kV to AURORA T1 9 (643008) 13.8 kV Three Winding #1 b.4. AURORA_7 (640063) 115.0 kV to AURORA_8 (640416) 69.0 kV to AURORA T2 9 (643009) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault47 | Single Phase Fault with Stuck Breaker on BEEMER 7 115.00 (640078) 115 kV Bus a. Apply Fault at the BEEMER 7 115.00 (640078) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.3. BEEMER 7 (640078) 115.0 kV to BEEMER G (640079) 34.5 kV to BEEMER T1 9 (643015) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault48 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault49 | Single Phase Fault with Stuck Breaker on BROKENB7 115.00 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 b.2. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 b.3. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.4. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 b.5. BROKENB7 (640089) 115.0 kV to BROKENBG (640090) 69.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 b.6. BROKENB7 (640089) 115.0 kV to BROKENBG (640090) 69.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault50 | Single Phase Fault with Stuck Breaker on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply Fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 b.2. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 b.3. CALAWAY7 (640098) 115.0 kV to CALAWAY8 (640099) 69.0 kV to CALLAWAY T19 (643027) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault51 | Single Phase Fault with Stuck Breaker on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply Fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.3. CARLJCT7 (640105) 115.0 kV to CARLJCT9 (640106) 34.5 kV to CARLTNJCTT19 (643030) 13.8 kV Three Winding #1 b.4. CARLJCT7 (640105) 115.0 kV to CARLJCT8 (640415) 69.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault52 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.3. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT19 (643032) 13.8 kV Three Winding #1 b.4. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT29 (643033) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault53 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault54 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.2. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.3. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T1 9 (643046) 4.2 kV Three Winding #1 b.4. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T2 9 (643047) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault55 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault56 | Single Phase Fault with Stuck Breaker on EMERSON7 115.00 (640163) 115 kV Bus a. Apply Fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.3. EMERSON7 (640163) 115.0 kV to EMERSONG (640164) 69.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault57 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.3. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.4. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.5. GENEVA 7 (640178) 115.0 kV to GENEVA 8 (640179) 69.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault58 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T1 9 (643064) 13.8 kV Three Winding #1 b.4. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T2 9 (643065) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault59 | Single Phase Fault with Stuck Breaker on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.3. HEBRN N7 (640218) 115.0 kV to HEBRON G (640012) 13.8 kV Two Winding #1 b.4. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 b.5. HEBRON G (640012) Machine #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault60 | Single Phase Fault with Stuck Breaker on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.2. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.3. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. LOUPCTY7 (640259) 115.0 kV to LOUPCTY9 (640260) 34.5 kV to LOUP CITYT19 (643095) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault61 | Single Phase Fault with Stuck Breaker on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply Fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 b.2. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault62 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.4. MCCOOL 7 (640272) 115.0 kV to MCCOOL 8 (640273) 69.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault63 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault64 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault65 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault66 | Single Phase Fault with Stuck Breaker on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply Fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.2. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 b.3. N.LOUP 7 (640284) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.4. N.LOUP 7 (640284) 115.0 kV to N.LOUP 9 (640285) 34.5 kV to NORTHLOUPT19 (643105) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault67 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.3. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.4. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.5. OAKLAND7 (640300) 115.0 kV to OAKLAND9 (640301) 34.5 kV to OAKLAND T1 9 (643114) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault68 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.4. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.5. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.6. PAULINE7 (640313) 115.0 kV to PAULINE8 (640314) 69.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault69 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.3. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T19 (643139) 13.8 kV Three Winding #1 b.4. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T29 (643169) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault70 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault71 | Single Phase Fault with Stuck Breaker on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply Fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.2. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.3. SUTTON 7 (640372) 115.0 kV to SUTTON 8 (640373) 69.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault72 | Single Phase Fault with Stuck Breaker on TEKAMAH7 115.00 (640378) 115 kV Bus a. Apply Fault at the TEKAMAH7 115.00 (640378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH9 (640379) 34.5 kV to TEKAMAH T2 9 (643152) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault73 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.3. THEDFRD7 (640381) 115.0 kV to THEDFRD9 (640382) 34.5 kV to THEDFORD T19 (643153) 13.8 kV Three Winding #1 b.4. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault74 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.4. YORK 7 (640411) 115.0 kV to YORK 9 (640412) 34.5 kV to YORK T1 9 (643166) 13.8 kV Three Winding #1 b.5. YORK 7 (640411) 115.0 kV to YORK 8 (640443) 69.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault75 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. YORK SW7 (640413) 115.0 kV to YORK SW9 (640414) 34.5 kV to YORK.SW T1 9 (643168) 13.8 kV Three Winding #1 b.4. YORK SW7 (640413) 115.0 kV to YORK.SW T2 8 (640447) 69.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault76 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault77 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault78 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault79 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to BEATRCE7 (640076) 115.0 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.4. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.7. BEATRCE9 (640077) 34.5 kV to Load #NW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault80 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to BEATRCE7 (640076) 115.0 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 b.4. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE9 (640077) 34.5 kV to Load #NW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault81 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault82 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault83 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault84 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.4. HOSKINS9 (640229) 34.5 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.7. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.8. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.9. HOSKINS9 (640229) 34.5 kV to Load #N2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault85 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 b.4. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.8. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.9. HOSKINS9 (640229) 34.5 kV to Load #N2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault86 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault87 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.2. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.3. PETERSBRG.N7 (640444) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault88 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.7. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault89 | Single Phase Fault with Stuck Breaker on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply Fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. ELKRDG.PLT D (640419) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.4. CROFTN.PLT D (640423) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.5. BLMFLD 7 (640084) 115.0 kV to BLMFLD 8 (640085) 69.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault90 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to COLMBS1G (640006) 13.8 kV Two Winding #1 b.2. COLMBUS7 (640136) 115.0 kV to COLMBS2G (640007) 13.8 kV Two Winding #1 b.3. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.5. COLMBUS9 (640137) 34.5 kV to COLMBUS7 (640136) 115.0 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.9. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.10. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.11. COLMBUS7 (640136) 115.0 kV to Switched Shunt Device # b.12. COLMBUS9 (640137) 34.5 kV to Load #N0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault91 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.6. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault92 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.5. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.6. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.7. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.8. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault93 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG9 (640225) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.5. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.10. HOLDREG7 (640224) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault94 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault95 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.3. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.4. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault96 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to Load #O0 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault97 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1210 5 (646210) 161.0 kV to Load #O0 b.3. S1217 5 (646217) 161.0 kV to Load #O0 b.4. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.5. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.7. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault98 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault99 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault100 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault101 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault102 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault103 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault104 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault105 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault106 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault107 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault108 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault109 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault110 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault111 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault112 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault113 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault114 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault115 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault116 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault117 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault118 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault119 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault120 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211T39 (645127) 13.8 kV to Load #S4 b.2. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault121 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault122 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault123 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.4. NO4 AUX9 (645124) 2.4 kV to Load #S1 b.5. S1299 5 (646299) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault124 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.4. NO5 AUX9 (645125) 4.2 kV to Load #S1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault125 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 b.3. S1211T39 (645127) 13.8 kV to Load #S4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault126 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1216 5 (646216) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault127 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1216 5 (646216) 161.0 kV to Load #O0 b.8. S1217 5 (646217) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault128 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1216 5 (646216) 161.0 kV to Load #O0 b.8. S1210 5 (646210) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault129 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1217 5 (646217) 161.0 kV to Load #O0 b.8. S1210 5 (646210) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault130 | Single Phase Fault with Stuck Breaker on S1220 5 161.00 (646220) 161 kV Bus a. Apply Fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault131 | Single Phase Fault with Stuck Breaker on S1222 5 161.00 (646222) 161 kV Bus a. Apply Fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault132 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault133 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault134 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault135 | Single Phase Fault with Stuck Breaker on S1229 5 161.00 (646229) 161 kV Bus a. Apply Fault at the S1229 5 161.00 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault136 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault137 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault138 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault139 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault140 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault141 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault142 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load #O0 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault143 | Single Phase Fault with Stuck Breaker on S1250 5 161.0 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.0 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault144 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1341 5 (646341) 161.0 kV to Load #O0 b.2. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault145 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault146 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault147 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault148 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault149 | Single Phase Fault with Stuck Breaker on S1286 5 161.00 (646286) 161 kV Bus a. Apply Fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault150 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault151 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault152 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault153 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault154 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault155 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault156 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault157 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault158 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault159 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.4. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.5. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault160 | Single Phase Fault with Stuck Breaker on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply Fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. GAVINS 7 (652511) 115.0 kV to GAVINS1G (652575) 13.2 kV Two Winding #1 b.4. GAVINS 7 (652511) 115.0 kV to GAVINS2G (652576) 13.2 kV Two Winding #1 b.5. GAVINS 7 (652511) 115.0 kV to GAVINS3G (652577) 13.2 kV Two Winding #1 b.6. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 b.7. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault161 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault162 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault163 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault164 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault165 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault166 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault167 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault168 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault169 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.0 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.0 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault170 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault171 | Single Phase Fault with Stuck Breaker on 6815TP98 69.000 (647017) 69 kV Bus a. Apply Fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.8. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault172 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.4. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.5. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault173 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault174 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault175 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault176 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault178 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault179 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault180 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault181 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault182 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault183 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault184 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault185 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault186 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault187 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault188 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault189 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault190 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault191 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault192 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault193 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault194 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault195 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault196 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault197 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault198 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault199 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault200 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault201 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault203 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault204 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to EGYCTR2G (641089) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault205 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault206 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault207 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault209 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault210 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault211 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault212 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault213 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault214 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault215 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault216 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault217 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault218 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault219 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault220 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault221 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault222 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault223 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault224 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault225 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault226 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault227 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault228 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault229 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault230 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault231 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault232 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault233 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault234 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault235 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault236 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault237 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault238 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault239 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault240 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault241 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault242 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault243 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault244 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault245 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.3. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.4. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.5. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.6. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault246 | Single Phase Fault with Stuck Breaker on S985 8 69.000 (647985) 69 kV Bus a. Apply Fault at the S985 8 69.000 (647985) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.3. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault247 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault248 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.9. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault249 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault250 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault251 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault252 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault253 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault254 | Single Phase Fault with Stuck Breaker on S923 8 69.000 (647923) 69 kV Bus a. Apply Fault at the S923 8 69.000 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault255 | Single Phase Fault with Stuck Breaker on S924 8 69.000 (647924) 69 kV Bus a. Apply Fault at the S924 8 69.000 (647924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault256 | Single Phase Fault with Stuck Breaker on S928 8 69.000 (647928) 69 kV Bus a. Apply Fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault257 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.6. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault258 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault259 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault260 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault261 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault262 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault263 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault264 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault265 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault266 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault267 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault268 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault269 | Single Phase Fault with Stuck Breaker on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply Fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.2. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault270 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault271 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault272 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault273 | Single Phase Fault with Stuck Breaker on ORD 7 115.00 (640308) 115 kV Bus a. Apply Fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 b.2. ORD 7 (640308) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault274 | Single Phase Fault with Stuck Breaker on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. ST.LIB 7 (640353) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault275 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 b.2. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault276 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERRYC3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. CHERRYC3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault277 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault278 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault279 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault280 | Single Phase Fault with Stuck Breaker on ROSEMONT 7115.00 (640583) 115 kV Bus a. Apply Fault at the ROSEMONT 7115.00 (640583) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEMONT 7 (640583) 115.0 kV to GUIDE R7 (640206) 115.0 kV Transmission Circuit #1 b.2. ROSEMONT 7 (640583) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault281 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault282 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault283 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault284 | Single Phase Fault with Stuck Breaker on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #2 b.2. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault285 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault286 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault287 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault288 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault289 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault290 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault291 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault292 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to HILDRTH7 (640222) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault293 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.2. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault294 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault295 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault296 | Single Phase Fault with Stuck Breaker on HASTCTY7 115.00 (641088) 115 kV Bus a. Apply Fault at the HASTCTY7 115.00 (641088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTCTY7 (641088) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. HASTCTY7 (641088) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault297 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S3456 3 (645456) 345.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault298 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault299 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault300 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault301 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY2 (652552) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault303 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault304 | Single Phase Fault with Stuck Breaker on BROKENB7 115.00 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 b.2. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault305 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault306 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault307 | Single Phase Fault with Stuck Breaker on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.2. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault308 | Single Phase Fault with Stuck Breaker on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply Fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.LOUP 7 (640284) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.2. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault309 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault310 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault311 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault312 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault313 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault314 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault315 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault316 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARD AVE 3 (635219) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault317 | Single Phase Fault with Stuck Breaker on KNOX 8 69.000 (635243) 69 kV Bus a. Apply Fault at the KNOX 8 69.000 (635243) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOX 8 (635243) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 b.2. KNOX 8 (635243) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault318 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLND 3 (635400) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. HIGHLND 3 (635400) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault319 | Single Phase Fault with Stuck Breaker on MUDDY CREEK7115.00 (640455) 115 kV Bus a. Apply Fault at the MUDDY CREEK7115.00 (640455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUDDY CREEK7 (640455) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 b.2. MUDDY CREEK7 (640455) 115.0 kV to BROKENB7 (640089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault320 | Single Phase Fault with Stuck Breaker on S.SIOUXCITY7115.00 (640424) 115 kV Bus a. Apply Fault at the S.SIOUXCITY7115.00 (640424) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault321 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault322 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault323 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault324 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault325 | Single Phase Fault with Stuck Breaker on GRPR2 3 345.00 (648520) 345 kV Bus a. Apply Fault at the GRPR2 3 345.00 (648520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR2 3 (648520) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 b.2. GRPR2 3 (648520) 345.0 kV to GRPR21X9 (648521) 34.5 kV to GRPR21Y9 (648522) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault326 | Single Phase Fault with Stuck Breaker on GRPR_DMY_BUS345.00 (648527) 345 kV Bus a. Apply Fault at the GRPR_DMY_BUS345.00 (648527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 b.2. GRPR_DMY_BUS (648527) 345.0 kV to GRPR12X9 (648517) 34.5 kV to GRPR12Y9 (648518) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault327 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault328 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault329 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault330 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault331 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault332 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault333 | Single Phase Fault with Stuck Breaker on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply Fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to BELDEN 7 (640080) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault334 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault335 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault336 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault337 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL4 (640330) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault338 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault339 | Single Phase Fault with Stuck Breaker on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply Fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault340 | Single Phase Fault with Stuck Breaker on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply Fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. SUTTON 7 (640372) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault341 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault342 | Single Phase Fault with Stuck Breaker on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply Fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.2. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault343 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK SW7 (640413) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. YORK SW7 (640413) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault344 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault345 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault346 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING4 (640214) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault347 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault348 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S906 S 8 (647906) 69.0 kV to S904 8 (647904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault349 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault350 | Single Phase Fault with Stuck Breaker on S910 8 69.000 (647910) 69 kV Bus a. Apply Fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 b.2. S910 8 (647910) 69.0 kV to JCT205 8 (647105) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault351 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault352 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault353 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to PLYMOTH5 (635223) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault354 | Single Phase Fault with Stuck Breaker on OAKLAND7 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault355 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault356 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault357 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault358 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault359 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault360 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault361 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault362 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault363 | Single Phase Fault with Stuck Breaker on MONOLITH 7 (640591) 115 kV Bus a. Apply Fault at the MONOLITH 7 (640591) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault364 | Single Phase Fault with Stuck Breaker on TOBIAS 3 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault365 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault366 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault367 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active and reactive powers of GEN-2015-088, GEN-2017-181 and GEN-2017-182. | GEN-2015-088 controller model correction
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault368 | Single Phase Fault with Stuck Breaker on MCCOOL 3 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault369 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault370 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault371 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault372 | Single Phase Fault with Stuck Breaker on HILDRTH7 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault374 | Single Phase Fault with Stuck Breaker on S910 8 (647910) 69 kV Bus a. Apply Fault at the S910 8 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault375 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault376 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault377 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault378 | Single Phase Fault with Stuck Breaker on NORFOLK7 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault379 | Single Phase Fault with Stuck Breaker on BELDEN 7 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault380 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault381 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault382 | Single Phase Fault with Stuck Breaker on ORD 7 (640308) 115 kV Bus a. Apply Fault at the ORD 7 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault383 | Single Phase Fault with Stuck Breaker on BROKENB7 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault384 | Single Phase Fault with Stuck Breaker on LOUPCTY7 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault385 | Single Phase Fault with Stuck Breaker on ST.LIB 7 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault386 | Single Phase Fault with Stuck Breaker on ALBION 7 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_LOCAL_P4_Fault387 | Single Phase Fault with Stuck Breaker on GENOA 7 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault1 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault2 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault3 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault4 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault5 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault6 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault7 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault8 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault9 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault10 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault11 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault12 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault13 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault14 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault15 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault16 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault17 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault18 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault19 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault20 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault21 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault22 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault23 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault24 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault25 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault26 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault27 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault28 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault29 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault30 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault31 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault32 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault33 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault34 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault35 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault36 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault37 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault38 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault39 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault40 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault41 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault42 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault43 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault44 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault45 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault46 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault47 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault48 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault49 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault50 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault51 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault52 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault53 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault54 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault55 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault56 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault57 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault58 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault59 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault60 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault61 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault62 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault63 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault64 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault65 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault66 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault67 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault68 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault69 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault70 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault71 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault72 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault73 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault74 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault75 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault76 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault77 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault79 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault80 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault81 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault82 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault83 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault84 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault85 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault86 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault87 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault88 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault89 | Single Phase Fault with Stuck Breaker on STHLND 3 345.00 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 345.00 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. STHLND 3 (635016) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault90 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault91 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault92 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault93 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault94 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault95 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault96 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault98 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault99 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault100 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault102 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault103 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault104 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault105 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault106 | Single Phase Fault with Stuck Breaker on G17-183-TAP (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault107 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault108 | Single Phase Fault with Stuck Breaker on STHLND 3 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault109 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault110 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault111 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault114 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault115 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault116 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault117 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault118 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault119 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault120 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault121 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault122 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault123 | Single Phase Fault with Stuck Breaker on S1280 5 (646280) 161 kV Bus a. Apply Fault at the S1280 5 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault124 | Single Phase Fault with Stuck Breaker on N.PLATT4 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.PLATT4 (640286) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault125 | Single Phase Fault with Stuck Breaker on BEVERLY7 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault126 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault127 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault128 | Single Phase Fault with Stuck Breaker on IDA CO 3 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault129 | Single Phase Fault with Stuck Breaker on 7FAIRPT (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 | 25W | Transfer | GROUP2_REGIONAL_P4_Fault130 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT2 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT3 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT4 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT5 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.2. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.4. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.5. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT6 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT7 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT8 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT9 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT10 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT11 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT12 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT13 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT14 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT15 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT16 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT17 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT18 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT19 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT20 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT21 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT22 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT23 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT24 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT25 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT26 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT27 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT28 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT29 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT30 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips Wavergen (532957) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT31 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips WCGS U1 (532751) | Protection was disabled with no impact to stability
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT32 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT33 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT34 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT35 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT36 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT37 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT38 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT39 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT40 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT41 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT42 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT43 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT44 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT45 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT46 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT47 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT48 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT49 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT50 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT51 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT52 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT53 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT54 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT55 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT56 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT57 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT58 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT59 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT60 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT61 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT62 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT63 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT64 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT65 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT66 | 3 Phase fault on QUINTON3 115.00 (533172) 115 kV Bus a. Apply fault at the QUINTON3 115.00 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT67 | 3 Phase fault on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT68 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT69 | 3 Phase fault on INDIANH3 115.00 (533166) 115 kV Bus a. Apply fault at the INDIANH3 115.00 (533166) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT70 | 3 Phase fault on 17&FAIR3 115.00 (533175) 115 kV Bus a. Apply fault at the 17&FAIR3 115.00 (533175) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT71 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT72 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT73 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT74 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT75 | 3 Phase fault on BONITA 3 115.00 (533262) 115 kV Bus a. Apply fault at the BONITA 3 115.00 (533262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SPRINGH3 (533267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT76 | 3 Phase fault on GEARY 3 115.00 (533336) 115 kV Bus a. Apply fault at the GEARY 3 115.00 (533336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT77 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT78 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT79 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT80 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT81 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT82 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT83 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT84 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT85 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT86 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT87 | 3 Phase fault on EMANHAT3 115.00 (533326) 115 kV Bus a. Apply fault at the EMANHAT3 115.00 (533326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT88 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT89 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT90 | 3 Phase fault on FAIRGDS3 115.00 (533236) 115 kV Bus a. Apply fault at the FAIRGDS3 115.00 (533236) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT91 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT92 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT93 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT94 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT95 | 3 Phase fault on WM BROS3 115.00 (533183) 115 kV Bus a. Apply fault at the WM BROS3 115.00 (533183) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WM BROS3 (533183) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT96 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT97 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT98 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT99 | 3 Phase fault on KERFORD3 115.00 (533216) 115 kV Bus a. Apply fault at the KERFORD3 115.00 (533216) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT100 | 3 Phase fault on KSU W 3 115.00 (533333) 115 kV Bus a. Apply fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT101 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT102 | 3 Phase fault on MANVILE3 115.00 (533426) 115 kV Bus a. Apply fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT103 | 3 Phase fault on REFINRY3 115.00 (533427) 115 kV Bus a. Apply fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT104 | 3 Phase fault on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT105 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT106 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT107 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT108 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT109 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT110 | 3 Phase fault on STRANGR3 115.00 (533268) 115 kV Bus a. Apply fault at the STRANGR3 115.00 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT111 | 3 Phase fault on UNIONRG3 115.00 (533359) 115 kV Bus a. Apply fault at the UNIONRG3 115.00 (533359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG3 (533359) 115.0 kV to TCHOPE 3 (533360) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT112 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT113 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT114 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT115 | 3 Phase fault on FRNTR N2 69.000 (533593) 69 kV Bus a. Apply fault at the FRNTR N2 69.000 (533593) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT116 | 3 Phase fault on BUTLERN2 69.000 (533583) 69 kV Bus a. Apply fault at the BUTLERN2 69.000 (533583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT117 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT118 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT119 | 3 Phase fault on DAVIS 2 69.000 (533506) 69 kV Bus a. Apply fault at the DAVIS 2 69.000 (533506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV to MWIRNJ22 (533529) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT120 | 3 Phase fault on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT121 | 3 Phase fault on INDEPEN2 69.000 (533694) 69 kV Bus a. Apply fault at the INDEPEN2 69.000 (533694) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT122 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT123 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCAN 2 (533850) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT124 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT125 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT126 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT127 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT128 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT129 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT130 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT131 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT132 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT133 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT134 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT135 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT136 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT137 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT138 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT139 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT140 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT141 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT142 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT143 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT144 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT145 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT146 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT147 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT148 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT149 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT150 | 3 Phase fault on 5WEDK 1 161.00 (345975) 161 kV Bus a. Apply fault at the 5WEDK 1 161.00 (345975) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5CAPE GIR2 (344282) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR1 (344280) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #1 b.3. 5CAPE GIR1 (344280) 161.0 kV to 5WEDK 1 (345975) 161.0 kV Transmission Circuit #1 b.4. 5CHARMN 1 (344338) 161.0 kV to 5TRAIL_TR TP (345824) 161.0 kV Transmission Circuit #1 b.5. 5TRAIL TR (345823) 161.0 kV to 5TRAIL_TR TP (345824) 161.0 kV Transmission Circuit #z b.6. 5WEDK 1 (345975) 161.0 kV to 5WEDK 2 (345984) 161.0 kV Transmission Circuit #z b.7. 1CHARMIN (346035) 13.2 kV to 5CHARMN 1 (344338) 161.0 kV Two Winding #1 b.8. 1CHARMIN (346035) 13.2 kV to 5CHARMN 1 (344338) 161.0 kV Two Winding #2 b.9. 2TRAIL TR (346144) 69.0 kV to 5TRAIL TR (345823) 161.0 kV Two Winding #1 b.10. 1WEDEKIND (346157) 34.5 kV to 5WEDK 1 (345975) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT151 | 3 Phase fault on 5ORAN 161.00 (345375) 161 kV Bus a. Apply fault at the 5ORAN 161.00 (345375) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORLEY (300121) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 b.2. 5KELSO 2 (344850) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT152 | 3 Phase fault on 7KELSO 2 345.00 (344849) 345 kV Bus a. Apply fault at the 7KELSO 2 345.00 (344849) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 2 (344849) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT153 | 3 Phase fault on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7LUTESVIL (344974) 345.0 kV to 7ST FRANC (345773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT154 | 3 Phase fault on 7HERITAGE 345.00 (345434) 345 kV Bus a. Apply fault at the 7HERITAGE 345.00 (345434) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7LUTESVIL (344974) 345.0 kV to 7HERITAGE (345434) 345.0 kV Transmission Circuit #1 b.2. 7HERITAGE (345434) 345.0 kV to 5HERITAGE 1 (345976) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT155 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT156 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT157 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT158 | 3 Phase fault on 7KELSO 2 345.00 (344849) 345 kV Bus a. Apply fault at the 7KELSO 2 345.00 (344849) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 2 (344849) 345.0 kV to 5KELSO 2 (344850) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT159 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT160 | 3 Phase fault on 5CAPE GIR2 161.00 (344282) 161 kV Bus a. Apply fault at the 5CAPE GIR2 161.00 (344282) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5CAPE GIR2 (344282) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR2 (344282) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #z b.3. 5CAPE GIR2 (344282) 161.0 kV to 5VIADUCT 1 (345894) 161.0 kV Transmission Circuit #z b.4. 5CAPE GIR2 (344282) 161.0 kV to 5JOPPA SR (351006) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT161 | 3 Phase fault on 5CAPE GIR3 161.00 (344286) 161 kV Bus a. Apply fault at the 5CAPE GIR3 161.00 (344286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR2 (344282) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR3 (344286) 161.0 kV to 5VIAD_TP (345891) 161.0 kV Transmission Circuit #2 b.3. 5CAPE GIR3 (344286) 161.0 kV to 5VIADUCT 2 (345893) 161.0 kV Transmission Circuit #z b.4. 5CAPE GIR3 (344286) 161.0 kV to 5HERITAGE 1 (345976) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT162 | 3 Phase fault on 8NEWMAD 500.00 (300035) 500 kV Bus a. Apply fault at the 8NEWMAD 500.00 (300035) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8NEWMAD (300035) 500.0 kV to 8WNEWMADRID (301406) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT163 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7STFRAN (300048) 345.0 kV to 7GOBKNOB (300054) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT164 | 3 Phase fault on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT165 | 3 Phase fault on 5GRNFRT 161.00 (300084) 161 kV Bus a. Apply fault at the 5GRNFRT 161.00 (300084) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRNFRT (300084) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT166 | 3 Phase fault on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 2GIBSON (301291) 69.0 kV to 5GIBSON (300083) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT167 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT168 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT169 | 3 Phase fault on 2CAMBEL 69.000 (301196) 69 kV Bus a. Apply fault at the 2CAMBEL 69.000 (301196) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CAMBEL (301196) 69.0 kV to 2GIBSON (301291) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT170 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT171 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT172 | 3 Phase fault on 2GIBSON 69.000 (301291) 69 kV Bus a. Apply fault at the 2GIBSON 69.000 (301291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GIBSON (301291) 69.0 kV to 2KENNET (301294) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT173 | 3 Phase fault on 2GIBSON 69.000 (301291) 69 kV Bus a. Apply fault at the 2GIBSON 69.000 (301291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GIBSON (301291) 69.0 kV to 2CLARKTON (301432) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT174 | 3 Phase fault on 8POWERLN_RD%500.00 (338156) 500 kV Bus a. Apply fault at the 8POWERLN_RD%500.00 (338156) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8POWERLN_RD% (338156) 500.0 kV to 8DELL% (338187) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT175 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T1 (338597) 13.8 kV Three Winding #1 b.2. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T2 (338598) 13.8 kV Three Winding #1 b.3. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T3 (338599) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT176 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 8SANS SOUCI% (338188) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT177 | 3 Phase fault on 5STEELE! 161.00 (338194) 161 kV Bus a. Apply fault at the 5STEELE! 161.00 (338194) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STEELE! (338194) 161.0 kV to 5HAYTI.S% (338200) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT178 | 3 Phase fault on 5HAYTI.S% 161.00 (338200) 161 kV Bus a. Apply fault at the 5HAYTI.S% 161.00 (338200) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HAYTI.S% (338200) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT179 | 3 Phase fault on 5JIM HILL% 161.00 (338202) 161 kV Bus a. Apply fault at the 5JIM HILL% 161.00 (338202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JIM HILL% (338202) 161.0 kV to 5RECTOR.N# (338689) 161.0 kV Transmission Circuit #1 b.2. 5PARAGOULD% (338204) 161.0 kV to 5HALLIDAY# (338709) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT180 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.2. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 b.3. NMA X1 1 (505401) 13.8 kV to N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV Three Winding #1 b.6. NMA X2 1 (505403) 13.8 kV to N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT181 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT182 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEN X1 1 (505407) 13.8 kV to KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV Three Winding #1 b.3. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 b.5. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT183 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT184 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRG X1 1 (505411) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 b.2. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.3. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 b.4. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X3 1 (505415) 13.8 kV Three Winding #1 b.5. PRG X2 1 (505413) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 b.9. PRG X3 1 (505415) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT185 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT186 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to JONESBO5 (505418) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT187 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT188 | 3 Phase fault on POP BLF5 161.00 (505438) 161 kV Bus a. Apply fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PBL X1 1 (505435) 13.8 kV to POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV Three Winding #1 b.3. POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV to PBL X2 1 (505437) 13.8 kV Three Winding #1 b.4. POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV to PBL X3 1 (505439) 13.8 kV Three Winding #1 b.6. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X1 1 (505435) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT189 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT5 (505410) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT190 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD5 (505412) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT191 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT192 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT193 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT194 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT195 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT196 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT197 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT198 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT199 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT200 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT201 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT202 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT203 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT204 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT205 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT206 | 3 Phase fault on 5STFRANB2 161.00 (300115) 161 kV Bus a. Apply fault at the 5STFRANB2 161.00 (300115) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STFRANB2 (300115) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT207 | 3 Phase fault on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WNEWMADRID (301406) 500.0 kV to 8DELL% (338187) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT208 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT209 | 3 Phase fault on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.3. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT210 | 3 Phase fault on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 8W.MEMPHIS% (338162) 500.0 kV to 8BHAM STEEL (360075) 500.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT211 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT212 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT213 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT214 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT215 | 3 Phase fault on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT216 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT217 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT218 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT219 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT220 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT221 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT222 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT223 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT224 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT225 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT226 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT227 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT228 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT229 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT230 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT231 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT232 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT233 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT234 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT235 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT236 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT237 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT238 | 3 Phase fault on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT239 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT240 | 3 Phase fault on S GAGEE3 115.00 (533178) 115 kV Bus a. Apply fault at the S GAGEE3 115.00 (533178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT241 | 3 Phase fault on CORONAD3 115.00 (533394) 115 kV Bus a. Apply fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT242 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT243 | 3 Phase fault on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT244 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT245 | 3 Phase fault on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIANW2 (533597) 69.0 kV to THUNBRD2 (533603) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT246 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT247 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT248 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT249 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT250 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT251 | 3 Phase fault on COMOTAR4 138.00 (533037) 138 kV Bus a. Apply fault at the COMOTAR4 138.00 (533037) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT252 | 3 Phase fault on INTERST4 138.00 (533051) 138 kV Bus a. Apply fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT253 | 3 Phase fault on 43LORAN 115.00 (533440) 115 kV Bus a. Apply fault at the 43LORAN 115.00 (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT254 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT255 | 3 Phase fault on PEIL 3 115.00 (533343) 115 kV Bus a. Apply fault at the PEIL 3 115.00 (533343) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT256 | 3 Phase fault on FRONTEN2 69.000 (533775) 69 kV Bus a. Apply fault at the FRONTEN2 69.000 (533775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.2. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT257 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 b.5. DEARING1 (533089) 13.2 kV to DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT258 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.4. LIBERTY1 (533090) 13.2 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT259 | 3 Phase fault on NINMLTP4 138.00 (521128) 138 kV Bus a. Apply fault at the NINMLTP4 138.00 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT260 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT261 | 3 Phase fault on CDRDLTP4 138.00 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 138.00 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT262 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT263 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT264 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT265 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT266 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT267 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT268 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT269 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT270 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT271 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT272 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT273 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT274 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT275 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT276 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT277 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT278 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT279 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT280 | 3 Phase fault on FOWLER 4 138.00 (533043) 138 kV Bus a. Apply fault at the FOWLER 4 138.00 (533043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT281 | 3 Phase fault on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT282 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT283 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT284 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT285 | 3 Phase fault on TALLGRS4 138.00 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 138.00 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT286 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT287 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT288 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT289 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT290 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT291 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT292 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT293 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT294 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT295 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.2. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.4. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT296 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT297 | 3 Phase fault on ANDOVER4 138.00 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 138.00 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT298 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT299 | 3 Phase fault on 29EVENG3 115.00 (533185) 115 kV Bus a. Apply fault at the 29EVENG3 115.00 (533185) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT300 | 3 Phase fault on SALTCRK3 115.00 (533434) 115 kV Bus a. Apply fault at the SALTCRK3 115.00 (533434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT301 | 3 Phase fault on 27CROCO3 115.00 (533187) 115 kV Bus a. Apply fault at the 27CROCO3 115.00 (533187) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT302 | 3 Phase fault on N TYLER3 115.00 (533168) 115 kV Bus a. Apply fault at the N TYLER3 115.00 (533168) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.2. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT303 | 3 Phase fault on FMC 3 115.00 (533241) 115 kV Bus a. Apply fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT304 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.2. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT305 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT306 | 3 Phase fault on EABILEN3 115.00 (533365) 115 kV Bus a. Apply fault at the EABILEN3 115.00 (533365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT307 | 3 Phase fault on JCTCTY 3 115.00 (533330) 115 kV Bus a. Apply fault at the JCTCTY 3 115.00 (533330) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT308 | 3 Phase fault on PARALEL3 115.00 (533218) 115 kV Bus a. Apply fault at the PARALEL3 115.00 (533218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT309 | 3 Phase fault on SHERWOD3 115.00 (533194) 115 kV Bus a. Apply fault at the SHERWOD3 115.00 (533194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT310 | 3 Phase fault on KEENE 3 115.00 (533167) 115 kV Bus a. Apply fault at the KEENE 3 115.00 (533167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.2. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT311 | 3 Phase fault on SOUTHTN3 115.00 (533265) 115 kV Bus a. Apply fault at the SOUTHTN3 115.00 (533265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.2. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT312 | 3 Phase fault on FORBES 3 115.00 (533157) 115 kV Bus a. Apply fault at the FORBES 3 115.00 (533157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT313 | 3 Phase fault on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT314 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT315 | 3 Phase fault on 54&MERI3 115.00 (533156) 115 kV Bus a. Apply fault at the 54&MERI3 115.00 (533156) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT316 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT317 | 3 Phase fault on LEVEE 3 115.00 (533327) 115 kV Bus a. Apply fault at the LEVEE 3 115.00 (533327) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to LEVEE 3 (533327) 115.0 kV Transmission Circuit #1 b.2. LEVEE 3 (533327) 115.0 kV to MATTERS3 (533334) 115.0 kV Transmission Circuit #1 b.3. MATTERS3 (533334) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT318 | 3 Phase fault on BISMARK3 115.00 (533234) 115 kV Bus a. Apply fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT319 | 3 Phase fault on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. OSAGE 3 (533170) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.3. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.4. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.5. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT320 | 3 Phase fault on NTHLAND3 115.00 (533169) 115 kV Bus a. Apply fault at the NTHLAND3 115.00 (533169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.2. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT321 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT322 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT323 | 3 Phase fault on HALLMRK3 115.00 (533242) 115 kV Bus a. Apply fault at the HALLMRK3 115.00 (533242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT324 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT325 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT326 | 3 Phase fault on STULL T3 115.00 (533270) 115 kV Bus a. Apply fault at the STULL T3 115.00 (533270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.3. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT327 | 3 Phase fault on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT328 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT329 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT330 | 3 Phase fault on NORTHST3 115.00 (533370) 115 kV Bus a. Apply fault at the NORTHST3 115.00 (533370) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT331 | 3 Phase fault on FRTLEAV3 115.00 (533274) 115 kV Bus a. Apply fault at the FRTLEAV3 115.00 (533274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.2. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT332 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT333 | 3 Phase fault on MAPLE J2 69.000 (533516) 69 kV Bus a. Apply fault at the MAPLE J2 69.000 (533516) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV to MAPLE J2 (533516) 69.0 kV Transmission Circuit #1 b.2. E MADSN2 (533508) 69.0 kV to F MONRO2 (533510) 69.0 kV Transmission Circuit #1 b.3. E MADSN2 (533508) 69.0 kV to MAPLE J2 (533516) 69.0 kV Transmission Circuit #1 b.4. E MADSN2 (533508) 69.0 kV to 3 VANBU2 (533527) 69.0 kV Transmission Circuit #1 b.5. MAPLE J2 (533516) 69.0 kV to 2ND ELM2 (533520) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT334 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT335 | 3 Phase fault on ARCOTAP2 69.000 (533620) 69 kV Bus a. Apply fault at the ARCOTAP2 69.000 (533620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO 2 (533619) 69.0 kV to ARCOTAP2 (533620) 69.0 kV Transmission Circuit #1 b.2. ARCOTAP2 (533620) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.3. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.4. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.6. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT336 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT337 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT338 | 3 Phase fault on ROCKCRK2 69.000 (533458) 69 kV Bus a. Apply fault at the ROCKCRK2 69.000 (533458) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 2 (533456) 69.0 kV to ROCKCRK2 (533458) 69.0 kV Transmission Circuit #1 b.2. ROCKCRK2 (533458) 69.0 kV to VALLEY22 (533483) 69.0 kV Transmission Circuit #1 b.3. ARNOLD 2 (533471) 69.0 kV to NORTONV2 (533481) 69.0 kV Transmission Circuit #1 b.4. NORTONV2 (533481) 69.0 kV to VALLEY22 (533483) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT339 | 3 Phase fault on ORCHARD2 69.000 (533643) 69 kV Bus a. Apply fault at the ORCHARD2 69.000 (533643) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.3. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT340 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT341 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT342 | 3 Phase fault on PECK 2 69.000 (533830) 69 kV Bus a. Apply fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. GILL W 2 (533796) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.3. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT343 | 3 Phase fault on MIDIANE2 69.000 (533610) 69 kV Bus a. Apply fault at the MIDIANE2 69.000 (533610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.2. MIDIANE2 (533610) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT344 | 3 Phase fault on BU5FURL2 69.000 (533861) 69 kV Bus a. Apply fault at the BU5FURL2 69.000 (533861) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THUNBRD2 (533603) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 b.3. GRANT 2 (533799) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT345 | 3 Phase fault on HYDROTP2 69.000 (533833) 69 kV Bus a. Apply fault at the HYDROTP2 69.000 (533833) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMAN2 (533787) 69.0 kV to HYDROTP2 (533833) 69.0 kV Transmission Circuit #1 b.2. RENEW 2 (533831) 69.0 kV to HYDROTP2 (533833) 69.0 kV Transmission Circuit #1 b.3. RENEW 2 (533831) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT346 | 3 Phase fault on COFFSUB2 69.000 (533683) 69 kV Bus a. Apply fault at the COFFSUB2 69.000 (533683) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFSUB2 (533683) 69.0 kV to CRA S 2 (533685) 69.0 kV Transmission Circuit #1 b.2. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT347 | 3 Phase fault on BEECRK2 69.000 (533677) 69 kV Bus a. Apply fault at the BEECRK2 69.000 (533677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEECRK2 (533677) 69.0 kV to CANEY 2 (533678) 69.0 kV Transmission Circuit #1 b.2. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.3. BEECRK2 (533677) 69.0 kV to COBBTAP2 (533710) 69.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT348 | 3 Phase fault on ROUSE 2 69.000 (533771) 69 kV Bus a. Apply fault at the ROUSE 2 69.000 (533771) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.2. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT349 | 3 Phase fault on WILLJCT2 69.000 (533713) 69 kV Bus a. Apply fault at the WILLJCT2 69.000 (533713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.2. WILLJCT2 (533713) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT350 | 3 Phase fault on WARE 2 69.000 (533652) 69 kV Bus a. Apply fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 b.3. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT351 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT352 | 3 Phase fault on PITNAC 2 69.000 (533769) 69 kV Bus a. Apply fault at the PITNAC 2 69.000 (533769) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.2. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.3. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT353 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT354 | 3 Phase fault on AQUARS 2 69.000 (533756) 69 kV Bus a. Apply fault at the AQUARS 2 69.000 (533756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT355 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT356 | 3 Phase fault on ADA 2 69.000 (533581) 69 kV Bus a. Apply fault at the ADA 2 69.000 (533581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADA 2 (533581) 69.0 kV to ELDORAD2 (533590) 69.0 kV Transmission Circuit #1 b.2. ADA 2 (533581) 69.0 kV to PESTER 2 (533600) 69.0 kV Transmission Circuit #1 b.3. CHESNEY2 (533589) 69.0 kV to MIDIANW2 (533597) 69.0 kV Transmission Circuit #1 b.4. CHESNEY2 (533589) 69.0 kV to PESTER 2 (533600) 69.0 kV Transmission Circuit #1 b.5. ELDORAD2 (533590) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT357 | 3 Phase fault on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT358 | 3 Phase fault on VULCTP 2 69.000 (533851) 69 kV Bus a. Apply fault at the VULCTP 2 69.000 (533851) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.3. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 b.4. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 b.5. SG1CHEN2 (533871) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT359 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT360 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT361 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT362 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.3. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT363 | 3 Phase fault on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.2. ASHGRV22 (533658) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.3. ASHGRJ12 (533659) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #z1 b.4. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT364 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT365 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage does not recover above 0.9 p.u. following the event in Holt (541510), Ketchem (541500), Rock Creek (541511), and Mullen Creek (541197) busbars. | Operational steady state fixes (existing caps/taps/gen set points) using the cap-banks at Rock Creek generating station as well as switching the reactors at Mullen Creek.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT366 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT367 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT368 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.5. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.6. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT369 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT370 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT371 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT372 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT373 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT374 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT375 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT376 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT377 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT378 | 3 Phase fault on MAYSOTH5 161.00 (546722) 161 kV Bus a. Apply fault at the MAYSOTH5 161.00 (546722) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT379 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT380 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT381 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT382 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT383 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT384 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT385 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT386 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT387 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT388 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT389 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT390 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT391 | 3 Phase fault on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT392 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT393 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT394 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT395 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT396 | 3 Phase fault on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPMAN3 (533362) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT397 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT398 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT399 | 3 Phase fault on HARTLND3 115.00 (533197) 115 kV Bus a. Apply fault at the HARTLND3 115.00 (533197) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTLND3 (533197) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT400 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT401 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT402 | 3 Phase fault on KSU E 3 115.00 (533346) 115 kV Bus a. Apply fault at the KSU E 3 115.00 (533346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU E 3 (533346) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT403 | 3 Phase fault on NMANHT3 115.00 (533347) 115 kV Bus a. Apply fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT3 (533347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT404 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT405 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT406 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT407 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT408 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT409 | 3 Phase fault on WILDCAT3 115.00 (533345) 115 kV Bus a. Apply fault at the WILDCAT3 115.00 (533345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILDCAT3 (533345) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT410 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT411 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT412 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT413 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT414 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT415 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT416 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT417 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT418 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT419 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT420 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT421 | 3 Phase fault on COALCRK2 69.000 (533633) 69 kV Bus a. Apply fault at the COALCRK2 69.000 (533633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALCRK2 (533633) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT422 | 3 Phase fault on DAVIS 2 69.000 (533506) 69 kV Bus a. Apply fault at the DAVIS 2 69.000 (533506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT423 | 3 Phase fault on DEARING2 69.000 (533688) 69 kV Bus a. Apply fault at the DEARING2 69.000 (533688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT424 | 3 Phase fault on MONTGOM2 69.000 (533698) 69 kV Bus a. Apply fault at the MONTGOM2 69.000 (533698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT425 | 3 Phase fault on MULBERY2 69.000 (533767) 69 kV Bus a. Apply fault at the MULBERY2 69.000 (533767) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULBERY2 (533767) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT426 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT427 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT428 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT429 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT430 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT431 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT432 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT433 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT434 | 3 Phase fault on 19THST 3 115.00 (533256) 115 kV Bus a. Apply fault at the 19THST 3 115.00 (533256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to 19THST 3 (533256) 115.0 kV Transmission Circuit #1 b.2. 19THST 3 (533256) 115.0 kV to FREESTATE3 (533257) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT435 | 3 Phase fault on CARB-KW 3 115.00 (533195) 115 kV Bus a. Apply fault at the CARB-KW 3 115.00 (533195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.2. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT436 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT437 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT438 | 3 Phase fault on CRAWFRD3 115.00 (533364) 115 kV Bus a. Apply fault at the CRAWFRD3 115.00 (533364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD3 (533364) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 b.3. MENTOR 3 (533374) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT439 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT440 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT441 | 3 Phase fault on MOONLIT3 115.00 (533254) 115 kV Bus a. Apply fault at the MOONLIT3 115.00 (533254) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT442 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT443 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT444 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT445 | 3 Phase fault on DEERCRK2 69.000 (533457) 69 kV Bus a. Apply fault at the DEERCRK2 69.000 (533457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 2 (533456) 69.0 kV to DEERCRK2 (533457) 69.0 kV Transmission Circuit #1 b.2. DEERCRK2 (533457) 69.0 kV to SANTAFJ2 (533460) 69.0 kV Transmission Circuit #1 b.3. SANTAFJ2 (533460) 69.0 kV to 2MADISN2 (533461) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT446 | 3 Phase fault on LITCH S2 69.000 (533766) 69 kV Bus a. Apply fault at the LITCH S2 69.000 (533766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT447 | 3 Phase fault on HUDSON-2 69.000 (533763) 69 kV Bus a. Apply fault at the HUDSON-2 69.000 (533763) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON-2 (533763) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT448 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT449 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT450 | 3 Phase fault on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRINGH3 (533267) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT451 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT452 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT453 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT454 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT455 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT456 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT457 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT458 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT459 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT460 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT461 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT462 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT463 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT464 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT465 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT466 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT467 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT468 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT469 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT470 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT471 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT472 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT473 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT474 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT475 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT476 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT477 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT478 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT479 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT480 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT481 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT482 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT483 | 3 Phase fault on S1250 5 161 (646250) 161 kV Bus a. Apply fault at the S1250 5 161 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT484 | 3 Phase fault on S1211 5 161 (646211) 161 kV Bus a. Apply fault at the S1211 5 161 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT485 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT486 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT487 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT488 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT489 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT490 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT491 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT492 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT493 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT494 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT495 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT496 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT497 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT498 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT499 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT500 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT501 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT502 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT503 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT504 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT505 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT506 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT507 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT508 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT509 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT510 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT511 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT512 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT513 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT514 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT515 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT516 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT517 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT518 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT519 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT520 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT521 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT522 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT523 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT524 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT525 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT526 | 3 Phase fault on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to SIKETAP5 (505427) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT527 | 3 Phase fault on IODINE 4 138.00 (520957) 138 kV Bus a. Apply fault at the IODINE 4 138.00 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT528 | 3 Phase fault on GLASMTN4 138.00 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 138.00 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT529 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT530 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT531 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT532 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT533 | 3 Phase fault on SEILING4 138.00 (520553) 138 kV Bus a. Apply fault at the SEILING4 138.00 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT534 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT535 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT536 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT537 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT538 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT539 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT540 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT541 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT542 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT543 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT544 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT545 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT546 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT547 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT548 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT549 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT550 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT551 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT552 | 3 Phase fault on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT553 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT554 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT555 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT556 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT557 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT558 | 3 Phase fault on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT559 | 3 Phase fault on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT560 | 3 Phase fault on CONCRD6 230.00 (539658) 230 kV Bus a. Apply fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT561 | 3 Phase fault on BARBER 4 138.00 (539674) 138 kV Bus a. Apply fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT562 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT563 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT564 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT565 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT566 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT567 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT568 | 3 Phase fault on 8NEWMAD 500.00 (300035) 500 kV Bus a. Apply fault at the 8NEWMAD 500.00 (300035) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8NEWMAD (300035) 500.0 kV to 8NEWMADXF34 (301528) 500.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT569 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT570 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT571 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT572 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7NEWMADXF34 (301529) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT573 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7NEWMADXF12 (301530) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT574 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7STFRAN (300048) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT575 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT576 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT577 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage does not recover above 0.9 pu at GEN-2017-108 POI due to the inadequacy of the reactive support provided by the unit at that location following the event. | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT578 | 3 Phase fault on 5GENTRY 161.00 (300073) 161 kV Bus a. Apply fault at the 5GENTRY 161.00 (300073) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GENTRY (300073) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT579 | 3 Phase fault on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT580 | 3 Phase fault on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT581 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT582 | 3 Phase fault on 5MARYVB2 161.00 (300097) 161 kV Bus a. Apply fault at the 5MARYVB2 161.00 (300097) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARYVB2 (300097) 161.0 kV to MARYVLE5 (541251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT583 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M0 (301396) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT584 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M1 (301397) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT585 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M2 (301398) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT586 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M3 (301399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT587 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NEWMADCP (301405) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT588 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NEWMADXF12 (301531) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT589 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NMDSU100HS (301538) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT590 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NMDSU200HS (301539) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT591 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT592 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT593 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT594 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT595 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT596 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT597 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT598 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to 2NMCOAL (300171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT599 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT600 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT601 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2MAGNOL (300328) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT602 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT603 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT604 | 3 Phase fault on 2CHAPHL 69.000 (300324) 69 kV Bus a. Apply fault at the 2CHAPHL 69.000 (300324) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CHAPHL (300324) 69.0 kV to 2RT Z (300325) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT605 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2COLMBUS (300326) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT606 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT607 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT608 | 3 Phase fault on 2ROSEHL 69.000 (300334) 69 kV Bus a. Apply fault at the 2ROSEHL 69.000 (300334) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROSEHL (300334) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT609 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT610 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT611 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT612 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT613 | 3 Phase fault on 5GRAVOIB1 161.00 (300555) 161 kV Bus a. Apply fault at the 5GRAVOIB1 161.00 (300555) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRAVOIB1 (300555) 161.0 kV to 5GRAVOIB2 (300574) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT614 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT615 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT616 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT617 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT618 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT619 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT620 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT621 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT622 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT623 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT624 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT625 | 3 Phase fault on 2KNOBBY 69.000 (300780) 69 kV Bus a. Apply fault at the 2KNOBBY 69.000 (300780) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOBBY (300780) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT626 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT627 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT628 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT629 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT630 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT631 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT632 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT633 | 3 Phase fault on 2AID 69.000 (301190) 69 kV Bus a. Apply fault at the 2AID 69.000 (301190) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AID (301190) 69.0 kV to 2AIDJCT (301191) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT634 | 3 Phase fault on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AIDJCT (301191) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT635 | 3 Phase fault on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AIDJCT (301191) 69.0 kV to 2BLOOMF (301237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT636 | 3 Phase fault on 2ARAB 69.000 (301192) 69 kV Bus a. Apply fault at the 2ARAB 69.000 (301192) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ARAB (301192) 69.0 kV to 2ADVANC (301235) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT637 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2FISK (301205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT638 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT639 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2ROMBAR (301223) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT640 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2WAPELO (301226) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT641 | 3 Phase fault on 2FISK 69.000 (301205) 69 kV Bus a. Apply fault at the 2FISK 69.000 (301205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISK (301205) 69.0 kV to 2DUDLEY (301228) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT642 | 3 Phase fault on 2MALDEN 69.000 (301214) 69 kV Bus a. Apply fault at the 2MALDEN 69.000 (301214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALDEN (301214) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT643 | 3 Phase fault on 2ROMBAR 69.000 (301223) 69 kV Bus a. Apply fault at the 2ROMBAR 69.000 (301223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROMBAR (301223) 69.0 kV to 2PBNORTH (301412) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT644 | 3 Phase fault on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADVANC (301235) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT645 | 3 Phase fault on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADVANC (301235) 69.0 kV to 2WHTWTR (301279) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT646 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2DOGWOD (301239) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT647 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2LILBRN (301246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT648 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2WOLFIS (301252) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT649 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2WYATT (301253) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT650 | 3 Phase fault on 2BLOOMF 69.000 (301237) 69 kV Bus a. Apply fault at the 2BLOOMF 69.000 (301237) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLOOMF (301237) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT651 | 3 Phase fault on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT652 | 3 Phase fault on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MINER (301254) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT653 | 3 Phase fault on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRISCO (301240) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT654 | 3 Phase fault on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRISCO (301240) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT655 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2IDALMA (301244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT656 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT657 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT658 | 3 Phase fault on 2IDALMA 69.000 (301244) 69 kV Bus a. Apply fault at the 2IDALMA 69.000 (301244) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALMA (301244) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT659 | 3 Phase fault on 2KELLY 69.000 (301245) 69 kV Bus a. Apply fault at the 2KELLY 69.000 (301245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KELLY (301245) 69.0 kV to 2VANDSR (301251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT660 | 3 Phase fault on 2LILBRN 69.000 (301246) 69 kV Bus a. Apply fault at the 2LILBRN 69.000 (301246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT661 | 3 Phase fault on 2MATHWS 69.000 (301247) 69 kV Bus a. Apply fault at the 2MATHWS 69.000 (301247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MATHWS (301247) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT662 | 3 Phase fault on 2MOREHS 69.000 (301248) 69 kV Bus a. Apply fault at the 2MOREHS 69.000 (301248) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOREHS (301248) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT663 | 3 Phase fault on 2MOREJT 69.000 (301249) 69 kV Bus a. Apply fault at the 2MOREJT 69.000 (301249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOREJT (301249) 69.0 kV to 2VANDSR (301251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT664 | 3 Phase fault on 2PARMA 69.000 (301250) 69 kV Bus a. Apply fault at the 2PARMA 69.000 (301250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PARMA (301250) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT665 | 3 Phase fault on 2VANDSR 69.000 (301251) 69 kV Bus a. Apply fault at the 2VANDSR 69.000 (301251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VANDSR (301251) 69.0 kV to 2MORLEY (301255) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT666 | 3 Phase fault on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AVONKN (301285) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT667 | 3 Phase fault on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AVONKN (301285) 69.0 kV to 2GIDJCT (301293) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT668 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT669 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT670 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT671 | 3 Phase fault on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT672 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT673 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT674 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT675 | 3 Phase fault on 5CHARLSTN 161.00 (344333) 161 kV Bus a. Apply fault at the 5CHARLSTN 161.00 (344333) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHARLSTN (344333) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT676 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT677 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT678 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5VIAD_TP (345891) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT679 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7KELSO 2 (344849) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT680 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT681 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT682 | 3 Phase fault on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MINER 1 (345203) 161.0 kV to 5MINER 2 (345204) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT683 | 3 Phase fault on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT684 | 3 Phase fault on 5RCHLND 1 161.00 (345588) 161 kV Bus a. Apply fault at the 5RCHLND 1 161.00 (345588) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RCHLND 1 (345588) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT685 | 3 Phase fault on 5STODDARD 1 161.00 (345790) 161 kV Bus a. Apply fault at the 5STODDARD 1 161.00 (345790) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STODDARD 1 (345790) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT686 | 3 Phase fault on 5VIAD_TP 161.00 (345891) 161 kV Bus a. Apply fault at the 5VIAD_TP 161.00 (345891) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5VIAD_TP (345891) 161.0 kV to 5VIADUCT 3 (345892) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT687 | 3 Phase fault on 7W_FRFT_E 345.00 (346992) 345 kV Bus a. Apply fault at the 7W_FRFT_E 345.00 (346992) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7W_FRFT_E (346992) 345.0 kV to 7SHAWNEE FP (360002) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT688 | 3 Phase fault on 7JOPPA TS 345.00 (347325) 345 kV Bus a. Apply fault at the 7JOPPA TS 345.00 (347325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JOPPA TS (347325) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT689 | 3 Phase fault on 5JOPPA S TP1161.00 (347334) 161 kV Bus a. Apply fault at the 5JOPPA S TP1161.00 (347334) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA S TP1 (347334) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT690 | 3 Phase fault on 5JOPPA T3 161.00 (347335) 161 kV Bus a. Apply fault at the 5JOPPA T3 161.00 (347335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA T3 (347335) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT691 | 3 Phase fault on 5MARION S 161.00 (347523) 161 kV Bus a. Apply fault at the 5MARION S 161.00 (347523) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARION S (347523) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT692 | 3 Phase fault on 7COMM 345.00 (348287) 345 kV Bus a. Apply fault at the 7COMM 345.00 (348287) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7COMM (348287) 345.0 kV to 7JORD (348289) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT693 | 3 Phase fault on 7JORD 345.00 (348289) 345 kV Bus a. Apply fault at the 7JORD 345.00 (348289) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JORD (348289) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT694 | 3 Phase fault on 7MASS 345.00 (348294) 345 kV Bus a. Apply fault at the 7MASS 345.00 (348294) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MASS (348294) 345.0 kV to 7SHAWNEE FP (360002) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT695 | 3 Phase fault on 5NAUVOO TN 161.00 (360479) 161 kV Bus a. Apply fault at the 5NAUVOO TN 161.00 (360479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NAUVOO TN (360479) 161.0 kV to 5RIDGELY TN (360521) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT696 | 3 Phase fault on 5RIDGELY TN 161.00 (360521) 161 kV Bus a. Apply fault at the 5RIDGELY TN 161.00 (360521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RIDGELY TN (360521) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT697 | 3 Phase fault on 5TIPTONVL TN161.00 (361261) 161 kV Bus a. Apply fault at the 5TIPTONVL TN161.00 (361261) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TIPTONVL TN (361261) 161.0 kV to 5POLK TP (361596) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT698 | 3 Phase fault on 5TROY TN 161.00 (361422) 161 kV Bus a. Apply fault at the 5TROY TN 161.00 (361422) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TROY TN (361422) 161.0 kV to 5POLK TP (361596) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT699 | 3 Phase fault on 5POLK TP 161.00 (361596) 161 kV Bus a. Apply fault at the 5POLK TP 161.00 (361596) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5POLK TP (361596) 161.0 kV to 5POLK (361597) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT700 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT701 | 3 Phase fault on N MADRD2 69.000 (505402) 69 kV Bus a. Apply fault at the N MADRD2 69.000 (505402) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT702 | 3 Phase fault on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT703 | 3 Phase fault on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT704 | 3 Phase fault on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKETAP5 (505427) 161.0 kV to SIKE SW5 (505433) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT705 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT706 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDALIA 5 (505434) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT707 | 3 Phase fault on POP BLF5 161.00 (505438) 161 kV Bus a. Apply fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POP BLF5 (505438) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT708 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT709 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT710 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT711 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT712 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT713 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT714 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT715 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT716 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT717 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT719 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT720 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT721 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT722 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT723 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT724 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT725 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT726 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT727 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT728 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT729 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT730 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT731 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT732 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT733 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT734 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT735 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT736 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT737 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT738 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT739 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT740 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT741 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT742 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT743 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT744 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT745 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT746 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT747 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT748 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT749 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT750 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT751 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT752 | 3 Phase fault on KSU W 3 115.00 (533333) 115 kV Bus a. Apply fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU W 3 (533333) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT753 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT754 | 3 Phase fault on AEC 3 115.00 (533361) 115 kV Bus a. Apply fault at the AEC 3 115.00 (533361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT755 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT756 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT757 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT758 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT759 | 3 Phase fault on ARKVAL 3 115.00 (533411) 115 kV Bus a. Apply fault at the ARKVAL 3 115.00 (533411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT760 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT761 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT762 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT763 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT764 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT765 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT766 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT767 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT768 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT769 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT770 | 3 Phase fault on BUTLERN2 69.000 (533583) 69 kV Bus a. Apply fault at the BUTLERN2 69.000 (533583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT771 | 3 Phase fault on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIANW2 (533597) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT772 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT773 | 3 Phase fault on CGENSUB2 69.000 (533662) 69 kV Bus a. Apply fault at the CGENSUB2 69.000 (533662) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CGENSUB2 (533662) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT774 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT775 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODESH2 (533699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT776 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT777 | 3 Phase fault on CHERRYV2 69.000 (533679) 69 kV Bus a. Apply fault at the CHERRYV2 69.000 (533679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYV2 (533679) 69.0 kV to CHRYJCT2 (533680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT778 | 3 Phase fault on YELLOWJ2 69.000 (533692) 69 kV Bus a. Apply fault at the YELLOWJ2 69.000 (533692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YELLOWJ2 (533692) 69.0 kV to NEW ALB2 (533701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT779 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT780 | 3 Phase fault on NEODJCT2 69.000 (533700) 69 kV Bus a. Apply fault at the NEODJCT2 69.000 (533700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEODJCT2 (533700) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT781 | 3 Phase fault on NEW ALB2 69.000 (533701) 69 kV Bus a. Apply fault at the NEW ALB2 69.000 (533701) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEW ALB2 (533701) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT782 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT783 | 3 Phase fault on LITCH N2 69.000 (533765) 69 kV Bus a. Apply fault at the LITCH N2 69.000 (533765) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT784 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT785 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT786 | 3 Phase fault on RIPLEYE2 69.000 (533859) 69 kV Bus a. Apply fault at the RIPLEYE2 69.000 (533859) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIPLEYE2 (533859) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT787 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT788 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT789 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT790 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT791 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT792 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT793 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT794 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT795 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT796 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT797 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT798 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT799 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT800 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT801 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT802 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT803 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT804 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT805 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT806 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT807 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT808 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT809 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT810 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT811 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT812 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT813 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT814 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to POPE (541349) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT815 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT816 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT817 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT818 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT819 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT820 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT821 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT822 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT823 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT824 | 3 Phase fault on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT825 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT826 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT827 | 3 Phase fault on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT828 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT829 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT830 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT831 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT832 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT833 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT834 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT835 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to BRADDYVILLE5 (635038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT836 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT837 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT838 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT839 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT840 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT841 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT842 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to ALABAMA5 (541354) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT843 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT844 | 3 Phase fault on IND PRK5 161.00 (541256) 161 kV Bus a. Apply fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT845 | 3 Phase fault on COOK 5 161.00 (541257) 161 kV Bus a. Apply fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT846 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT847 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT848 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT849 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT850 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT851 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT852 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT853 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT854 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT855 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT856 | 3 Phase fault on IATAN5 161.00 (541350) 161 kV Bus a. Apply fault at the IATAN5 161.00 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT857 | 3 Phase fault on AMOIL 2 69.000 (541358) 69 kV Bus a. Apply fault at the AMOIL 2 69.000 (541358) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOIL 2 (541358) 69.0 kV to MIDWY1 2 (541368) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT858 | 3 Phase fault on MIDWY1 2 69.000 (541368) 69 kV Bus a. Apply fault at the MIDWY1 2 69.000 (541368) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWY1 2 (541368) 69.0 kV to MDWYTP 2 (541389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT859 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT860 | 3 Phase fault on SAVANAH2 69.000 (541391) 69 kV Bus a. Apply fault at the SAVANAH2 69.000 (541391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAVANAH2 (541391) 69.0 kV to EDMOND2 (541392) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT861 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT862 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT863 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT864 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT865 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT866 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT867 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM_CAP5 (542947) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT868 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT869 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN_CAP5 (542950) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT870 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT871 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT872 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT873 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT874 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT875 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT876 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT877 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT878 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT879 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT880 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT881 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT882 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT883 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT884 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT885 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT886 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT887 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT888 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT889 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT890 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT891 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT892 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT893 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT894 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT895 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT896 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT897 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT898 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT899 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT900 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT901 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT902 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT903 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT904 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT905 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT906 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT907 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT908 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT909 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT910 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT911 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT912 | 3 Phase fault on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT913 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT914 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT915 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT916 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT917 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT918 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT919 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT920 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT921 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT922 | 3 Phase fault on CLAYCM15 161.00 (543022) 161 kV Bus a. Apply fault at the CLAYCM15 161.00 (543022) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLAYCM15 (543022) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT923 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT924 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT925 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT926 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT927 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT928 | 3 Phase fault on BRKRIDG5 161.00 (543033) 161 kV Bus a. Apply fault at the BRKRIDG5 161.00 (543033) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKRIDG5 (543033) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT929 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT930 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT931 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT932 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT933 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT934 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT935 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT936 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT937 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT938 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT939 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT940 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT941 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT942 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT943 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT944 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT945 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT946 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT947 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT948 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT949 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT950 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT951 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT952 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT953 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT954 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT955 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT956 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT957 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT958 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT959 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT960 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT961 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT962 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT963 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT964 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT965 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT966 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT967 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT968 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT969 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT970 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT971 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT972 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT973 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT974 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT975 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT976 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT977 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT978 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT979 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT980 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT981 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT982 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT983 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT984 | 3 Phase fault on COOPER_602 869.000 (640143) 69 kV Bus a. Apply fault at the COOPER_602 869.000 (640143) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT985 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT986 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT987 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT988 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT989 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT990 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT991 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT992 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT993 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT994 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT995 | 3 Phase fault on GI94_POI 345.00 (709400) 345 kV Bus a. Apply fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT996 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to 7ESSEX (300038) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT997 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5STFRNB3 (300116) 161.0 kV to 7STFRAN (300048) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT998 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT999 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1000 | 3 Phase fault on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB2 (300076) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1001 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1002 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1003 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1004 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1005 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1006 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1007 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1008 | 3 Phase fault on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1009 | 3 Phase fault on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1010 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEYCRK (301401) 69.0 kV to 5TURKEYCRK (301370) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1011 | 3 Phase fault on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1012 | 3 Phase fault on 8NEWMADXF34 500.00 (301528) 500 kV Bus a. Apply fault at the 8NEWMADXF34 500.00 (301528) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMADXF34 (301529) 345.0 kV to 8NEWMADXF34 (301528) 500.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1013 | 3 Phase fault on 8NEWMADXF34 500.00 (301528) 500 kV Bus a. Apply fault at the 8NEWMADXF34 500.00 (301528) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMADXF34 (301529) 345.0 kV to 8NEWMADXF34 (301528) 500.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1014 | 3 Phase fault on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1015 | 3 Phase fault on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1016 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL% (338185) 161.0 kV to 1DELL1 (338183) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1017 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL% (338185) 161.0 kV to 1DELL2 (338184) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1018 | 3 Phase fault on 5JIM HILL% 161.00 (338202) 161 kV Bus a. Apply fault at the 5JIM HILL% 161.00 (338202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JIM HILL% (338202) 161.0 kV to 3JIM HILL! (338230) 115.0 kV to 1JIM HILL (338209) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1019 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 5KELSO 1 (344847) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1020 | 3 Phase fault on 7JOPPA TS 345.00 (347325) 345 kV Bus a. Apply fault at the 7JOPPA TS 345.00 (347325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JOPPA TS (351003) 161.0 kV to 7JOPPA TS (347325) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1021 | 3 Phase fault on 7JORD 345.00 (348289) 345 kV Bus a. Apply fault at the 7JORD 345.00 (348289) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JORD (348289) 345.0 kV to 4JORD (348292) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1022 | 3 Phase fault on 7MASS 345.00 (348294) 345 kV Bus a. Apply fault at the 7MASS 345.00 (348294) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MASS (348294) 345.0 kV to 5MASS (348295) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1023 | 3 Phase fault on 8SHAWNEE FP 500.00 (360001) 500 kV Bus a. Apply fault at the 8SHAWNEE FP 500.00 (360001) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHAWNEE FP (360001) 500.0 kV to 7SHAWNEE FP (360002) 345.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1024 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X1 1 (505417) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1025 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X2 1 (505419) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1026 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to SIKESTN2 (505430) 69.0 kV to SIK X1 1 (505429) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1027 | 3 Phase fault on SIKE SW5 161.00 (505433) 161 kV Bus a. Apply fault at the SIKE SW5 161.00 (505433) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKE SW5 (505433) 161.0 kV to SIKE SW2 (505423) 69.0 kV to SIK X2 1 (505431) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1028 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1029 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1030 | 3 Phase fault on MOORLND4 138.00 (520999) 138 kV Bus a. Apply fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 (520999) 138.0 kV to MOORLND2 (520995) 69.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1031 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1032 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1033 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1034 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1035 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1036 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1037 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1038 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1039 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1040 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1041 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1042 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1043 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1044 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1045 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1046 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1047 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1048 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1049 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1050 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1051 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1052 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1053 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1054 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1055 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1056 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1057 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1058 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1059 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1060 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV to NMANHX1 (532901) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1061 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1062 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1063 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1064 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1065 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1066 | 3 Phase fault on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1067 | 3 Phase fault on TECHILL5 161.00 (532920) 161 kV Bus a. Apply fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1068 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1069 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1070 | 3 Phase fault on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1071 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1072 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1073 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1074 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1075 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1076 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1077 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1078 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1079 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1080 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1081 | 3 Phase fault on 17TH 4 138.00 (533064) 138 kV Bus a. Apply fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1082 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1083 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to ARNOLD 2 (533471) 69.0 kV to ARNOLD 1 (533449) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1084 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1085 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1086 | 3 Phase fault on HEC 3 115.00 (533419) 115 kV Bus a. Apply fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1087 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1088 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips GEN-2017-121 (761841 and 761844). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1089 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1090 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1091 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1092 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1093 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1094 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1095 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1096 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1097 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 2 (533742) 69.0 kV to MOUND 4 (533013) 138.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1098 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1099 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1100 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1101 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1102 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1103 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1104 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1105 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1106 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1107 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1108 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1109 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1110 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1111 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1112 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1113 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1114 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1115 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1116 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1117 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1118 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1119 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MRVL#1 (541378) 69.0 kV to MARYVIL11 (541519) 13.2 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1120 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MRVL#2 (541359) 69.0 kV to MARYVIL21 (541520) 13.2 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1121 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1122 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1123 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1124 | 3 Phase fault on EDMOND5 161.00 (541355) 161 kV Bus a. Apply fault at the EDMOND5 161.00 (541355) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDMOND5 (541355) 161.0 kV to EDMOND2 (541392) 69.0 kV to EDMOND-T (541522) 13.1 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1125 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to MIDWY1 2 (541368) 69.0 kV to MIDWY-T1 (541521) 13.2 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1126 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to MIDWY2 2 (541390) 69.0 kV to MIDWY-T2 (541393) 13.2 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1127 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1128 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1129 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1130 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1131 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1132 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1133 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1134 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1135 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1136 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1137 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1138 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1139 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1140 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1141 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1142 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1143 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1144 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1145 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1146 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1147 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1148 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1149 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1150 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1151 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1152 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1153 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1154 | 3 Phase fault on 5NEWMADCP 161.00 (301405) 161 kV Bus a. Apply fault at the 5NEWMADCP 161.00 (301405) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMADCP (301405) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1155 | 3 Phase fault on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALDEN 2 (505404) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1156 | 3 Phase fault on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIGGOTT2 (505406) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1157 | 3 Phase fault on KENNETT2 69.000 (505408) 69 kV Bus a. Apply fault at the KENNETT2 69.000 (505408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT2 (505408) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1158 | 3 Phase fault on PARAGLD2 69.000 (505414) 69 kV Bus a. Apply fault at the PARAGLD2 69.000 (505414) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD2 (505414) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1159 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT1 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT2 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT3 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT4 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT5 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT6 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT7 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT8 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips Wavergen (532957) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT9 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT10 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT11 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT12 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT13 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT14 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT15 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT16 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT17 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT18 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT19 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT20 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT21 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT22 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT23 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT24 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT25 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT26 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT27 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT28 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT29 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT30 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT31 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT32 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT33 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT34 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT35 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT36 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT37 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT38 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT39 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT40 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT41 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT42 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT43 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT44 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT45 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT46 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT47 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT48 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT49 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT50 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT51 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT1 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.5. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.6. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.7. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.8. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.9. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.10. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.11. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.12. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.13. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.14. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.15. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.16. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.17. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT2 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 b.3. LITCH 5 (532932) 161.0 kV to LITCH N2 (533765) 69.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 b.4. LITCH 5 (532932) 161.0 kV to LITCH S2 (533766) 69.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT3 | Single Phase Fault with Stuck Breaker on 29TH 4 138.00 (533024) 138 kV Bus a. Apply Fault at the 29TH 4 138.00 (533024) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT4 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT5 | Single Phase Fault with Stuck Breaker on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply Fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT6 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT7 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT8 | Single Phase Fault with Stuck Breaker on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply Fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT9 | Single Phase Fault with Stuck Breaker on AEC 3 115.00 (533361) 115 kV Bus a. Apply Fault at the AEC 3 115.00 (533361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AEC 3 (533361) 115.0 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.2. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.4. AEC 3 (533361) 115.0 kV to AEC W1 (533887) 34.5 kV Two Winding #1 b.5. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT10 | Single Phase Fault with Stuck Breaker on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.3. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT11 | Single Phase Fault with Stuck Breaker on INDIANH3 115.00 (533166) 115 kV Bus a. Apply Fault at the INDIANH3 115.00 (533166) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.3. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT12 | Single Phase Fault with Stuck Breaker on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply Fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 (532662) 14.4 kV to LEC U4 3 (533249) 115.0 kV Two Winding #1 b.2. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.3. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT13 | Single Phase Fault with Stuck Breaker on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply Fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT14 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT15 | Single Phase Fault with Stuck Breaker on SMOKYHLLS3 115.00 (533378) 115 kV Bus a. Apply Fault at the SMOKYHLLS3 115.00 (533378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 b.2. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT16 | Single Phase Fault with Stuck Breaker on S ALMA 3 115.00 (533339) 115 kV Bus a. Apply Fault at the S ALMA 3 115.00 (533339) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 b.2. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT17 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT18 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT19 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT20 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT21 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT22 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT23 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT24 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT25 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT26 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT27 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT28 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT29 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT30 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT31 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT32 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT33 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT34 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT35 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT36 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT37 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT38 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT39 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT40 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT41 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT42 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT43 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT44 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT45 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT46 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT47 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT48 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT49 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT50 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT51 | Single Phase Fault with Stuck Breaker on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.3. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT52 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT53 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT54 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT55 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT56 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT57 | Single Phase Fault with Stuck Breaker on JEC 6 230.00 (532852) 230 kV Bus a. Apply Fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT58 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT59 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT60 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT61 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT62 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT63 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT64 | Single Phase Fault with Stuck Breaker on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply Fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT65 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT66 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT67 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT68 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT69 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT70 | Single Phase Fault with Stuck Breaker on NMANHT6 230.00 (532865) 230 kV Bus a. Apply Fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.2. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 b.3. NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV to NMANHX1 (532901) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT71 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT72 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT73 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT74 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT75 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT76 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT77 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT78 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT79 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT80 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT81 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT82 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT83 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT84 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.3. FRANKLIN5 (532938) 161.0 kV to FRANKLIN2 (533876) 69.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT85 | Single Phase Fault with Stuck Breaker on 17TH 4 138.00 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.3. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT86 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.6. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.8. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT87 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.6. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT88 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT89 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT90 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT91 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT92 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT93 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT94 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT95 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.4. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT96 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT97 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT98 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.2. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.3. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT99 | Single Phase Fault with Stuck Breaker on SLATECRK4 138.00 (533070) 138 kV Bus a. Apply Fault at the SLATECRK4 138.00 (533070) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to SLATECRK4 (533070) 138.0 kV Transmission Circuit #1 b.3. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.4. SLATEXFMR1 (533139) 34.5 kV to SLATEGSU1 (533140) 34.5 kV Transmission Circuit #1 b.5. SLATEGEN1 (533141) 0.7 kV to SLATEGSU1 (533140) 34.5 kV Two Winding #1 b.6. SLATECRK4 (533070) 138.0 kV to SLATEXFMR1 (533139) 34.5 kV to SLATETV1 (533142) 13.2 kV Three Winding #1 b.7. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT100 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.9. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT101 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.9. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT102 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.5. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT103 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.6. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT104 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.6. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT105 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT106 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT107 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT108 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT109 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT110 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT111 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEC DG 1 (532730) 4.2 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT112 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT113 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT114 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT115 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT116 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT117 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT118 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT119 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT120 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT121 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.6. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT122 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. NEAST3X1 (533110) 11.3 kV to NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT123 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.4. NEAST5X1 (533111) 13.2 kV to NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT124 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.8. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.10. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT125 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT126 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT127 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT128 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.4. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.5. SUMNER 4 (532984) 138.0 kV to GEN-2017-121 (761838) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT129 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT130 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT131 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT132 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT133 | Single Phase Fault with Stuck Breaker on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT134 | Single Phase Fault with Stuck Breaker on 17&FAIR3 115.00 (533175) 115 kV Bus a. Apply Fault at the 17&FAIR3 115.00 (533175) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 b.2. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.3. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT135 | Single Phase Fault with Stuck Breaker on FORBES 3 115.00 (533157) 115 kV Bus a. Apply Fault at the FORBES 3 115.00 (533157) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.3. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.4. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT136 | Single Phase Fault with Stuck Breaker on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply Fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.3. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT137 | Single Phase Fault with Stuck Breaker on FMC 3 115.00 (533241) 115 kV Bus a. Apply Fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 b.3. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT138 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.3. 87TH 1X1 (532818) 13.8 kV to 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT139 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT140 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 b.2. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT141 | Single Phase Fault with Stuck Breaker on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. AUBURN 1 (532880) 14.4 kV to AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT142 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 1 (532880) 14.4 kV to AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV Three Winding #1 b.2. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT143 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.3. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT144 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT145 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT146 | Single Phase Fault with Stuck Breaker on CLAYCTR3 115.00 (533323) 115 kV Bus a. Apply Fault at the CLAYCTR3 115.00 (533323) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCSS3 (533320) 115.0 kV to CLAYCTR3 (533323) 115.0 kV Transmission Circuit #1 b.2. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT147 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT148 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT149 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT150 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT151 | Single Phase Fault with Stuck Breaker on HEC GT 3 115.00 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 115.00 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT152 | Single Phase Fault with Stuck Breaker on CITIES 3 115.00 (533414) 115 kV Bus a. Apply Fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.3. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.4. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT153 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT154 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT155 | Single Phase Fault with Stuck Breaker on COLINE 3 115.00 (533153) 115 kV Bus a. Apply Fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.3. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.5. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT156 | Single Phase Fault with Stuck Breaker on BISMARK3 115.00 (533234) 115 kV Bus a. Apply Fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.5. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT157 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT158 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT159 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT160 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT161 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT162 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.3. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT163 | Single Phase Fault with Stuck Breaker on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply Fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHAL3 (533303) 115.0 kV to KNOB HL3 (533332) 115.0 kV Transmission Circuit #1 b.2. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.4. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.5. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT164 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT165 | Single Phase Fault with Stuck Breaker on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT166 | Single Phase Fault with Stuck Breaker on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 b.3. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT167 | Single Phase Fault with Stuck Breaker on STULL T3 115.00 (533270) 115 kV Bus a. Apply Fault at the STULL T3 115.00 (533270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.3. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT168 | Single Phase Fault with Stuck Breaker on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply Fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT169 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LAWHILL1 (532882) 14.4 kV to LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT170 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 b.2. LAWHILL1 (532882) 14.4 kV to LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT171 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.7. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT172 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT173 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT174 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT175 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT176 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHX1 (532901) 14.4 kV to NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV Three Winding #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT177 | Single Phase Fault with Stuck Breaker on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.3. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.4. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT178 | Single Phase Fault with Stuck Breaker on PENTAGN3 115.00 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 115.00 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.2. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.4. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.5. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT179 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT180 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT181 | Single Phase Fault with Stuck Breaker on RENO 3 115.00 (533416) 115 kV Bus a. Apply Fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT182 | Single Phase Fault with Stuck Breaker on SALINA 3 115.00 (533376) 115 kV Bus a. Apply Fault at the SALINA 3 115.00 (533376) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT183 | Single Phase Fault with Stuck Breaker on 29EVENG3 115.00 (533185) 115 kV Bus a. Apply Fault at the 29EVENG3 115.00 (533185) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT184 | Single Phase Fault with Stuck Breaker on S GAGEE3 115.00 (533178) 115 kV Bus a. Apply Fault at the S GAGEE3 115.00 (533178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT185 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.3. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.4. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.5. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT186 | Single Phase Fault with Stuck Breaker on SWLWRNC3 115.00 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 115.00 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.8. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT187 | Single Phase Fault with Stuck Breaker on SWLWRNC3 115.00 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 115.00 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT188 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.8. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.9. AEC E1 (533886) 34.5 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.10. AEC E1 (533886) 34.5 kV to AEC W1 (533887) 34.5 kV Transmission Circuit #z1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT189 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.4. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.5. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.7. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.8. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.10. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.11. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT190 | Single Phase Fault with Stuck Breaker on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.5. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT191 | Single Phase Fault with Stuck Breaker on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT192 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.6. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.7. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.8. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT193 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.3. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.6. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT194 | Single Phase Fault with Stuck Breaker on WJCCTY 3 115.00 (533342) 115 kV Bus a. Apply Fault at the WJCCTY 3 115.00 (533342) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.5. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT195 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT196 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT197 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT198 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT199 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.6. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.7. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT200 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 b.6. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.8. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT201 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.5. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT202 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT203 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.7. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.8. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT204 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.5. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT205 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.7. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT206 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.7. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT207 | Single Phase Fault with Stuck Breaker on KSU W 3 115.00 (533333) 115 kV Bus a. Apply Fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #z1 b.2. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.3. MATTERS3 (533334) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT208 | Single Phase Fault with Stuck Breaker on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.5. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 b.6. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.7. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT209 | Single Phase Fault with Stuck Breaker on TECHILL5 161.00 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 b.6. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILW3 (533181) 115.0 kV to TECHILL5 (532920) 161.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.13. TECHIL4X (533885) 12.5 kV to TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT210 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT211 | Single Phase Fault with Stuck Breaker on 5KELSO 2 161.00 (344850) 161 kV Bus a. Apply Fault at the 5KELSO 2 161.00 (344850) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #1 b.2. 5KELSO 1 (344847) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #z b.3. 7KELSO 2 (344849) 345.0 kV to 5KELSO 2 (344850) 161.0 kV Two Winding #2 b.4. 5KELSO 2 (344850) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT212 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT213 | Single Phase Fault with Stuck Breaker on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply Fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5STEELE! (338194) 161.0 kV to 5HAYTI.S% (338200) 161.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.4. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT214 | Single Phase Fault with Stuck Breaker on 5HAYTI.S% 161.00 (338200) 161 kV Bus a. Apply Fault at the 5HAYTI.S% 161.00 (338200) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.3. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 b.4. 1HAYTI N (344720) 34.5 kV to 5HAYTI.S% (338200) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT215 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 5JIM HILL% (338202) 161.0 kV to 5RECTOR.N# (338689) 161.0 kV Transmission Circuit #1 b.4. 5PARAGOULD% (338204) 161.0 kV to 5HALLIDAY# (338709) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT216 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT217 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT218 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT219 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT220 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT221 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT222 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT223 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT224 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT225 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT226 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT227 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT228 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT229 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT230 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT231 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT232 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT233 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT234 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT235 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT236 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT237 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT238 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT239 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT240 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT241 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT242 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT243 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT244 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT245 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT246 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT247 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT248 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT249 | Single Phase Fault with Stuck Breaker on CAR395 5 161.00 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.4. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT250 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT251 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT252 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT253 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT254 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT255 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT256 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT257 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT258 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT259 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT260 | Single Phase Fault with Stuck Breaker on CAR395 5 161.00 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to A1G349 1 (547649) 13.8 kV Two Winding #1 b.4. ASB349 5 (547476) 161.0 kV to A2G349 1 (547650) 13.8 kV Two Winding #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT261 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT262 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT263 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT264 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT265 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT266 | Single Phase Fault with Stuck Breaker on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT267 | Single Phase Fault with Stuck Breaker on NEASTN5 161.0 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.0 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.5. NEASTN5 (543666) 161.0 kV to Load #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT268 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT269 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT270 | Single Phase Fault with Stuck Breaker on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT271 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT272 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT273 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT274 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT275 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT276 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT277 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT278 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT279 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 b.2. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.3. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.4. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.5. MARMTNW5 (532935) 161.0 kV to MARMATN2 (533639) 69.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT280 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.5. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.6. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.9. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT281 | Single Phase Fault with Stuck Breaker on CORONAD3 115.00 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT282 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT283 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT284 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT285 | Single Phase Fault with Stuck Breaker on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply Fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 b.2. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT286 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 b.2. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.3. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT287 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT288 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT289 | Single Phase Fault with Stuck Breaker on CGENSUB2 69.000 (533662) 69 kV Bus a. Apply Fault at the CGENSUB2 69.000 (533662) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.2. CGENTAP2 (533661) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.3. CGENSUB2 (533662) 69.0 kV to CHANP2 2 (533664) 69.0 kV Transmission Circuit #1 b.4. CGENSUB2 (533662) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT290 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT291 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT292 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT293 | Single Phase Fault with Stuck Breaker on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply Fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.3. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT294 | Single Phase Fault with Stuck Breaker on WILDCAT3 115.00 (533345) 115 kV Bus a. Apply Fault at the WILDCAT3 115.00 (533345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.3. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT295 | Single Phase Fault with Stuck Breaker on ALLEN 2 69.000 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 69.000 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.5. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT296 | Single Phase Fault with Stuck Breaker on ALLEN 2 69.000 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 69.000 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT297 | Single Phase Fault with Stuck Breaker on ATHENS 2 69.000 (533623) 69 kV Bus a. Apply Fault at the ATHENS 2 69.000 (533623) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. ATHENS 2 (533623) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.3. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.4. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT298 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 b.3. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 b.4. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.5. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 b.6. BUTLERS2 (533609) 69.0 kV to BUTLERS4 (532989) 138.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT299 | Single Phase Fault with Stuck Breaker on CHRYJCT2 69.000 (533680) 69 kV Bus a. Apply Fault at the CHRYJCT2 69.000 (533680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERRYV2 (533679) 69.0 kV to CHRYJCT2 (533680) 69.0 kV Transmission Circuit #1 b.2. CHERRYV2 (533679) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 b.3. CHRYJCT2 (533680) 69.0 kV to INDEPEN2 (533694) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT300 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.5. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.6. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT301 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 b.3. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.5. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT302 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.2. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT303 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT304 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.2. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT305 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.5. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT306 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASO 2 (533793) 69.0 kV to MULVANE2 (533821) 69.0 kV Transmission Circuit #1 b.6. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT307 | Single Phase Fault with Stuck Breaker on FTSCOTT2 69.000 (533635) 69 kV Bus a. Apply Fault at the FTSCOTT2 69.000 (533635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.4. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.5. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT308 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT309 | Single Phase Fault with Stuck Breaker on WARE 2 69.000 (533652) 69 kV Bus a. Apply Fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.5. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT310 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.6. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT311 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. SUNFLRS2 (533670) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.5. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT312 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.5. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT313 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.5. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT314 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT315 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH1 1 (532952) 13.2 kV to LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT316 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT317 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.5. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.6. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT318 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 b.4. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT319 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT320 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT321 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.3. NEC U3 (532711) 12.0 kV to NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV Three Winding #1 b.4. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT322 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.3. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT323 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. GIRARD 2 (533761) 69.0 kV to GIR JCT2 (533762) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.6. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.7. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.8. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT324 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT325 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.3. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.4. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.5. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT326 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT327 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT328 | Single Phase Fault with Stuck Breaker on PITTSBG2 69.000 (533770) 69 kV Bus a. Apply Fault at the PITTSBG2 69.000 (533770) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. HUDSON-2 (533763) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.5. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT329 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.3. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.5. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT330 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.3. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.5. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT331 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT332 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT333 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT334 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.3. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.4. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.6. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 b.7. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT335 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.4. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.6. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 b.7. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT336 | Single Phase Fault with Stuck Breaker on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.3. BU10BEN2 (533585) 69.0 kV to WEAVER 2 (533604) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.5. WEAVER 2 (533604) 69.0 kV to WEAVER 4 (532991) 138.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT337 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 b.7. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT338 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT339 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT340 | Single Phase Fault with Stuck Breaker on BAX488 5 161.00 (547729) 161 kV Bus a. Apply Fault at the BAX488 5 161.00 (547729) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT341 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.4. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT342 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.6. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT343 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT344 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT345 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT346 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT347 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT348 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT349 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT350 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT351 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT352 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT353 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT354 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT355 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT356 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT357 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT358 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT359 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT360 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT361 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT362 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT363 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT364 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT365 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT366 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT367 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT368 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT369 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT370 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT371 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT372 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT373 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT374 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT375 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT376 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT377 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT378 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT379 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT380 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT381 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT382 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT383 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT384 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT385 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT386 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT387 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT388 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT389 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT390 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT391 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT392 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT393 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT394 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT395 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT396 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT397 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT398 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT399 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT400 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT401 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT402 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT403 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT404 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.5. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT405 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT406 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT407 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT408 | Single Phase Fault with Stuck Breaker on N MADRD5 161.00 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 b.2. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.3. N MADRD5 (505400) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.4. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.5. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT409 | Single Phase Fault with Stuck Breaker on N MADRD5 161.00 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.3. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.4. N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.5. N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT410 | Single Phase Fault with Stuck Breaker on KENNETT5 161.00 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 b.2. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 b.3. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT411 | Single Phase Fault with Stuck Breaker on KENNETT5 161.00 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.2. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 b.3. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 b.4. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT412 | Single Phase Fault with Stuck Breaker on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply Fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT413 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 b.2. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 b.3. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.4. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 b.5. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X3 1 (505415) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT414 | Single Phase Fault with Stuck Breaker on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply Fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.3. SIKESTN5 (505428) 161.0 kV to SIKGEN 1 (505432) 13.8 kV Two Winding #1 b.4. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.5. SIKESTN5 (505428) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.6. SIKESTN5 (505428) 161.0 kV to SIKESTN2 (505430) 69.0 kV to SIK X1 1 (505429) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT415 | Single Phase Fault with Stuck Breaker on POP BLF5 161.00 (505438) 161 kV Bus a. Apply Fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GRNFRT (300084) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 b.2. POP BLF5 (505438) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 b.3. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X1 1 (505435) 13.8 kV Three Winding #1 b.4. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X2 1 (505437) 13.8 kV Three Winding #1 b.5. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X3 1 (505439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT416 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT417 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT418 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT419 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT420 | Single Phase Fault with Stuck Breaker on CENTR H5 161.00 (505416) 161 kV Bus a. Apply Fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 b.2. CENTR H5 (505416) 161.0 kV to JONESBO5 (505418) 161.0 kV Transmission Circuit #1 b.3. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X1 1 (505417) 13.8 kV Three Winding #1 b.4. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X2 1 (505419) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT421 | Single Phase Fault with Stuck Breaker on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply Fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5ESSEX (300075) 161.0 kV to 7ESSEX (300038) 345.0 kV Two Winding #1 b.2. 5ESSEX (300075) 161.0 kV to 5ESSEXGSU1 (301533) 161.0 kV Transmission Circuit #1 b.3. 5ESSEX (300075) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 b.4. 5ESSEX (300075) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.5. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 b.6. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 b.7. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.8. IDALIA 5 (505434) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT422 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT423 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT424 | Single Phase Fault with Stuck Breaker on STROTHR2 69.000 (533556) 69 kV Bus a. Apply Fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.2. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT425 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.0 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.0 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.3. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.4. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.5. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT426 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT427 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT428 | Single Phase Fault with Stuck Breaker on CONCRD6 230.00 (539658) 230 kV Bus a. Apply Fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT429 | Single Phase Fault with Stuck Breaker on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply Fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON1 (539655) 13.8 kV to CLIFTON3 (539656) 115.0 kV Two Winding #1 b.3. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.4. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.5. CLIFTON3 (539656) 115.0 kV to CLIFSUB1 (539704) 34.5 kV to CLIFTN-T (539903) 13.8 kV Three Winding #1 b.6. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT430 | Single Phase Fault with Stuck Breaker on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply Fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 b.4. CLIFTN-T (539903) 13.8 kV to CLIFSUB1 (539704) 34.5 kV to CLIFTON3 (539656) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT431 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT432 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT433 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT434 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT435 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT436 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP#1 (541165) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP#2 (541166) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.3. S.HARP#3 (541167) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.4. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT437 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT438 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT439 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT440 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT441 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT442 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT443 | Single Phase Fault with Stuck Breaker on METRO 5 161.00 (546742) 161 kV Bus a. Apply Fault at the METRO 5 161.00 (546742) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT444 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT445 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT446 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. KINSLEY3 (530619) 115.0 kV to GEN-2016-016 (587120) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.8. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.9. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.10. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.11. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT447 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT448 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT449 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT450 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT451 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT452 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT453 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT454 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT455 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT456 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT457 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT458 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT459 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 b.2. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT460 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.3. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.5. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.7. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.8. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT461 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT462 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT463 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT464 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT465 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT466 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT467 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT468 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT469 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT470 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT471 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT472 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT473 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT474 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT475 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT476 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT477 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage does not recover above 0.9 pu at GEN-2017-108 POI due to the inadequacy of the reactive support provided by the unit at that location following the event. | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT478 | Single Phase Fault with Stuck Breaker on 5GENTRY 161.00 (300073) 161 kV Bus a. Apply Fault at the 5GENTRY 161.00 (300073) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GENTRY (300073) 161.0 kV to 5NODWAY (300104) 161.0 kV Transmission Circuit #1 b.2. 5GENTRY (300073) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT479 | Single Phase Fault with Stuck Breaker on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply Fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.2. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT480 | Single Phase Fault with Stuck Breaker on 5HICKCK 161.00 (300087) 161 kV Bus a. Apply Fault at the 5HICKCK 161.00 (300087) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HICKCK (300087) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #1 b.2. 5HICKCK (300087) 161.0 kV to 5LOCUST (300094) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT481 | Single Phase Fault with Stuck Breaker on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply Fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5NEWMAD (300103) 161.0 kV to 5NEWMADCP (301405) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT482 | Single Phase Fault with Stuck Breaker on 5OSBORN 161.00 (300107) 161 kV Bus a. Apply Fault at the 5OSBORN 161.00 (300107) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSBORN (300107) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #1 b.2. 5OSBORN (300107) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT483 | Single Phase Fault with Stuck Breaker on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply Fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT484 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT485 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT486 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT487 | Single Phase Fault with Stuck Breaker on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply Fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2STJUDEW (300170) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT488 | Single Phase Fault with Stuck Breaker on 2JAMESN 69.000 (300202) 69 kV Bus a. Apply Fault at the 2JAMESN 69.000 (300202) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JAMESN (300202) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2JAMESN (300202) 69.0 kV to 2GALLTN (300198) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT489 | Single Phase Fault with Stuck Breaker on 2KIDDER 69.000 (300203) 69 kV Bus a. Apply Fault at the 2KIDDER 69.000 (300203) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KIDDER (300203) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2KIDDER (300203) 69.0 kV to 2MABELTP (300215) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT490 | Single Phase Fault with Stuck Breaker on 2PATBRG 69.000 (300209) 69 kV Bus a. Apply Fault at the 2PATBRG 69.000 (300209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PATBRG (300209) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2PATBRG (300209) 69.0 kV to 2BETHNY (300220) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT491 | Single Phase Fault with Stuck Breaker on 2DRLNGT 69.000 (300248) 69 kV Bus a. Apply Fault at the 2DRLNGT 69.000 (300248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DRLNGT (300248) 69.0 kV to 2ALBNYTP (300245) 69.0 kV Transmission Circuit #1 b.2. 2DRLNGT (300248) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT492 | Single Phase Fault with Stuck Breaker on 5FAIRPTB1 161.00 (301564) 161 kV Bus a. Apply Fault at the 5FAIRPTB1 161.00 (301564) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB2 (300076) 161.0 kV Two Winding #2 b.2. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB1 (301564) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT493 | Single Phase Fault with Stuck Breaker on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply Fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 b.2. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT494 | Single Phase Fault with Stuck Breaker on 2RT Z 69.000 (300325) 69 kV Bus a. Apply Fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 b.2. 2RT Z (300325) 69.0 kV to 2COLMBUS (300326) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT495 | Single Phase Fault with Stuck Breaker on 2ELM 69.000 (300327) 69 kV Bus a. Apply Fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ELM (300327) 69.0 kV to 2RT Z (300325) 69.0 kV Transmission Circuit #1 b.2. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT496 | Single Phase Fault with Stuck Breaker on 2ROSEHL 69.000 (300334) 69 kV Bus a. Apply Fault at the 2ROSEHL 69.000 (300334) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ROSEHL (300334) 69.0 kV to 2CENTRV (300323) 69.0 kV Transmission Circuit #1 b.2. 2ROSEHL (300334) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT497 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT498 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT499 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT500 | Single Phase Fault with Stuck Breaker on 2IVYBND 69.000 (300557) 69 kV Bus a. Apply Fault at the 2IVYBND 69.000 (300557) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IVYBND (300557) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 b.2. 2IVYBND (300557) 69.0 kV to 2VERSAL (300565) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT501 | Single Phase Fault with Stuck Breaker on 2MTHULD 69.000 (300558) 69 kV Bus a. Apply Fault at the 2MTHULD 69.000 (300558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTHULD (300558) 69.0 kV to 2LINCLN (300534) 69.0 kV Transmission Circuit #1 b.2. 2MTHULD (300558) 69.0 kV to 2IVYBND (300557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT502 | Single Phase Fault with Stuck Breaker on 2APPLTN 69.000 (300687) 69 kV Bus a. Apply Fault at the 2APPLTN 69.000 (300687) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2APPLTN (300687) 69.0 kV to 2LADUE (300702) 69.0 kV Transmission Circuit #1 b.2. 2APPLTN (300687) 69.0 kV to 2TABORVL (300813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT503 | Single Phase Fault with Stuck Breaker on 2AUSTIN 69.000 (300688) 69 kV Bus a. Apply Fault at the 2AUSTIN 69.000 (300688) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AUSTIN (300688) 69.0 kV to 2ELYNTP (300699) 69.0 kV Transmission Circuit #1 b.2. 2AUSTIN (300688) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT504 | Single Phase Fault with Stuck Breaker on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply Fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV Two Winding #1 b.2. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT505 | Single Phase Fault with Stuck Breaker on 2BUTLERE 69.000 (300690) 69 kV Bus a. Apply Fault at the 2BUTLERE 69.000 (300690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BUTLERE (300690) 69.0 kV to 2BUTLER (300689) 69.0 kV Transmission Circuit #1 b.2. 2BUTLERE (300690) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT506 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 b.2. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT507 | Single Phase Fault with Stuck Breaker on 2CREIGH 69.000 (300696) 69 kV Bus a. Apply Fault at the 2CREIGH 69.000 (300696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CREIGH (300696) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 b.2. 2CREIGH (300696) 69.0 kV to 2AUSTIN (300688) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT508 | Single Phase Fault with Stuck Breaker on 2GAINES 69.000 (300701) 69 kV Bus a. Apply Fault at the 2GAINES 69.000 (300701) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GAINES (300701) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2GAINES (300701) 69.0 kV to 2MTZION (300810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT509 | Single Phase Fault with Stuck Breaker on 2LADUE 69.000 (300702) 69 kV Bus a. Apply Fault at the 2LADUE 69.000 (300702) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LADUE (300702) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 b.2. 2LADUE (300702) 69.0 kV to 2APPLTN (300687) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT510 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT511 | Single Phase Fault with Stuck Breaker on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply Fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2MTZION (300810) 69.0 kV Transmission Circuit #1 b.2. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT512 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT513 | Single Phase Fault with Stuck Breaker on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply Fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AIDJCT (301191) 69.0 kV to 2BLOOMF (301237) 69.0 kV Transmission Circuit #1 b.2. 2AIDJCT (301191) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT514 | Single Phase Fault with Stuck Breaker on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply Fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ADVANC (301235) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 b.2. 2ADVANC (301235) 69.0 kV to 2WHTWTR (301279) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT515 | Single Phase Fault with Stuck Breaker on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply Fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ANNSTN (301236) 69.0 kV to 2LILBRN (301246) 69.0 kV Transmission Circuit #1 b.2. 2ANNSTN (301236) 69.0 kV to 2DOGWOD (301239) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT516 | Single Phase Fault with Stuck Breaker on 2BLOOMF 69.000 (301237) 69 kV Bus a. Apply Fault at the 2BLOOMF 69.000 (301237) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BLOOMF (301237) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2BLOOMF (301237) 69.0 kV to 2AIDJCT (301191) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT517 | Single Phase Fault with Stuck Breaker on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply Fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FRISCO (301240) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2FRISCO (301240) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT518 | Single Phase Fault with Stuck Breaker on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply Fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 b.2. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT519 | Single Phase Fault with Stuck Breaker on 2IDALMA 69.000 (301244) 69 kV Bus a. Apply Fault at the 2IDALMA 69.000 (301244) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IDALMA (301244) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2IDALMA (301244) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT520 | Single Phase Fault with Stuck Breaker on 2MOREHS 69.000 (301248) 69 kV Bus a. Apply Fault at the 2MOREHS 69.000 (301248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOREHS (301248) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 b.2. 2MOREHS (301248) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT521 | Single Phase Fault with Stuck Breaker on 2MOREJT 69.000 (301249) 69 kV Bus a. Apply Fault at the 2MOREJT 69.000 (301249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOREJT (301249) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 b.2. 2MOREJT (301249) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT522 | Single Phase Fault with Stuck Breaker on 2PARMA 69.000 (301250) 69 kV Bus a. Apply Fault at the 2PARMA 69.000 (301250) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PARMA (301250) 69.0 kV to 2FRISCO (301240) 69.0 kV Transmission Circuit #1 b.2. 2PARMA (301250) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT523 | Single Phase Fault with Stuck Breaker on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply Fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AVONKN (301285) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 b.2. 2AVONKN (301285) 69.0 kV to 2GIDJCT (301293) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT524 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT525 | Single Phase Fault with Stuck Breaker on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply Fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KELSO 1 (344847) 161.0 kV to 7KELSO 1 (344848) 345.0 kV Two Winding #1 b.2. 5KELSO 1 (344847) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT526 | Single Phase Fault with Stuck Breaker on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply Fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MINER 1 (345203) 161.0 kV to 5KELSO 1 (344847) 161.0 kV Transmission Circuit #1 b.2. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT527 | Single Phase Fault with Stuck Breaker on 5RIDGELY TN 161.00 (360521) 161 kV Bus a. Apply Fault at the 5RIDGELY TN 161.00 (360521) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RIDGELY TN (360521) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5RIDGELY TN (360521) 161.0 kV to 5NAUVOO TN (360479) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT528 | Single Phase Fault with Stuck Breaker on 5TIPTONVL TN161.00 (361261) 161 kV Bus a. Apply Fault at the 5TIPTONVL TN161.00 (361261) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5TIPTONVL TN (361261) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5TIPTONVL TN (361261) 161.0 kV to 5RIDGELY TN (360521) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT529 | Single Phase Fault with Stuck Breaker on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply Fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT530 | Single Phase Fault with Stuck Breaker on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply Fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT531 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT532 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT533 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT534 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT535 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT536 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT537 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to GEN-2017-125 (761901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT538 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT539 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT540 | Single Phase Fault with Stuck Breaker on EXPED WF7 345.00 (532790) 345 kV Bus a. Apply Fault at the EXPED WF7 345.00 (532790) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPED WF7 (532790) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EXPED WF7 (532790) 345.0 kV to E1 TX1 (534048) 34.5 kV to E1 TERT1 (534049) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT541 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT542 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT543 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT544 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT545 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT546 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT547 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT548 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT549 | Single Phase Fault with Stuck Breaker on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply Fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT550 | Single Phase Fault with Stuck Breaker on BERG 3 115.00 (533367) 115 kV Bus a. Apply Fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 b.2. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT551 | Single Phase Fault with Stuck Breaker on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply Fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT552 | Single Phase Fault with Stuck Breaker on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. MOUNDRG3 (533429) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT553 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT554 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT555 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT556 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT557 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT558 | Single Phase Fault with Stuck Breaker on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply Fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT559 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips Outlaw (541546, 541549 and 541550) and Rock Creek Unit (541514). | Protections at Outlaw and Rock Creek were disabled with no impact on system stability.
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT560 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT561 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT562 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT563 | Single Phase Fault with Stuck Breaker on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply Fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT564 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT565 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT566 | Single Phase Fault with Stuck Breaker on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. PLTCTY 5 (541221) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT567 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT568 | Single Phase Fault with Stuck Breaker on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply Fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARYVLE5 (541251) 161.0 kV to 5MARYVB2 (300097) 161.0 kV Transmission Circuit #1 b.2. MARYVLE5 (541251) 161.0 kV to BRADDYVILLE5 (635038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT569 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT570 | Single Phase Fault with Stuck Breaker on EAST 5 161.00 (541254) 161 kV Bus a. Apply Fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT571 | Single Phase Fault with Stuck Breaker on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply Fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 b.2. LAKE RD5 (541255) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT572 | Single Phase Fault with Stuck Breaker on IND PRK5 161.00 (541256) 161 kV Bus a. Apply Fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 b.2. IND PRK5 (541256) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT573 | Single Phase Fault with Stuck Breaker on COOK 5 161.00 (541257) 161 kV Bus a. Apply Fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOK 5 (541257) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT574 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 b.2. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT575 | Single Phase Fault with Stuck Breaker on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply Fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT576 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT577 | Single Phase Fault with Stuck Breaker on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply Fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT578 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT579 | Single Phase Fault with Stuck Breaker on BELTONS5 161.00 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 b.2. BELTONS5 (541340) 161.0 kV to TURNER_RD5 (541259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT580 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 b.2. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT581 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT582 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT583 | Single Phase Fault with Stuck Breaker on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply Fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDWAY_5 (541369) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 b.2. MIDWAY_5 (541369) 161.0 kV to MARYVLE5 (541251) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT584 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT585 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT586 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT587 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT588 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT589 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT590 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT591 | Single Phase Fault with Stuck Breaker on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply Fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PFLUMM 5 (542979) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT592 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT593 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT594 | Single Phase Fault with Stuck Breaker on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply Fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT595 | Single Phase Fault with Stuck Breaker on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 b.2. STHTOWN5 (542993) 161.0 kV to BENDIX 5 (542992) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT596 | Single Phase Fault with Stuck Breaker on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply Fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT597 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT598 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT599 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT600 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to BARRY_CAP 5 (542944) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT601 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT602 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT603 | Single Phase Fault with Stuck Breaker on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply Fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 b.2. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT604 | Single Phase Fault with Stuck Breaker on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply Fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 b.2. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT605 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT606 | Single Phase Fault with Stuck Breaker on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply Fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. MOONLT 5 (543044) 161.0 kV to QUARRY 5 (543037) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT607 | Single Phase Fault with Stuck Breaker on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply Fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 b.2. OXFORD 5 (543046) 161.0 kV to OLATHE 5 (543036) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT608 | Single Phase Fault with Stuck Breaker on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply Fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 b.2. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT609 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT610 | Single Phase Fault with Stuck Breaker on CENTENL5 161.00 (543067) 161 kV Bus a. Apply Fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 b.2. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT611 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT612 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT613 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT614 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT615 | Single Phase Fault with Stuck Breaker on G14-001-TAP 345.00 (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP 345.00 (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. G14-001-TAP (562476) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT616 | Single Phase Fault with Stuck Breaker on GEN-2016-111345.00 (587880) 345 kV Bus a. Apply Fault at the GEN-2016-111345.00 (587880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-111 (587880) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-111 (587880) 345.0 kV to G16-111XFMR1 (587881) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT617 | Single Phase Fault with Stuck Breaker on GEN-2017-004345.00 (588490) 345 kV Bus a. Apply Fault at the GEN-2017-004345.00 (588490) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-004 (588490) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-004 (588490) 345.0 kV to G17-004XFMR1 (588491) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT618 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT619 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT620 | Single Phase Fault with Stuck Breaker on GEN-2017-202161.00 (761418) 161 kV Bus a. Apply Fault at the GEN-2017-202161.00 (761418) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-202 (761418) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-202 (761418) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT621 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GIBSON (301291) 69.0 kV to 5GIBSON (300083) 161.0 kV Two Winding #1 b.2. 2GIBSON (301291) 69.0 kV to 2CAMBEL (301196) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT622 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 b.2. 2HOLDEN (300336) 69.0 kV to 2CENTRV (300323) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT623 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT624 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT625 | Single Phase Fault with Stuck Breaker on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply Fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #1 b.2. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT626 | Single Phase Fault with Stuck Breaker on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply Fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #z1 b.2. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT627 | Single Phase Fault with Stuck Breaker on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply Fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 b.2. 7KELSO 1 (344848) 345.0 kV to 7KELSO 2 (344849) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT628 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.2. PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT629 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to DELWARE4 (510379) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to SCOFCTY4 (510378) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT630 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL6 (532857) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT631 | Single Phase Fault with Stuck Breaker on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply Fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT6 (532861) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT632 | Single Phase Fault with Stuck Breaker on TECHILL5 161.00 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL5 (532920) 161.0 kV to KELLY 5 (532913) 161.0 kV Transmission Circuit #1 b.2. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT633 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 b.2. OTTRCRK4 (532997) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT634 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUND 4 (533013) 138.0 kV to MOUND 2 (533742) 69.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 b.2. MOUND 4 (533013) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT635 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 b.2. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT636 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 b.2. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT637 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 b.2. FRANKLIN2 (533876) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT638 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTN N2 (541303) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT639 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 b.2. CLNTN S2 (541320) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT640 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP 2 (541343) 69.0 kV to FREEMAN2 (541291) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT641 | Single Phase Fault with Stuck Breaker on EDMOND5 161.00 (541355) 161 kV Bus a. Apply Fault at the EDMOND5 161.00 (541355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDMOND5 (541355) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. EDMOND5 (541355) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT642 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT643 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT644 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTON5 (541242) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #z1 b.2. CLINTON5 (541242) 161.0 kV to CLNTN N2 (541303) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT645 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT646 | Single Phase Fault with Stuck Breaker on 5NODWAY 161.00 (300104) 161 kV Bus a. Apply Fault at the 5NODWAY 161.00 (300104) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NODWAY (300104) 161.0 kV to 5GENTRY (300073) 161.0 kV Transmission Circuit #1 b.2. 5NODWAY (300104) 161.0 kV to 5MARYVLB1 (301592) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT647 | Single Phase Fault with Stuck Breaker on 5WINSLOW 161.00 (301347) 161 kV Bus a. Apply Fault at the 5WINSLOW 161.00 (301347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5WINSLOW (301347) 161.0 kV to 1WINSLOW (301356) 34.5 kV Two Winding #1 b.2. 5WINSLOW (301347) 161.0 kV to 1WINSLOW (301356) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT648 | Single Phase Fault with Stuck Breaker on 5FAIRPTB1 161.00 (301564) 161 kV Bus a. Apply Fault at the 5FAIRPTB1 161.00 (301564) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5FAIRPTB1 (301564) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #z1 b.2. 5FAIRPTB1 (301564) 161.0 kV to 5OSBORN (300107) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT649 | Single Phase Fault with Stuck Breaker on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply Fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5COLLINS (300816) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT650 | Single Phase Fault with Stuck Breaker on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply Fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOL (301040) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOL (301040) 161.0 kV to 2OSCEOL (300811) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT651 | Single Phase Fault with Stuck Breaker on 5HOLDENB1 161.00 (301561) 161 kV Bus a. Apply Fault at the 5HOLDENB1 161.00 (301561) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB1 (301561) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #z1 b.2. 5HOLDENB1 (301561) 161.0 kV to 5PITTSV (300110) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT652 | Single Phase Fault with Stuck Breaker on 2BAELLS 69.000 (301286) 69 kV Bus a. Apply Fault at the 2BAELLS 69.000 (301286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BAELLS (301286) 69.0 kV to 2STJUDEW (300170) 69.0 kV Transmission Circuit #1 b.2. 2BAELLS (301286) 69.0 kV to 2AVONKN (301285) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT653 | Single Phase Fault with Stuck Breaker on 2KINGCT 69.000 (300257) 69 kV Bus a. Apply Fault at the 2KINGCT 69.000 (300257) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KINGCT (300257) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2KINGCT (300257) 69.0 kV to 2FLGGSP (300251) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT654 | Single Phase Fault with Stuck Breaker on 2MAYSVL 69.000 (300259) 69 kV Bus a. Apply Fault at the 2MAYSVL 69.000 (300259) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MAYSVL (300259) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2MAYSVL (300259) 69.0 kV to 2STEWRV (300268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT655 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT656 | Single Phase Fault with Stuck Breaker on 2PIPER 69.000 (300706) 69 kV Bus a. Apply Fault at the 2PIPER 69.000 (300706) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PIPER (300706) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2PIPER (300706) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT657 | Single Phase Fault with Stuck Breaker on 2LEETON 69.000 (300703) 69 kV Bus a. Apply Fault at the 2LEETON 69.000 (300703) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LEETON (300703) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 b.2. 2LEETON (300703) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT658 | Single Phase Fault with Stuck Breaker on 2CLINTNLD 69.000 (301626) 69 kV Bus a. Apply Fault at the 2CLINTNLD 69.000 (301626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTNLD (301626) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2CLINTNLD (301626) 69.0 kV to 2LADUE (300702) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT659 | Single Phase Fault with Stuck Breaker on 2MTZION 69.000 (300810) 69 kV Bus a. Apply Fault at the 2MTZION 69.000 (300810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTZION (300810) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 b.2. 2MTZION (300810) 69.0 kV to 2DAMSCUS (300804) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT660 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT661 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT662 | Single Phase Fault with Stuck Breaker on GI94_POI 345.00 (709400) 345 kV Bus a. Apply Fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. GI94_POI (709400) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT663 | Single Phase Fault with Stuck Breaker on 2ARDEOLA 69.000 (301257) 69 kV Bus a. Apply Fault at the 2ARDEOLA 69.000 (301257) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ARDEOLA (301257) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2ARDEOLA (301257) 69.0 kV to 2ADVANC (301235) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT664 | Single Phase Fault with Stuck Breaker on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply Fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 b.2. 2DOGWOD (301239) 69.0 kV to 2ANNSTN (301236) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT665 | Single Phase Fault with Stuck Breaker on 2LILBRN 69.000 (301246) 69 kV Bus a. Apply Fault at the 2LILBRN 69.000 (301246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2LILBRN (301246) 69.0 kV to 2ANNSTN (301236) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT666 | Single Phase Fault with Stuck Breaker on 2VANDSR 69.000 (301251) 69 kV Bus a. Apply Fault at the 2VANDSR 69.000 (301251) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VANDSR (301251) 69.0 kV to 2MORLEY (301255) 69.0 kV Transmission Circuit #1 b.2. 2VANDSR (301251) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT667 | Single Phase Fault with Stuck Breaker on 5VIAD_TP 161.00 (345891) 161 kV Bus a. Apply Fault at the 5VIAD_TP 161.00 (345891) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5VIAD_TP (345891) 161.0 kV to 5VIADUCT 3 (345892) 161.0 kV Transmission Circuit #1 b.2. 5VIAD_TP (345891) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT668 | Single Phase Fault with Stuck Breaker on 5POLK TP 161.00 (361596) 161 kV Bus a. Apply Fault at the 5POLK TP 161.00 (361596) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5POLK TP (361596) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5POLK TP (361596) 161.0 kV to 5TROY TN (361422) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT669 | Single Phase Fault with Stuck Breaker on EXPEDITION7 345.00 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. EXPEDITION7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT670 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT671 | Single Phase Fault with Stuck Breaker on G17-004-TAP 345.00 (588494) 345 kV Bus a. Apply Fault at the G17-004-TAP 345.00 (588494) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-004-TAP (588494) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G17-004-TAP (588494) 345.0 kV to ELMCREEK7 (539805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT672 | Single Phase Fault with Stuck Breaker on GEN-2017-125345.00 (761901) 345 kV Bus a. Apply Fault at the GEN-2017-125345.00 (761901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT673 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G17-086XFMR (589241) 34.5 kV Two Winding #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT674 | Single Phase Fault with Stuck Breaker on G17-209-TAP 345.00 (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP 345.00 (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT675 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT676 | Single Phase Fault with Stuck Breaker on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply Fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACKMAN5 (543126) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. LACKMAN5 (543126) 161.0 kV to SPRGHL 5 (532914) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT677 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT678 | Single Phase Fault with Stuck Breaker on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply Fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT679 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK3 (533315) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #2 b.2. OTTRCRK3 (533315) 115.0 kV to OTTRCRK4 (532997) 138.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT680 | Single Phase Fault with Stuck Breaker on SCHILNG3 115.00 (533377) 115 kV Bus a. Apply Fault at the SCHILNG3 115.00 (533377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHILNG3 (533377) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 b.2. SCHILNG3 (533377) 115.0 kV to CRAWFRD3 (533364) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT681 | Single Phase Fault with Stuck Breaker on CHANTAP2 69.000 (533666) 69 kV Bus a. Apply Fault at the CHANTAP2 69.000 (533666) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHANTAP2 (533666) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.2. CHANTAP2 (533666) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT682 | Single Phase Fault with Stuck Breaker on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply Fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHGRJ22 (533660) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.2. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT683 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT684 | Single Phase Fault with Stuck Breaker on SOPITT 2 69.000 (533773) 69 kV Bus a. Apply Fault at the SOPITT 2 69.000 (533773) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOPITT 2 (533773) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 b.2. SOPITT 2 (533773) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT685 | Single Phase Fault with Stuck Breaker on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. ELMCREK6 (539639) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT686 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT687 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT688 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT689 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT690 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT691 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT692 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT693 | Single Phase Fault with Stuck Breaker on WESTON 5 161.00 (541351) 161 kV Bus a. Apply Fault at the WESTON 5 161.00 (541351) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTON 5 (541351) 161.0 kV to IATAN5 (541350) 161.0 kV Transmission Circuit #1 b.2. WESTON 5 (541351) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT694 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT695 | Single Phase Fault with Stuck Breaker on WOODBIN5 161.00 (541258) 161 kV Bus a. Apply Fault at the WOODBIN5 161.00 (541258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODBIN5 (541258) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. WOODBIN5 (541258) 161.0 kV to EAST 5 (541254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT696 | Single Phase Fault with Stuck Breaker on AVENUECTY 5 161.00 (541394) 161 kV Bus a. Apply Fault at the AVENUECTY 5 161.00 (541394) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVENUECTY 5 (541394) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. AVENUECTY 5 (541394) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT697 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT698 | Single Phase Fault with Stuck Breaker on STALEY 2 69.000 (541261) 69 kV Bus a. Apply Fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STALEY 2 (541261) 69.0 kV to RNRDGE 2 (541260) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT699 | Single Phase Fault with Stuck Breaker on URICHTP2 69.000 (541304) 69 kV Bus a. Apply Fault at the URICHTP2 69.000 (541304) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. URICHTP2 (541304) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT700 | Single Phase Fault with Stuck Breaker on PECULRS5 161.00 (541344) 161 kV Bus a. Apply Fault at the PECULRS5 161.00 (541344) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULRS5 (541344) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 b.2. PECULRS5 (541344) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT701 | Single Phase Fault with Stuck Breaker on CEDRCRK5 161.00 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 161.00 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. CEDRCRK5 (543049) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT702 | Single Phase Fault with Stuck Breaker on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. PLSTVAL5 (543077) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT703 | Single Phase Fault with Stuck Breaker on BNSF 5 161.00 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 161.00 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. BNSF 5 (543132) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT704 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT705 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT706 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT707 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT708 | Single Phase Fault with Stuck Breaker on COLLEGE5 161.00 (543048) 161 kV Bus a. Apply Fault at the COLLEGE5 161.00 (543048) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLLEGE5 (543048) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. COLLEGE5 (543048) 161.0 kV to OLATHE 5 (543036) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT709 | Single Phase Fault with Stuck Breaker on OVERLPK5 161.00 (543047) 161 kV Bus a. Apply Fault at the OVERLPK5 161.00 (543047) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVERLPK5 (543047) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 b.2. OVERLPK5 (543047) 161.0 kV to BRKRIDG5 (543033) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT710 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT711 | Single Phase Fault with Stuck Breaker on BUNKRDG5 161.00 (543008) 161 kV Bus a. Apply Fault at the BUNKRDG5 161.00 (543008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUNKRDG5 (543008) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BUNKRDG5 (543008) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT712 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT713 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT714 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT715 | Single Phase Fault with Stuck Breaker on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply Fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MERRIAM5 (543032) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. MERRIAM5 (543032) 161.0 kV to MERRIAM_CAP5 (542947) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT716 | Single Phase Fault with Stuck Breaker on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply Fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT717 | Single Phase Fault with Stuck Breaker on REEDER 5 161.00 (543052) 161 kV Bus a. Apply Fault at the REEDER 5 161.00 (543052) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REEDER 5 (543052) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 b.2. REEDER 5 (543052) 161.0 kV to KNLWRTH5 (543034) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT718 | Single Phase Fault with Stuck Breaker on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 b.2. S.OTTWA5 (543066) 161.0 kV to S.OTTWA21 (543121) 34.5 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT719 | Single Phase Fault with Stuck Breaker on WAGSTAF5 161.00 (543068) 161 kV Bus a. Apply Fault at the WAGSTAF5 161.00 (543068) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGSTAF5 (543068) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. WAGSTAF5 (543068) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT720 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STL439 5 (547498) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. STL439 5 (547498) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT721 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT722 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT723 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to G14-001XFMR1 (583851) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT724 | Single Phase Fault with Stuck Breaker on G17-022-TAP 138.00 (588664) 138 kV Bus a. Apply Fault at the G17-022-TAP 138.00 (588664) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-022-TAP (588664) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. G17-022-TAP (588664) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT725 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT726 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT727 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT728 | Single Phase Fault with Stuck Breaker on G17-120-TAP 115.00 (760007) 115 kV Bus a. Apply Fault at the G17-120-TAP 115.00 (760007) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-120-TAP (760007) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. G17-120-TAP (760007) 115.0 kV to AEC 3 (533361) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT729 | Single Phase Fault with Stuck Breaker on G17-202-TAP 161.00 (761422) 161 kV Bus a. Apply Fault at the G17-202-TAP 161.00 (761422) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-202-TAP (761422) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 b.2. G17-202-TAP (761422) 161.0 kV to GEN-2017-202 (761418) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT730 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 2GIBSON (301291) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT731 | Single Phase Fault with Stuck Breaker on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply Fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHRVL5 (505441) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.2. ASHRVL5 (505441) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT732 | Single Phase Fault with Stuck Breaker on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply Fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7NEWMADXF12 (301530) 345.0 kV to 7NEWMAD (300046) 345.0 kV Transmission Circuit #z1 b.2. 7NEWMADXF12 (301530) 345.0 kV to 5NEWMADXF12 (301531) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT733 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.2. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT734 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT735 | Single Phase Fault with Stuck Breaker on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 b.2. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT736 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT737 | Single Phase Fault with Stuck Breaker on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply Fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT3 (533326) 115.0 kV to EMANHAT6 (532861) 230.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 b.2. EMANHAT3 (533326) 115.0 kV to LEVEE 3 (533327) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT738 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRINGH3 (533267) 115.0 kV to SPRGHL 5 (532914) 161.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.2. SPRINGH3 (533267) 115.0 kV to BONITA 3 (533262) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT739 | Single Phase Fault with Stuck Breaker on TECHILW3 115.00 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT740 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to CRESWLS2 (533573) 69.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 b.2. CRESWLN4 (532981) 138.0 kV to CRESWLN2 (533543) 69.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT741 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT4 (532992) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT742 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT743 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT744 | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage does not recover above 0.9 pu at GEN-2017-108 POI due to the inadequacy of the reactive support provided by the unit at that location following the event. | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT745 | Single Phase Fault with Stuck Breaker on 5SEDALA (300117) 161 kV Bus a. Apply Fault at the 5SEDALA (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT746 | Single Phase Fault with Stuck Breaker on 2HOLDEN (300336) 69 kV Bus a. Apply Fault at the 2HOLDEN (300336) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HOLDEN (300336) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT747 | Single Phase Fault with Stuck Breaker on 2CENTRV (300323) 69 kV Bus a. Apply Fault at the 2CENTRV (300323) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CENTRV (300323) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT748 | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT749 | Single Phase Fault with Stuck Breaker on STHTOWN5 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT750 | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT751 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT752 | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT753 | Single Phase Fault with Stuck Breaker on PECULR 5 (541342) 161 kV Bus a. Apply Fault at the PECULR 5 (541342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT754 | Single Phase Fault with Stuck Breaker on BELTONS5 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT755 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT756 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT757 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT758 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT759 | Single Phase Fault with Stuck Breaker on NMANHT3 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHT3 (533347) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT760 | Single Phase Fault with Stuck Breaker on SUMMIT 7 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT761 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT762 | Single Phase Fault with Stuck Breaker on GEARY 3 (533336) 115 kV Bus a. Apply Fault at the GEARY 3 (533336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 3 (533336) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT763 | Single Phase Fault with Stuck Breaker on MCDOWEL3 (533335) 115 kV Bus a. Apply Fault at the MCDOWEL3 (533335) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL3 (533335) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT764 | Single Phase Fault with Stuck Breaker on GEARY 7 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 7 (532767) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT765 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT766 | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT767 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT768 | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT769 | Single Phase Fault with Stuck Breaker on SUMMIT 3 (533381) 115 kV Bus a. Apply Fault at the SUMMIT 3 (533381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 3 (533381) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT770 | Single Phase Fault with Stuck Breaker on MENTOR 3 (533374) 115 kV Bus a. Apply Fault at the MENTOR 3 (533374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT771 | Single Phase Fault with Stuck Breaker on NORTHVW3 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT772 | Single Phase Fault with Stuck Breaker on CRESWLN4 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT773 | Single Phase Fault with Stuck Breaker on TIMBJCT2 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT774 | Single Phase Fault with Stuck Breaker on CRESWLN2 (533543) 69 kV Bus a. Apply Fault at the CRESWLN2 (533543) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT775 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT776 | Single Phase Fault with Stuck Breaker on GILL 4 (533047) 138 kV Bus a. Apply Fault at the GILL 4 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT777 | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT778 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT779 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT780 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT781 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT782 | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT783 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT784 | Single Phase Fault with Stuck Breaker on CEDRCRK5 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT785 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT786 | Single Phase Fault with Stuck Breaker on SWISVAL6 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT787 | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT788 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT789 | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT790 | Single Phase Fault with Stuck Breaker on TECHILW3 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT791 | Single Phase Fault with Stuck Breaker on LWRNCHL3 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LWRNCHL3 (533250) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT792 | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT793 | Single Phase Fault with Stuck Breaker on TIOGA 2 (533646) 69 kV Bus a. Apply Fault at the TIOGA 2 (533646) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 2 (533646) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT794 | Single Phase Fault with Stuck Breaker on ALTOO E2 (533673) 69 kV Bus a. Apply Fault at the ALTOO E2 (533673) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOO E2 (533673) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT795 | Single Phase Fault with Stuck Breaker on MONTGOM4 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM4 (533004) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT796 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT797 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT798 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT799 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT800 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT801 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT802 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT803 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT804 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT805 | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT806 | Single Phase Fault with Stuck Breaker on SMTHVL 5 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT807 | Single Phase Fault with Stuck Breaker on NASHUA 5 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT808 | Single Phase Fault with Stuck Breaker on NASHUA-5 (543028) 161 kV Bus a. Apply Fault at the NASHUA-5 (543028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT809 | Single Phase Fault with Stuck Breaker on RNRIDGE5 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT810 | Single Phase Fault with Stuck Breaker on HAWTHS5 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT811 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT812 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT813 | Single Phase Fault with Stuck Breaker on EASTOWN5 (541401) 161 kV Bus a. Apply Fault at the EASTOWN5 (541401) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT814 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT815 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT816 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT817 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT818 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT819 | Single Phase Fault with Stuck Breaker on MIDWAY_5 (541369) 161 kV Bus a. Apply Fault at the MIDWAY_5 (541369) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDWAY_5 (541369) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT820 | Single Phase Fault with Stuck Breaker on LITCH 5 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT821 | Single Phase Fault with Stuck Breaker on ORO110 5 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT822 | Single Phase Fault with Stuck Breaker on ORO110 2 (547534) 69 kV Bus a. Apply Fault at the ORO110 2 (547534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT823 | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT824 | Single Phase Fault with Stuck Breaker on FRANKLIN2 (533876) 69 kV Bus a. Apply Fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN2 (533876) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT825 | Single Phase Fault with Stuck Breaker on AUBURN 6 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT826 | Single Phase Fault with Stuck Breaker on PLSTVAL5 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT827 | Single Phase Fault with Stuck Breaker on MOONLT 5 (543044) 161 kV Bus a. Apply Fault at the MOONLT 5 (543044) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLT 5 (543044) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT828 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT829 | Single Phase Fault with Stuck Breaker on 87TH 7 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT830 | Single Phase Fault with Stuck Breaker on 87TH 3 (533283) 115 kV Bus a. Apply Fault at the 87TH 3 (533283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 3 (533283) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT831 | Single Phase Fault with Stuck Breaker on SIKETAP5 (505427) 161 kV Bus a. Apply Fault at the SIKETAP5 (505427) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIKETAP5 (505427) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT832 | Single Phase Fault with Stuck Breaker on N MADRD2 (505402) 69 kV Bus a. Apply Fault at the N MADRD2 (505402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT833 | Single Phase Fault with Stuck Breaker on N MADRD5 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD5 (505400) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT834 | Single Phase Fault with Stuck Breaker on KENNETT5 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENNETT5 (505410) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT835 | Single Phase Fault with Stuck Breaker on PARAGLD5 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT836 | Single Phase Fault with Stuck Breaker on 2BAELLS (301286) 69 kV Bus a. Apply Fault at the 2BAELLS (301286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BAELLS (301286) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT837 | Single Phase Fault with Stuck Breaker on 2ANNSTN (301236) 69 kV Bus a. Apply Fault at the 2ANNSTN (301236) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ANNSTN (301236) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT838 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT839 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT840 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT841 | Single Phase Fault with Stuck Breaker on MARMATN2 (533639) 69 kV Bus a. Apply Fault at the MARMATN2 (533639) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT842 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT843 | Single Phase Fault with Stuck Breaker on SOPITT 2 (533773) 69 kV Bus a. Apply Fault at the SOPITT 2 (533773) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOPITT 2 (533773) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT844 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT845 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT846 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT847 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT848 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT849 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT850 | Single Phase Fault with Stuck Breaker on EXPEDITION7 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT851 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT852 | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT853 | Single Phase Fault with Stuck Breaker on CIRCLE 3 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT854 | Single Phase Fault with Stuck Breaker on MOUNDRG3 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT855 | Single Phase Fault with Stuck Breaker on CHISHLM4 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT856 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT1 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT2 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT3 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT4 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT5 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT6 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT7 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT8 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT9 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT10 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT11 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT12 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT13 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT14 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT15 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT16 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT17 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT18 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT19 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT20 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT21 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT22 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT23 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT24 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT25 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes