04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WARWICK4_WFROSST4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO WFROSST4 138.0 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WARWICK4_WFROSST4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO WFROSST4 138.0 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WATNGSW4_CALUMET4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WATNGSW4_CALUMET4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WATNGSW4_OKEENE_4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WATNGSW4_OKEENE_4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WATNGSW4_OMEGA_4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WATNGSW4_OMEGA_4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WATNGSW4_WATONGA4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WATNGSW4_WATONGA4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WAUKOTP4_BULFTTP4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.4. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WAUKOTP4_BULFTTP4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.4. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WAUKOTP4_SO4TH_4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WAUKOTP4_SO4TH_4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WAUKOTP4_WOODRNG4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WAUKOTP4_WOODRNG4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WBOONVL2_507192 | 3 Phase fault on WBOONVL2 (507198) 69 kV Bus a. Apply fault at the WBOONVL2( 507198) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL2 507198 TO WBOONVL5 507192 TO WBOONVL1 507181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WBOONVL2_507192 | 3 Phase fault on WBOONVL2 (507198) 69 kV Bus a. Apply fault at the WBOONVL2( 507198) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL2 507198 TO WBOONVL5 507192 TO WBOONVL1 507181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WBOONVL5_NHUNTNT5 | 3 Phase fault on WBOONVL5 (507192) 161 kV Bus a. Apply fault at the WBOONVL5 (507192) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL5 161.0 KV 507192 TO NHUNTNT5 161.0 KV 507189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WBOONVL5_NHUNTNT5 | 3 Phase fault on WBOONVL5 (507192) 161 kV Bus a. Apply fault at the WBOONVL5 (507192) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL5 161.0 KV 507192 TO NHUNTNT5 161.0 KV 507189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WEDINGTON5_WEDINGTON_7 | 3 Phase fault on WEDINGTON5 (504275) 161 kV Bus a. Apply fault at the WEDINGTON5 (504275) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEDINGTON5 161.0 KV 504275 TO WEDINGTON 161.0 KV 506992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WEDINGTON5_WEDINGTON_7 | 3 Phase fault on WEDINGTON5 (504275) 161 kV Bus a. Apply fault at the WEDINGTON5 (504275) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEDINGTON5 161.0 KV 504275 TO WEDINGTON 161.0 KV 506992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WEKIWA__SAPLPRD7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WEKIWA__SAPLPRD7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WEKIWA__SOONER7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WEKIWA__SOONER7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WEKIWA__TNO7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WEKIWA__TNO7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WEKIWA4_509755 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WEKIWA4_509755 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WFROSST4_LINCOLN4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WFROSST4_LINCOLN4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WFROSST4_RSSVILE4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO RSSVILE4 138.0 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WFROSST4_RSSVILE4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO RSSVILE4 138.0 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WICHITA7_532796 | a. Apply single-phase fault on: a.1. WICHITA7 345.0 KV 532796 TO BENTON 7 345.0 KV 532791 CKT 1, b. with stuck breaker near WICHITA7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. RENO 7 345.0 KV 532771 TO WICHITA7 345.0 KV 532796 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WICHITA7_532796 | a. Apply single-phase fault on: a.1. WICHITA7 345.0 KV 532796 TO BENTON 7 345.0 KV 532791 CKT 1, b. with stuck breaker near WICHITA7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. RENO 7 345.0 KV 532771 TO WICHITA7 345.0 KV 532796 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WICHITA7_533040 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7( 532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 532796 TO EVANS N4 533040 TO WICH12 1 532830 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WICHITA7_533040 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7( 532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 532796 TO EVANS N4 533040 TO WICH12 1 532830 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WICHITA7_EXPEDITION7_6 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 345.0 KV 532796 TO EXPEDITION7 345.0 KV 532803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WICHITA7_EXPEDITION7_6 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 345.0 KV 532796 TO EXPEDITION7 345.0 KV 532803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WICHITA7_G14-001-TAP | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 345.0 KV 532796 TO G14-001-TAP 345.0 KV 562476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WICHITA7_G14-001-TAP | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 345.0 KV 532796 TO G14-001-TAP 345.0 KV 562476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WICHITA7_VIOLA_7_6 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 345.0 KV 532796 TO VIOLA 7 345.0 KV 532798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WICHITA7_VIOLA_7_6 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 345.0 KV 532796 TO VIOLA 7 345.0 KV 532798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WLNUTCK4_PAOLI_4 | 3 Phase fault on WLNUTCK4 (515097) 138 kV Bus a. Apply fault at the WLNUTCK4 (515097) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WLNUTCK4 138.0 KV 515097 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WLNUTCK4_PAOLI_4 | 3 Phase fault on WLNUTCK4 (515097) 138 kV Bus a. Apply fault at the WLNUTCK4 (515097) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WLNUTCK4 138.0 KV 515097 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG4_514715 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG4_514715 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG4_MARSHL_4 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG4_MARSHL_4 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG7_514715 | a. Apply single-phase fault on: a.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1, b. with stuck breaker near WOODRNG7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. REDNGTN7 345.0 KV 515875 TO WOODRNG7 345.0 KV 514715 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG7_514715 | a. Apply single-phase fault on: a.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1, b. with stuck breaker near WOODRNG7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. REDNGTN7 345.0 KV 515875 TO WOODRNG7 345.0 KV 514715 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG7_GEN_2017_164 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG7_GEN_2017_164 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG7_HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG7_HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG7_PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG7_PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG7_REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG7_REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WOODRNG7_SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WOODRNG7_SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WRVALLY4_WARREN_4 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WRVALLY4_WARREN_4 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WWDBORDT_755000 | a. Apply single-phase fault on: a.1. BORDER7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1, b. with stuck breaker near WWBORDT 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. WWDBORDT 345.0 KV 755000 TO CHISHOLM7 345.0 KV 511553 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WWDBORDT_755000 | a. Apply single-phase fault on: a.1. BORDER7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1, b. with stuck breaker near WWBORDT 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. WWDBORDT 345.0 KV 755000 TO CHISHOLM7 345.0 KV 511553 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV7_TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV7_TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | XEROX_4_CZECHAL4 | 3 Phase fault on XEROX 4 (514893) 138 kV Bus a. Apply fault at the XEROX 4 (514893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XEROX 4 138.0 KV 514893 TO CZECHAL4 138.0 KV 514894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | XEROX_4_CZECHAL4 | 3 Phase fault on XEROX 4 (514893) 138 kV Bus a. Apply fault at the XEROX 4 (514893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XEROX 4 138.0 KV 514893 TO CZECHAL4 138.0 KV 514894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | 112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | 112GORE4__RPPAPER4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | 34TH_ST_TP_3__COULTER____3 | 3 Phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 34TH_ST_TP 3 115.0 KV 524281 TO COULTER 3 115.0 KV 524306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ADAIR______2__SULPHUR____2 | 3 Phase fault on ADAIR 2 (527253) 69 kV Bus a. Apply fault at the ADAIR 2 (527253) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR 2 69.0 KV 527253 TO SULPHUR 2 69.0 KV 527261 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMOCO_SS___6__YOAKUM_____6 | 3 Phase fault on AMOCO_SS 6 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMOCO_TP___3__LG_LEVELAND3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMOCOWASSON6__MUSTANG____6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMOCOWASSON6__XTO_MAHONEY6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA7__SEMINOL7 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BENNETT____3__ARCO_TP____3 | 3 Phase fault on BENNETT 3 (527018) 115 kV Bus a. Apply fault at the BENNETT 3 (527018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BENNETT____3__ODC_TP_____3 | 3 Phase fault on BENNETT 3 (527018) 115 kV Bus a. Apply fault at the BENNETT 3 (527018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BORDER_____7__WWDBORDT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BROWNFIELD_2__BROWNFLD_TP2 | 3 Phase fault on BROWNFIELD 2 (526754) 69 kV Bus a. Apply fault at the BROWNFIELD 2 (526754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNFIELD 2 69.0 KV 526754 TO BROWNFLD_TP2 69.0 KV 526761 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BUSHLAND___3__COULTER____3 | 3 Phase fault on BUSHLAND 3 (524266) 115 kV Bus a. Apply fault at the BUSHLAND 3 (524266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUTPOST 3 115.0 KV 524243 TO BUSHLAND 3 115.0 KV 524266 CKT 1 b.2. OUTPOST 3 115.0 KV 524243 TO ARNOT 3 115.0 KV 524560 CKT 1 b.3. LOAD 1 524560 b.4. HILLSIDE 3 115.0 KV 524300 TO ARNOT 3 115.0 KV 524560 CKT 1 b.5. LOAD 1 524560 b.6. HILLSIDE 3 115.0 KV 524300 TO COULTER 3 115.0 KV 524306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BUSHLAND___6__DEAFSMITH__6 | 3 Phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 230.0 KV 524267 TO DEAFSMITH 6 230.0 KV 524623 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BUSHLAND___6__WILDOR2_JUS6 | 3 Phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 230.0 KV 524267 TO WILDOR2_JUS6 230.0 KV 524290 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | C_RIVER7__FIREWHL_TAP | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CANYON_E_TP3__CANYON_EAST3 | 3 Phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANYON_E_TP3 115.0 KV 524522 TO CANYON_EAST3 115.0 KV 524523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CARGILL____3__PARMER_CO__3 | 3 Phase fault on CARGILL 3 (524648) 115 kV Bus a. Apply fault at the CARGILL 3 (524648) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARGILL 3 115.0 KV 524648 TO DS-#24 +3 115.0 KV 524664 CKT 1 b.2. LOAD 1 524664 b.3. PARMER_CO 3 115.0 KV 524662 TO DS-#24 +3 115.0 KV 524664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CENTRE_ST__2__NE_HEREFORD2 | 3 Phase fault on CENTRE_ST 2 (524554) 69 kV Bus a. Apply fault at the CENTRE_ST 2 (524554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRE_ST 2 69.0 KV 524554 TO NE_HEREFORD2 69.0 KV 524573 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHISHOLM7__WWDBORDT | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CIMARON7__FSHRTAP7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CIMARON7__MATHWSN7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CIMARON7__NSUB345 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COULTER____3__ESTACADO_TP3 | 3 Phase fault on COULTER 3 (524306) 115 kV Bus a. Apply fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTER 3 115.0 KV 524306 TO ESTACADO_TP3 115.0 KV 524425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CURRY______3__FE_CLOVIS2_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DC_EAST____2__DENVER_CTY_2 | 3 Phase fault on DC_EAST 2 (527099) 69 kV Bus a. Apply fault at the DC_EAST 2 (527099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DC_EAST 2 69.0 KV 527099 TO DENVER_CTY 2 69.0 KV 527125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_CTY_2__JAYBEE_____2 | 3 Phase fault on DENVER_CTY 2 (527125) 69 kV Bus a. Apply fault at the DENVER_CTY 2 (527125) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_CTY 2 69.0 KV 527125 TO JAYBEE 2 69.0 KV 527183 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_CTY_2__MIDAMERI_TP2 | 3 Phase fault on DENVER_CTY 2 (527125) 69 kV Bus a. Apply fault at the DENVER_CTY 2 (527125) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_CTY 2 69.0 KV 527125 TO MIDAMERI_TP2 69.0 KV 527313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_N___3__HIGG_______3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 b.2. LOAD 1 527286 b.3. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_N___3__HIGGEAST___3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_N___3__SHELL_CO2__3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 b.2. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_S___3__SHELLC3_TP_3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 b.2. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DIAMONDBACK2__CEDARLAKE__2 | 3 Phase fault on DIAMONDBACK2 (527211) 69 kV Bus a. Apply fault at the DIAMONDBACK2 (527211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK2 69.0 KV 527211 TO OXY_CEDRLKE2 69.0 KV 527250 CKT 1 b.2. LOAD 1 527250 b.3. CEDARLAKE 2 69.0 KV 527247 TO OXY_CEDRLKE2 69.0 KV 527250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DIAMONDBACK2__LG_ASHMORE_2 | 3 Phase fault on DIAMONDBACK2 (527211) 69 kV Bus a. Apply fault at the DIAMONDBACK2 (527211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK2 69.0 KV 527211 TO LG-ASHMORE 2 69.0 KV 527235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DIAMONDBACK2__LG_SAWYERFL2 | 3 Phase fault on DIAMONDBACK2 (527211) 69 kV Bus a. Apply fault at the DIAMONDBACK2 (527211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK2 69.0 KV 527211 TO OZRK_MAH02 2 69.0 KV 527229 CKT 1 b.2. LOAD 1 527229 b.3. OZRK_MAH02 2 69.0 KV 527229 TO LG-SAWYERFL2 69.0 KV 527305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_7__NSUB345 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_7__SEMINOL7 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS__5&_11__2__CENTRE_ST__2 | 3 Phase fault on DS-#5&#11 2 (524536) 69 kV Bus a. Apply fault at the DS-#5&#11 2 (524536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#5&#11 2 69.0 KV 524536 TO CENTRE_ST 2 69.0 KV 524554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS__9______2__HERFRD_STH_2 | 3 Phase fault on DS-#9 +2 (524580) 69 kV Bus a. Apply fault at the DS-#9 +2 (524580) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#9 +2 69.0 KV 524580 TO HERFRD_STH 2 69.0 KV 524608 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DS_MTR_____2__NE_HEREFORD2 | 3 Phase fault on DS-MTR 2 (524561) 69 kV Bus a. Apply fault at the DS-MTR 2 (524561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-MTR 2 69.0 KV 524561 TO NE_HEREFORD2 69.0 KV 524573 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | E_CLOVIS___3__CURRY______3 | 3 Phase fault on E_CLOVIS 3 (524773) 115 kV Bus a. Apply fault at the E_CLOVIS 3 (524773) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | E_LEVELLAND2__SLAUGTER_TP2 | 3 Phase fault on E_LEVELLAND2 (526056) 69 kV Bus a. Apply fault at the E_LEVELLAND2 (526056) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_LEVELLAND2 69.0 KV 526056 TO SLAUGTER_TP2 69.0 KV 526416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ELKCITY6__CHISHOLM6 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EMULESH&VLY2__BAILEYCO___2 | 3 Phase fault on EMULESH&VLY2 (525017) 69 kV Bus a. Apply fault at the EMULESH&VLY2 (525017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMULESH&VLY2 69.0 KV 525017 TO BAILEYCO 2 69.0 KV 525027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FE_CHZPLT__3__OASIS______3 | 3 Phase fault on FE-CHZPLT 3 (524863) 115 kV Bus a. Apply fault at the FE-CHZPLT 3 (524863) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FT_SILL2__PO_HILL2 | 3 Phase fault on FT.SILL2 (511461) 69 kV Bus a. Apply fault at the FT.SILL2 (511461) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | GEORGIA____3__RANDALL____3 | 3 Phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEORGIA 3 115.0 KV 524322 TO RANDALL 3 115.0 KV 524364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HARRNG_WST_6__ROLLHILLS__6 | 3 Phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 230.0 KV 523977 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HEREFORD___3__CARGILL____3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO DS-#6 3 115.0 KV 524629 CKT 1 b.2. LOAD 1 524629 b.3. DS-#6 3 115.0 KV 524629 TO FRIONA 3 115.0 KV 524655 CKT 1 b.4. LOAD 1 524655 b.5. LOAD D1 524655 b.6. CARGILL 3 115.0 KV 524648 TO FRIONA 3 115.0 KV 524655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HERFRD_STH_2__DS__4______2 | 3 Phase fault on HERFRD_STH 2 (524608) 69 kV Bus a. Apply fault at the HERFRD_STH 2 (524608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERFRD_STH 2 69.0 KV 524608 TO DS-#4 +2 69.0 KV 524633 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HIGG_______3__BENSING____3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4__CANEYCK4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4__RUSSET_4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4__SXMLCKT4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KINNEY_____2__TOKIO_TP___2 | 3 Phase fault on KINNEY 2 (526965) 69 kV Bus a. Apply fault at the KINNEY 2 (526965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINNEY 2 69.0 KV 526965 TO TOKIO_TP 2 69.0 KV 526971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMB_CNTY__2__LC_LTTLFLD_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMB_CNTY__2__LC_LUMSCHAP2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LUMSCHAP2 69.0 KV 525687 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAPLATA____3__NE_HEREFORD3 | 3 Phase fault on LAPLATA 3 (524556) 115 kV Bus a. Apply fault at the LAPLATA 3 (524556) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAPLATA 3 115.0 KV 524556 TO NE_HEREFORD3 115.0 KV 524567 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LC_OPDYKE__3__SUNDOWN____3 | 3 Phase fault on LC-OPDYKE 3 (526036) 115 kV Bus a. Apply fault at the LC-OPDYKE 3 (526036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LG_ASHMORE_2__ADAIR______2 | 3 Phase fault on LG-ASHMORE 2 (527235) 69 kV Bus a. Apply fault at the LG-ASHMORE 2 (527235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-ASHMORE 2 69.0 KV 527235 TO ADAIR 2 69.0 KV 527253 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LG_DIXON___2__BROWNFIELD_2 | 3 Phase fault on LG-DIXON 2 (526711) 69 kV Bus a. Apply fault at the LG-DIXON 2 (526711) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DIXON 2 69.0 KV 526711 TO BROWNFIELD 2 69.0 KV 526754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LG_JS_SMITH2__WELLMAN____2 | 3 Phase fault on LG-JS_SMITH2 (526979) 69 kV Bus a. Apply fault at the LG-JS_SMITH2 (526979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-JS_SMITH2 69.0 KV 526979 TO WELLMAN 2 69.0 KV 526985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LG_MC&SMNL_2__LG_SAWYERFL2 | 3 Phase fault on LG-MC&SMNL+2 (527223) 69 kV Bus a. Apply fault at the LG-MC&SMNL+2 (527223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-MC&SMNL+2 69.0 KV 527223 TO LG-SAWYERFL2 69.0 KV 527305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LG_PLSHILL_3__SEAGRAVES__3 | 3 Phase fault on LG-PLSHILL 3 (527194) 115 kV Bus a. Apply fault at the LG-PLSHILL 3 (527194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LYDIA__7__VALIANT7 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MANHATTAN__3__RANDALL____3 | 3 Phase fault on MANHATTAN 3 (524224) 115 kV Bus a. Apply fault at the MANHATTAN 3 (524224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANHATTAN 3 115.0 KV 524224 TO RANDALL 3 115.0 KV 524364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MNCWND37__MNCWND47 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MOORE_CNTY_6__MCDWL_CREEK6 | 3 Phase fault on MOORE_CNTY 6 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 230.0 KV 523309 TO MCDWL_CREEK6 230.0 KV 523323 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MULESH_CTY_2__BAILEYCO___2 | 3 Phase fault on MULESH_CTY 2 (525008) 69 kV Bus a. Apply fault at the MULESH_CTY 2 (525008) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESH_CTY 2 69.0 KV 525008 TO BAILEYCO 2 69.0 KV 525027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NE_HEREFORD3__HEREFORD___3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO HEREFORD 3 115.0 KV 524606 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NEWHART____3__LAMTON_____3 | 3 Phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 b.2. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NORTH_LOVNG3__SOUTH_LOVNG3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NORTWST7__CIMARON7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NWTXARK7__VALIANT7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-033 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2017-033 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PACIFIC____3__SUNDOWN____3 | 3 Phase fault on PACIFIC 3 (526424) 115 kV Bus a. Apply fault at the PACIFIC 3 (526424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PARMER_CO__3__DS__20_____3 | 3 Phase fault on PARMER_CO 3 (524662) 115 kV Bus a. Apply fault at the PARMER_CO 3 (524662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARMER_CO 3 115.0 KV 524662 TO DS-#20 3 115.0 KV 524669 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PERIMETER__3__OASIS______3 | 3 Phase fault on PERIMETER 3 (524797) 115 kV Bus a. Apply fault at the PERIMETER 3 (524797) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PHANTOM____3__BOPCO_PKRLK3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PITTSB_7__C_RIVER7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PITTSB_7__KIOWA__7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PITTSB_7__SEMINOL7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PITTSB_7__VALIANT7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLAINS_INT_3__LG_PLAINS__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLAINVW_TP_2__LH_HALECTR_2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO LH-HALECTR 2 69.0 KV 525745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNT_HILL_3__E_CLOVIS___3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNT_HILL_3__FE_HOLLAND_3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PORTALES___3__GREYHOUND__3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO KILGORE 3 115.0 KV 524935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PRENTICE___3__YOAKUM_____3 | 3 Phase fault on PRENTICE 3 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PRINGLE____6__HARRNG_EST_6 | 3 Phase fault on PRINGLE 6 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 230.0 KV 523267 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PUCKETT____3__COULTER____3 | 3 Phase fault on PUCKETT 3 (524256) 115 kV Bus a. Apply fault at the PUCKETT 3 (524256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKETT 3 115.0 KV 524256 TO COULTER 3 115.0 KV 524306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RANDALL____3__CANYON_E_TP3 | 3 Phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 3 115.0 KV 524364 TO CANYON_E_TP3 115.0 KV 524522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RANDALL____3__PALO_DURO__3 | 3 Phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 3 115.0 KV 524364 TO PALO_DURO 3 115.0 KV 524530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER___3__AGAVE_RHILL3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SAGA_SDCOL_7__SAGA_SCOL__7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SAN_ANDS_TP3__SAN_ANDRES_3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SAN_ANDRES 3 115.0 KV 527106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEAGRAVES__2__TOKIO_TP___2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 b.2. LOAD 1 527217 b.3. TOKIO_TP 2 69.0 KV 526971 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEAGRAVES__2__WELLMAN____2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 b.2. WELLMAN 2 69.0 KV 526985 TO LG-WELLMAN 2 69.0 KV 526993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEAGRAVES__3__YOAKUM_____3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 b.2. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL7__MUSKOGE7 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SLAUGHTER__2__SLAUGTER_TP2 | 3 Phase fault on SLAUGHTER 2 (526409) 69 kV Bus a. Apply fault at the SLAUGHTER 2 (526409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLAUGHTER 2 69.0 KV 526409 TO SLAUGTER_TP2 69.0 KV 526416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SOUTHEAST__3__RANDALL____3 | 3 Phase fault on SOUTHEAST 3 (524338) 115 kV Bus a. Apply fault at the SOUTHEAST 3 (524338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHEAST 3 115.0 KV 524338 TO RANDALL 3 115.0 KV 524364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SP_BECTON__2__ALLMON_____2 | 3 Phase fault on SP-BECTON +2 (525860) 69 kV Bus a. Apply fault at the SP-BECTON +2 (525860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-BECTON +2 69.0 KV 525860 TO ALLMON 2 69.0 KV 525867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SP_ERSKINE_3__CARLISLE___3 | 3 Phase fault on SP-ERSKINE 3 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | STANTON_N__2__STANTON_E__2 | 3 Phase fault on STANTON_N 2 (526073) 69 kV Bus a. Apply fault at the STANTON_N 2 (526073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_N 2 69.0 KV 526073 TO STANTON_E 2 69.0 KV 526075 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | STANTON_N__2__SW_6786_N__2 | 3 Phase fault on STANTON_N 2 (526073) 69 kV Bus a. Apply fault at the STANTON_N 2 (526073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_N 2 69.0 KV 526073 TO SW_6786_N 2 69.0 KV 526086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SULPHUR____2__UNION_TX___2 | 3 Phase fault on SULPHUR 2 (527261) 69 kV Bus a. Apply fault at the SULPHUR 2 (527261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULPHUR 2 69.0 KV 527261 TO LG-FOSTER +2 69.0 KV 527271 CKT 1 b.2. LOAD 1 527271 b.3. UNION_TX 2 69.0 KV 526999 TO LG-FOSTER +2 69.0 KV 527271 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNDOWN____6__YOAKUM_____6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 b.2. LOAD 1 526460 b.3. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4__GEN_2017_167 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO GEN-2017-167 138.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4__LONEGRV4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4__UNIROY_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SWEETWT6__CHISHOLM6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRY_CNTY_2__BROWNFIELD_2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 b.2. LOAD 1 526747 b.3. LG-BROWNFLD2 69.0 KV 526747 TO BROWNFIELD 2 69.0 KV 526754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRY_CNTY_2__SLAUGTER_TP2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 b.2. LG-MEADOW 2 69.0 KV 526499 TO LG-DOCWEBR 2 69.0 KV 526506 CKT 1 b.3. LOAD 1 526506 b.4. SLAUGTER_TP2 69.0 KV 526416 TO LG-MEADOW 2 69.0 KV 526499 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRY_CNTY_3__YOAKUM_____3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 b.2. LOAD 1 526792 b.3. LOAD D1 526792 b.4. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TIERABLANCA3__CANYON_E_TP3 | 3 Phase fault on TIERABLANCA3 (524630) 115 kV Bus a. Apply fault at the TIERABLANCA3 (524630) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 b.2. DS-#25+ 3 115.0 KV 524575 TO PANDAHFD 3 115.0 KV 524597 CKT 1 b.3. LOAD 1 524597 b.4. DAWN 3 115.0 KV 524590 TO PANDAHFD 3 115.0 KV 524597 CKT 1 b.5. LOAD 1 524597 b.6. CANYON_WEST3 115.0 KV 524516 TO DAWN 3 115.0 KV 524590 CKT 1 b.7. LOAD 1 524590 b.8. CANYON_WEST3 115.0 KV 524516 TO HUNSLEY 3 115.0 KV 524520 CKT 1 b.9. LOAD 1 524520 b.10. HUNSLEY 3 115.0 KV 524520 TO CANYON_E_TP3 115.0 KV 524522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TIERABLANCA3__CASTRO_CNTY3 | 3 Phase fault on TIERABLANCA3 (524630) 115 kV Bus a. Apply fault at the TIERABLANCA3 (524630) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 b.2. LOAD 1 524734 b.3. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOKIO_TP___2__LG_SEAGRAVE2 | 3 Phase fault on TOKIO_TP 2 (526971) 69 kV Bus a. Apply fault at the TOKIO_TP 2 (526971) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOKIO_TP 2 69.0 KV 526971 TO LG-SEAGRAVE2 69.0 KV 527189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___2__LH_HALECTR_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 b.2. LOAD 1 525826 b.3. HALECENTER 2 69.0 KV 525738 TO LH-HALECTR 2 69.0 KV 525745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___2__SP_BECTON__2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 b.2. LOAD 1 525853 b.3. LOAD 2 525853 b.4. LH-WIL&ELN+2 69.0 KV 525853 TO SP-BECTON +2 69.0 KV 525860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___2__STANTON_N__2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 b.2. LOAD 1 525885 b.3. SP-NEWDEAL 2 69.0 KV 525885 TO MONROE 2 69.0 KV 525892 CKT 1 b.4. LOAD 1 525892 b.5. WHITEHEAD 2 69.0 KV 525891 TO MONROE 2 69.0 KV 525892 CKT 1 b.6. LOAD 1 525892 b.7. WHITEHEAD 2 69.0 KV 525891 TO SP-SHALLWTR2 69.0 KV 525899 CKT 1 b.8. LOAD 1 525899 b.9. SP-SHALLWTR2 69.0 KV 525899 TO STANTON_N 2 69.0 KV 526073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | W_LITTLFLD_2__LAMB_CNTY__2 | 3 Phase fault on W_LITTLFLD 2 (525613) 69 kV Bus a. Apply fault at the W_LITTLFLD 2 (525613) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WASSON_____2__DENVER_CTY_2 | 3 Phase fault on WASSON 2 (527111) 69 kV Bus a. Apply fault at the WASSON 2 (527111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASSON 2 69.0 KV 527111 TO DENVER_CTY 2 69.0 KV 527125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WELLMAN____2__UNION_TX___2 | 3 Phase fault on WELLMAN 2 (526985) 69 kV Bus a. Apply fault at the WELLMAN 2 (526985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLMAN 2 69.0 KV 526985 TO UNION_TX 2 69.0 KV 526999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WILDOR_WND_6__WILDOR2_JUS6 | 3 Phase fault on WILDOR_WND 6 (524276) 230 kV Bus a. Apply fault at the WILDOR_WND 6 (524276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILDOR_WND 6 230.0 KV 524276 TO WILDOR2_JUS6 230.0 KV 524290 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV7__WWDBORDT | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | XIT_INTG___6__CHAN_TASCOS6 | 3 Phase fault on XIT_INTG 6 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 230.0 KV 523221 TO CHAN+TASCOS6 230.0 KV 523869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | XTO_CORNEL_3__SHELLC3_TP_3 | 3 Phase fault on XTO_CORNEL+3 (527033) 115 kV Bus a. Apply fault at the XTO_CORNEL+3 (527033) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_____3__LG_PLSHILL_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YUMA_INT___3__WOLFFORTH__3 | 3 Phase fault on YUMA_INT 3 (526475) 115 kV Bus a. Apply fault at the YUMA_INT 3 (526475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BAILEYCO___3__525027_0 | 3 Phase fault on BAILEYCO 3 (525028) 115 kV Bus a. Apply fault at the BAILEYCO 3( 525028) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEYCO 3 525028 TO BAILEYCO 2 525027 TO BAILY_TR2 1 525026 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BUSHLAND___6__524266_0 | 3 Phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6( 524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 524267 TO BUSHLAND 3 524266 TO BSHLND_TR1 1 524263 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | C_RIVER7__510946_0 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CASTRO_CNTY3__524745_0 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3( 524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 524746 TO CASTRO_CNTY2 524745 TO CASTRO_TR1 1 524744 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CIMARON4__514901_0 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COULTER____3__524305_0 | 3 Phase fault on COULTER 3 (524306) 115 kV Bus a. Apply fault at the COULTER 3( 524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTER 3 524306 TO COULTER 2 524305 TO COLTER_TR1 1 524304 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | COX________3__525325_0 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3( 525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 525326 TO COX 2 525325 TO COX_TR1 1 525324 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DEAFSMITH__6__524619_0 | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6( 524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 524623 TO DFSMTH_EST 3 524619 TO DEFSMTH_TR21 524621 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DEAFSMITH__6__524622_0 | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6( 524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 524623 TO DFSMTH_WST 3 524622 TO DEFSMTH_TR11 524620 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DIAMONDBACK3__527211_0 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3( 527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 527212 TO DIAMONDBACK2 527211 TO DIMNDBK_TR11 527210 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HEREFORD___3__524604_0 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3( 524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 524606 TO HEREFRD_SB 2 524604 TO HERFRD_TR2 1 524603 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HEREFORD___3__524605_0 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3( 524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 524606 TO HEREFRD_NB 2 524605 TO HERFRD_TR1 1 524602 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7( 523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KRESS_INT__3__525191_0 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3( 525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 525192 TO KRESS_INT 2 525191 TO KRESS_TR1 1 525190 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMB_CNTY__3__525635_0 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3( 525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 525636 TO LAMB_CNTY 2 525635 TO LAMB_TR2 1 525632 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMTON_____3__525413_0 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3( 525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 525414 TO LAMTON 2 525413 TO LAMTON_TR1 1 525412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MCDWL_CREEK6__523322_0 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6( 523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 523323 TO MCDWL_CREEK3 523322 TO MCDWL_CRKTR1 523321 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NE_HEREFORD3__524573_0 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3( 524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 524567 TO NE_HEREFORD2 524573 TO NE_HRFD_TR11 524565 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OKLAUN_7__590003_0 | 3 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLVALLY4__555234_0 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RANDALL____6__524364_0 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6( 524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 524365 TO RANDALL 3 524364 TO RANDAL_TR1 1 524361 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ROLLHILLS__6__524007_0 | 3 Phase fault on ROLLHILLS 6 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6( 524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 524010 TO ROLLHILLS 3 524007 TO ROLHILLS_TR1 524008 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RSHSPR1_COL1__511979_0 | 3 Phase fault on RSHSPR1 (511978) 345 kV Bus a. Apply fault at the RSHSPR1( 511978) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL4__515045_0 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SULPHUR____3__527261_0 | 3 Phase fault on SULPHUR 3 (527262) 115 kV Bus a. Apply fault at the SULPHUR 3( 527262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULPHUR 3 527262 TO SULPHUR 2 527261 TO SLPHUR_TR2 1 527260 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | VALIANT4__510911_0 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BORDER7_345kV_515458 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, b. with stuck breaker near BORDER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BRU_SUB6_230kV_527009 | a. Apply single-phase fault on: a.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, b. with stuck breaker near BRU_SUB 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-239 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2017-239 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | BUSHLAND6_230kV_524267 | a. Apply single-phase fault on: a.1. POTTERCO6 230.0 KV 523959 TO BUSHLAND6 230.0 KV 524267 CKT 1, b. with stuck breaker near BUSHLAND 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CHINA_DRAW7_345kV_528223 | a. Apply single-phase fault on: a.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, b. with stuck breaker near CHINA_DRAW 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CROSSROADS7_345kV_527656 | a. Apply single-phase fault on: a.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1, b. with stuck breaker near CROSSROADS 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. HOBBS_INT 7 345.0 KV 527896 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CUNNINHAM3_115kV_527864 | a. Apply single-phase fault on: a.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, b. with stuck breaker near CUNNINHAM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CUNNINHAM6_230kV_527867 | a. Apply single-phase fault on: a.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, b. with stuck breaker near CUNNIGHM_S 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | CUNNINHAMN6_230kV_527865 | a. Apply single-phase fault on: a.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, b. with stuck breaker near CUNNIGHM_N 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | DEAFSMITH6_230kV_524623 | a. Apply single-phase fault on: a.1. DEAFSMITH6 230.0 KV 524623 TO G17146TAP 230.0 KV 760498 CKT 1, b. with stuck breaker near DEAFSMITH 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | EDDY_CNTY7_345kV_527802 | a. Apply single-phase fault on: a.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, b. with stuck breaker near EDDY_CNTY 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | FLATLAND3_115kV_527257 | a. Apply single-phase fault on: a.1. FLATLAND 3 115.0 KV 527257 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1, b. with stuck breaker near FLATLAND 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. FLATLAND 3 115.0 KV 527257 TO DIAMONDBACK3 115.0 KV 527212 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT3_115kV_527891 | a. Apply single-phase fault on: a.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, b. with stuck breaker near HOBBS_INT 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. HOBBS_INT 3 115.0 KV 527891 TO CUNNINHAM 3 115.0 KV 527864 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT6_230kV_527894 | a. Apply single-phase fault on: a.1. ANDREWS 6 230.0 KV 528604 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, b. with stuck breaker near HOBBS_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOBBS_INT7_345kV_527896 | a. Apply single-phase fault on: a.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, b. with stuck breaker near HOBBS_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. RDRUNNER 7 345.0 KV 528027 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | HOCKLEY3_115kV_526020 | a. Apply single-phase fault on: a.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 a.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, b. with stuck breaker near HOCKLEY 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | INK_BASIN3_115kV_527027 | a. Apply single-phase fault on: a.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, b. with stuck breaker near INK_BASIN 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | INK_BASIN6_230kV_527028 | a. Apply single-phase fault on: a.1. INK_BASIN 6 230.0 KV 527028 TO YOAKUM 6 230.0 KV 526935 CKT 1, b. with stuck breaker near INK_BASIN 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | JONES6_230kV_526337 | a. Apply single-phase fault on: a.1. TUCOINT6 230.0 KV 525830 TO JONES6 230.0 KV 526337 CKT 1, b. with stuck breaker near JONES 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. LUBBCKSTH6 230.0 KV 526269 TO JONES6 230.0 KV 526337 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | KIOWA7_345kV_527965 | a. Apply single-phase fault on: a.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, b. with stuck breaker near KIOWA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMB_CNTY_69kV_525635 | a. Apply single-phase fault on: a.1. LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 a.2. LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, b. with stuck breaker near LAMB_CNTY 2 69 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 c.3. LOAD 1 525613 c.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 c.5. LOAD 1 525606 c.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LAMB_CNTY3_115kV_525636 | a. Apply single-phase fault on: a.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, b. with stuck breaker near LAMB_CNTY 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LES4_138kV_511467 | a. Apply single-phase fault on: a.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 a.2. LOAD 1 511474 a.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, b. with stuck breaker near L.E.S.-4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-4 138.0 KV 511467 TO LWSTAP 4 138.0 KV 511439 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LES7_345kV_511468 | a. Apply single-phase fault on: a.1. L.E.S.-7 345.0 KV 511468 TO O.K.U.-7 345.0 KV 511456 CKT 1, b. with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | LUBBUCK_EST_115kV_526298 | a. Apply single-phase fault on: a.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, b. with stuck breaker near LUBBCK_EST 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | Maddox_115kV_528355 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO Hobbs Int 115KV 527891 CKT 1, b. with stuck breaker near MADDOX 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. Maddox 115KV 528355 TO SANGER_SW 3 115KV 528463 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | MUSTANG6_230kV_527149 | a. Apply single-phase fault on: a.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, b. with stuck breaker near MUSTANG 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | N_LOVING7_345kV_528185 | a. Apply single-phase fault on: a.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, b. with stuck breaker near N_LOVING 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NA_ENRICH3_115kV_528603 | a. Apply single-phase fault on: a.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, b. with stuck breaker near NA_ENRICH 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 c.2. LOAD 1 528605 c.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NEWHART3_115kV_525460 | a. Apply single-phase fault on: a.1. KRESSINT3 115.0 KV 525192 TO NEWHART3 115.0 KV 525460 CKT 1, b. with stuck breaker near NEWHART 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. HARTINDUST3 115.0 KV 525124 TO NEWHART3 115.0 KV 525460 CKT 1 c.2. HARTINDUST3 115.0 KV 525124 TO LAMTON3 115.0 KV 525414 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | NEWHART6_230kV_525461 | a. Apply single-phase fault on: a.1. NEWHART6 230.0 KV 525461 TO PLANTX6 230.0 KV 525481 CKT 1, b. with stuck breaker near NEWHART 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. POTTERCO6 230.0 KV 523959 TO NEWHART6 230.0 KV 525461 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OASIS3_115kV_524874 | a. Apply single-phase fault on: a.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, b. with stuck breaker near OASIS 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 c.2. LOAD 1 524863 c.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OASIS6_230kV_524875 | a. Apply single-phase fault on: a.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, b. with stuck breaker near OASIS 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SN_JUAN_TAP6 230.0 KV 524885 TO OASIS 6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | OKU7_345kV_511456 | a. Apply single-phase fault on: a.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1, b. with stuck breaker near O.K.U.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-033 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2017-033 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PHANTOM7_345kV_528015 | a. Apply single-phase fault on: a.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, b. with stuck breaker near PHANTOM 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANT_X3_115kV_525480 | a. Apply single-phase fault on: a.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1, b. with stuck breaker near PLANT_X 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLANTX_230kV_525481 | a. Apply single-phase fault on: a.1. PLANTX6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 1, b. with stuck breaker near PLANT_X 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLANTX6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNTHILL3_115kV_524768 | a. Apply single-phase fault on: a.1. PLSNTHILL3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1, b. with stuck breaker near PLSNT_HILL 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLSNTHILL3 115.0 KV 524768 TO NORTON 3 115.0 KV 524502 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | PLSNTHILL6_230kV_524770 | a. Apply single-phase fault on: a.1. PLSNTHILL6 230.0 KV 524770 TO ROOSEVELT6 230.0 KV 524909 CKT 1, b. with stuck breaker near PLSNT_HILL 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLSNTHILL6 230.0 KV 524770 TO OASIS6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTER_CO7_345kV_523961 | a. Apply single-phase fault on: a.1. POTTER_CO 7 345.0 KV 523961 TO HITCHLAND 7 345.0 KV 523097 CKT 1, b. with stuck breaker near POTTER_CO 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. SPNSPUR_WND7 345.0 KV 524296 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | POTTERCO6_230kV_523959 | a. Apply single-phase fault on: a.1. POTTERCO6 230.0 KV 523959 TO HARRNG_EST6 230.0 KV 523979 CKT 1, b. with stuck breaker near POTTER_CO 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. POTTERCO6 230.0 KV 523959 TO MCDWL_CREEK6 230.0 KV 523323 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER3_115kV_528025 | a. Apply single-phase fault on: a.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, b. with stuck breaker near RDRUNNER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNER7_345kV_528027 | a. Apply single-phase fault on: a.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, b. with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | RED_BLUFF_115kV_528018 | a. Apply single-phase fault on: a.1. REDBLUFF 115KV 528018 TO WOLFCAMPTP 115KV 528235 CKT 1, b. with stuck breaker near RED_BLUFF 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. REDBLUFF 115KV 528018 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | ROOSEVELT6_230kV_524909 | a. Apply single-phase fault on: a.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, b. with stuck breaker near ROOSEVELT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TOLK 6 230.0 KV 525531 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SEAGRAVES3_115kV_527202 | a. Apply single-phase fault on: a.1. SEAGRAVES3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1, b. with stuck breaker near SEAGRAVES 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSTANG3 115.0 KV 527146 TO SEAGRAVES3 115.0 KV 527202 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SULPHUR2_69kV_527261 | a. Apply single-phase fault on: a.1. ADAIR2 69.0 KV 527253 TO SULPHUR2 69.0 KV 527261 CKT 1, b. with stuck breaker near SULPHUR 2 69 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SULPHUR2 69.0 KV 527261 TO LGFOSTER2 69.0 KV 527271 CKT 1 c.2. UNIONTX2 69.0 KV 526999 TO LGFOSTER2 69.0 KV 527271 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SULPHUR3_115kV_527262 | a. Apply single-phase fault on: a.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR3 115.0 KV 527262 CKT 1, b. with stuck breaker near SULPHUR 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR3 115.0 KV 527262 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNDOWN6_230kV_526435 | a. Apply single-phase fault on: a.1. SUNDOWN 6 230.0 KV 526435 TO PLANT_X 6 230.0 KV 525481 CKT 1, b. with stuck breaker near SUNDOWN 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD7_345kV_515136 | a. Apply single-phase fault on: a.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1, b. with stuck breaker near SUNNYSD7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. G16-063-TAP 3 345.0 KV 560088 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | SWISHER6_230kV_525213 | a. Apply single-phase fault on: a.1. AMASOUTH6 230.0 KV 524415 TO SWISHER6 230.0 KV 525213 CKT 1, b. with stuck breaker near SWISHER 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SWISHER6 230.0 KV 525213 TO TUCO_INT6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRYCNTY3_115kV_526736 | a. Apply single-phase fault on: a.1. TERTRYCNTY3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1, b. with stuck breaker near TERRY_CNTY 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TERTRYCNTY3 115.0 KV 526736 TO DENVERN3 115.0 KV 527130 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7_345kV_511568 | a. Apply single-phase fault on: a.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, b. with stuck breaker near TERRYRD7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 3 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TIERABLANCA3_115kV_524630 | a. Apply single-phase fault on: a.1. DFSMTHEST3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1, b. with stuck breaker near TIERABLANCA3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TOLK6_230kV_525531 | a. Apply single-phase fault on: a.1. TOLK 6 230.0 KV 525531 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, b. with stuck breaker near TOLK 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT6_230kV_525830 | a. Apply single-phase fault on: a.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, b. with stuck breaker near TUCO_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT7_345kV_525832 | a. Apply single-phase fault on: a.1. TUCO_INT 7 345.0 KV 525832 TO BORDER 7 345.0 KV 515458 CKT 1, b. with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM_345kV_526936 | a. Apply single-phase fault on: a.1. YOAKUM_345 345.0 KV 526936 TO TUCO_INT 7 345.0 KV 525832 CKT 1, b. with stuck breaker near YOAKUM_345 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM3_115kV_526934 | a. Apply single-phase fault on: a.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 a.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, b. with stuck breaker near YOAKUM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25S | Transfer | YOAKUM6_230kV_526935 | a. Apply single-phase fault on: a.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, b. with stuck breaker near YOAKUM 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSTANG 6 230.0 KV 527149 TO YOAKUM 6 230.0 KV 526935 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-239 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2017-239 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | 112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | 112GORE4__RPPAPER4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | 34TH_ST_TP_3__COULTER____3 | 3 Phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 34TH_ST_TP 3 115.0 KV 524281 TO COULTER 3 115.0 KV 524306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ADAIR______2__SULPHUR____2 | 3 Phase fault on ADAIR 2 (527253) 69 kV Bus a. Apply fault at the ADAIR 2 (527253) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR 2 69.0 KV 527253 TO SULPHUR 2 69.0 KV 527261 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMOCO_SS___6__YOAKUM_____6 | 3 Phase fault on AMOCO_SS 6 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMOCO_TP___3__LG_LEVELAND3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMOCOWASSON6__MUSTANG____6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMOCOWASSON6__XTO_MAHONEY6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA7__SEMINOL7 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BENNETT____3__ARCO_TP____3 | 3 Phase fault on BENNETT 3 (527018) 115 kV Bus a. Apply fault at the BENNETT 3 (527018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BENNETT____3__ODC_TP_____3 | 3 Phase fault on BENNETT 3 (527018) 115 kV Bus a. Apply fault at the BENNETT 3 (527018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BORDER_____7__WWDBORDT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BROWNFIELD_2__BROWNFLD_TP2 | 3 Phase fault on BROWNFIELD 2 (526754) 69 kV Bus a. Apply fault at the BROWNFIELD 2 (526754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNFIELD 2 69.0 KV 526754 TO BROWNFLD_TP2 69.0 KV 526761 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BUSHLAND___3__COULTER____3 | 3 Phase fault on BUSHLAND 3 (524266) 115 kV Bus a. Apply fault at the BUSHLAND 3 (524266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUTPOST 3 115.0 KV 524243 TO BUSHLAND 3 115.0 KV 524266 CKT 1 b.2. OUTPOST 3 115.0 KV 524243 TO ARNOT 3 115.0 KV 524560 CKT 1 b.3. LOAD 1 524560 b.4. HILLSIDE 3 115.0 KV 524300 TO ARNOT 3 115.0 KV 524560 CKT 1 b.5. LOAD 1 524560 b.6. HILLSIDE 3 115.0 KV 524300 TO COULTER 3 115.0 KV 524306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BUSHLAND___6__DEAFSMITH__6 | 3 Phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 230.0 KV 524267 TO DEAFSMITH 6 230.0 KV 524623 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BUSHLAND___6__WILDOR2_JUS6 | 3 Phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 230.0 KV 524267 TO WILDOR2_JUS6 230.0 KV 524290 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | C_RIVER7__FIREWHL_TAP | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CANYON_E_TP3__CANYON_EAST3 | 3 Phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANYON_E_TP3 115.0 KV 524522 TO CANYON_EAST3 115.0 KV 524523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CARGILL____3__PARMER_CO__3 | 3 Phase fault on CARGILL 3 (524648) 115 kV Bus a. Apply fault at the CARGILL 3 (524648) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARGILL 3 115.0 KV 524648 TO DS-#24 +3 115.0 KV 524664 CKT 1 b.2. LOAD 1 524664 b.3. PARMER_CO 3 115.0 KV 524662 TO DS-#24 +3 115.0 KV 524664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CENTRE_ST__2__NE_HEREFORD2 | 3 Phase fault on CENTRE_ST 2 (524554) 69 kV Bus a. Apply fault at the CENTRE_ST 2 (524554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRE_ST 2 69.0 KV 524554 TO NE_HEREFORD2 69.0 KV 524573 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHISHOLM7__WWDBORDT | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CIMARON7__FSHRTAP7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CIMARON7__MATHWSN7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CIMARON7__NSUB345 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COULTER____3__ESTACADO_TP3 | 3 Phase fault on COULTER 3 (524306) 115 kV Bus a. Apply fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTER 3 115.0 KV 524306 TO ESTACADO_TP3 115.0 KV 524425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CURRY______3__FE_CLOVIS2_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DC_EAST____2__DENVER_CTY_2 | 3 Phase fault on DC_EAST 2 (527099) 69 kV Bus a. Apply fault at the DC_EAST 2 (527099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DC_EAST 2 69.0 KV 527099 TO DENVER_CTY 2 69.0 KV 527125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_CTY_2__JAYBEE_____2 | 3 Phase fault on DENVER_CTY 2 (527125) 69 kV Bus a. Apply fault at the DENVER_CTY 2 (527125) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_CTY 2 69.0 KV 527125 TO JAYBEE 2 69.0 KV 527183 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_CTY_2__MIDAMERI_TP2 | 3 Phase fault on DENVER_CTY 2 (527125) 69 kV Bus a. Apply fault at the DENVER_CTY 2 (527125) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_CTY 2 69.0 KV 527125 TO MIDAMERI_TP2 69.0 KV 527313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_N___3__HIGG_______3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 b.2. LOAD 1 527286 b.3. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_N___3__HIGGEAST___3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_N___3__SHELL_CO2__3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 b.2. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_S___3__SHELLC3_TP_3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 b.2. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DIAMONDBACK2__CEDARLAKE__2 | 3 Phase fault on DIAMONDBACK2 (527211) 69 kV Bus a. Apply fault at the DIAMONDBACK2 (527211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK2 69.0 KV 527211 TO OXY_CEDRLKE2 69.0 KV 527250 CKT 1 b.2. LOAD 1 527250 b.3. CEDARLAKE 2 69.0 KV 527247 TO OXY_CEDRLKE2 69.0 KV 527250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DIAMONDBACK2__LG_ASHMORE_2 | 3 Phase fault on DIAMONDBACK2 (527211) 69 kV Bus a. Apply fault at the DIAMONDBACK2 (527211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK2 69.0 KV 527211 TO LG-ASHMORE 2 69.0 KV 527235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DIAMONDBACK2__LG_SAWYERFL2 | 3 Phase fault on DIAMONDBACK2 (527211) 69 kV Bus a. Apply fault at the DIAMONDBACK2 (527211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK2 69.0 KV 527211 TO OZRK_MAH02 2 69.0 KV 527229 CKT 1 b.2. LOAD 1 527229 b.3. OZRK_MAH02 2 69.0 KV 527229 TO LG-SAWYERFL2 69.0 KV 527305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_7__NSUB345 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_7__SEMINOL7 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS__5&_11__2__CENTRE_ST__2 | 3 Phase fault on DS-#5&#11 2 (524536) 69 kV Bus a. Apply fault at the DS-#5&#11 2 (524536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#5&#11 2 69.0 KV 524536 TO CENTRE_ST 2 69.0 KV 524554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS__9______2__HERFRD_STH_2 | 3 Phase fault on DS-#9 +2 (524580) 69 kV Bus a. Apply fault at the DS-#9 +2 (524580) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#9 +2 69.0 KV 524580 TO HERFRD_STH 2 69.0 KV 524608 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DS_MTR_____2__NE_HEREFORD2 | 3 Phase fault on DS-MTR 2 (524561) 69 kV Bus a. Apply fault at the DS-MTR 2 (524561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-MTR 2 69.0 KV 524561 TO NE_HEREFORD2 69.0 KV 524573 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | E_CLOVIS___3__CURRY______3 | 3 Phase fault on E_CLOVIS 3 (524773) 115 kV Bus a. Apply fault at the E_CLOVIS 3 (524773) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | E_LEVELLAND2__SLAUGTER_TP2 | 3 Phase fault on E_LEVELLAND2 (526056) 69 kV Bus a. Apply fault at the E_LEVELLAND2 (526056) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_LEVELLAND2 69.0 KV 526056 TO SLAUGTER_TP2 69.0 KV 526416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ELKCITY6__CHISHOLM6 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EMULESH&VLY2__BAILEYCO___2 | 3 Phase fault on EMULESH&VLY2 (525017) 69 kV Bus a. Apply fault at the EMULESH&VLY2 (525017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMULESH&VLY2 69.0 KV 525017 TO BAILEYCO 2 69.0 KV 525027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FE_CHZPLT__3__OASIS______3 | 3 Phase fault on FE-CHZPLT 3 (524863) 115 kV Bus a. Apply fault at the FE-CHZPLT 3 (524863) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FT_SILL2__PO_HILL2 | 3 Phase fault on FT.SILL2 (511461) 69 kV Bus a. Apply fault at the FT.SILL2 (511461) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | GEORGIA____3__RANDALL____3 | 3 Phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEORGIA 3 115.0 KV 524322 TO RANDALL 3 115.0 KV 524364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HARRNG_WST_6__ROLLHILLS__6 | 3 Phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 230.0 KV 523977 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HEREFORD___3__CARGILL____3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO DS-#6 3 115.0 KV 524629 CKT 1 b.2. LOAD 1 524629 b.3. DS-#6 3 115.0 KV 524629 TO FRIONA 3 115.0 KV 524655 CKT 1 b.4. LOAD 1 524655 b.5. LOAD D1 524655 b.6. CARGILL 3 115.0 KV 524648 TO FRIONA 3 115.0 KV 524655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HERFRD_STH_2__DS__4______2 | 3 Phase fault on HERFRD_STH 2 (524608) 69 kV Bus a. Apply fault at the HERFRD_STH 2 (524608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERFRD_STH 2 69.0 KV 524608 TO DS-#4 +2 69.0 KV 524633 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HIGG_______3__BENSING____3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4__CANEYCK4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4__RUSSET_4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4__SXMLCKT4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KINNEY_____2__TOKIO_TP___2 | 3 Phase fault on KINNEY 2 (526965) 69 kV Bus a. Apply fault at the KINNEY 2 (526965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINNEY 2 69.0 KV 526965 TO TOKIO_TP 2 69.0 KV 526971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMB_CNTY__2__LC_LTTLFLD_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMB_CNTY__2__LC_LUMSCHAP2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LUMSCHAP2 69.0 KV 525687 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAPLATA____3__NE_HEREFORD3 | 3 Phase fault on LAPLATA 3 (524556) 115 kV Bus a. Apply fault at the LAPLATA 3 (524556) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAPLATA 3 115.0 KV 524556 TO NE_HEREFORD3 115.0 KV 524567 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LC_OPDYKE__3__SUNDOWN____3 | 3 Phase fault on LC-OPDYKE 3 (526036) 115 kV Bus a. Apply fault at the LC-OPDYKE 3 (526036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LG_ASHMORE_2__ADAIR______2 | 3 Phase fault on LG-ASHMORE 2 (527235) 69 kV Bus a. Apply fault at the LG-ASHMORE 2 (527235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-ASHMORE 2 69.0 KV 527235 TO ADAIR 2 69.0 KV 527253 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LG_DIXON___2__BROWNFIELD_2 | 3 Phase fault on LG-DIXON 2 (526711) 69 kV Bus a. Apply fault at the LG-DIXON 2 (526711) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DIXON 2 69.0 KV 526711 TO BROWNFIELD 2 69.0 KV 526754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LG_JS_SMITH2__WELLMAN____2 | 3 Phase fault on LG-JS_SMITH2 (526979) 69 kV Bus a. Apply fault at the LG-JS_SMITH2 (526979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-JS_SMITH2 69.0 KV 526979 TO WELLMAN 2 69.0 KV 526985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LG_MC&SMNL_2__LG_SAWYERFL2 | 3 Phase fault on LG-MC&SMNL+2 (527223) 69 kV Bus a. Apply fault at the LG-MC&SMNL+2 (527223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-MC&SMNL+2 69.0 KV 527223 TO LG-SAWYERFL2 69.0 KV 527305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LG_PLSHILL_3__SEAGRAVES__3 | 3 Phase fault on LG-PLSHILL 3 (527194) 115 kV Bus a. Apply fault at the LG-PLSHILL 3 (527194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LYDIA__7__VALIANT7 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MANHATTAN__3__RANDALL____3 | 3 Phase fault on MANHATTAN 3 (524224) 115 kV Bus a. Apply fault at the MANHATTAN 3 (524224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANHATTAN 3 115.0 KV 524224 TO RANDALL 3 115.0 KV 524364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MNCWND37__MNCWND47 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MOORE_CNTY_6__MCDWL_CREEK6 | 3 Phase fault on MOORE_CNTY 6 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 230.0 KV 523309 TO MCDWL_CREEK6 230.0 KV 523323 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MULESH_CTY_2__BAILEYCO___2 | 3 Phase fault on MULESH_CTY 2 (525008) 69 kV Bus a. Apply fault at the MULESH_CTY 2 (525008) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESH_CTY 2 69.0 KV 525008 TO BAILEYCO 2 69.0 KV 525027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NE_HEREFORD3__HEREFORD___3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO HEREFORD 3 115.0 KV 524606 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NEWHART____3__LAMTON_____3 | 3 Phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 b.2. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NORTH_LOVNG3__SOUTH_LOVNG3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NORTWST7__CIMARON7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NWTXARK7__VALIANT7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at Oklaunion due to capacitor banks online. | Switch off capacitor banks at Oklaunion following fault
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PACIFIC____3__SUNDOWN____3 | 3 Phase fault on PACIFIC 3 (526424) 115 kV Bus a. Apply fault at the PACIFIC 3 (526424) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PARMER_CO__3__DS__20_____3 | 3 Phase fault on PARMER_CO 3 (524662) 115 kV Bus a. Apply fault at the PARMER_CO 3 (524662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARMER_CO 3 115.0 KV 524662 TO DS-#20 3 115.0 KV 524669 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PERIMETER__3__OASIS______3 | 3 Phase fault on PERIMETER 3 (524797) 115 kV Bus a. Apply fault at the PERIMETER 3 (524797) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PHANTOM____3__BOPCO_PKRLK3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PITTSB_7__C_RIVER7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PITTSB_7__KIOWA__7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PITTSB_7__SEMINOL7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PITTSB_7__VALIANT7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLAINS_INT_3__LG_PLAINS__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLAINVW_TP_2__LH_HALECTR_2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO LH-HALECTR 2 69.0 KV 525745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNT_HILL_3__E_CLOVIS___3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNT_HILL_3__FE_HOLLAND_3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PORTALES___3__GREYHOUND__3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO KILGORE 3 115.0 KV 524935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PRENTICE___3__YOAKUM_____3 | 3 Phase fault on PRENTICE 3 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PRINGLE____6__HARRNG_EST_6 | 3 Phase fault on PRINGLE 6 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 230.0 KV 523267 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PUCKETT____3__COULTER____3 | 3 Phase fault on PUCKETT 3 (524256) 115 kV Bus a. Apply fault at the PUCKETT 3 (524256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKETT 3 115.0 KV 524256 TO COULTER 3 115.0 KV 524306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RANDALL____3__CANYON_E_TP3 | 3 Phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 3 115.0 KV 524364 TO CANYON_E_TP3 115.0 KV 524522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RANDALL____3__PALO_DURO__3 | 3 Phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 3 115.0 KV 524364 TO PALO_DURO 3 115.0 KV 524530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER___3__AGAVE_RHILL3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SAGA_SDCOL_7__SAGA_SCOL__7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SAN_ANDS_TP3__SAN_ANDRES_3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SAN_ANDRES 3 115.0 KV 527106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEAGRAVES__2__TOKIO_TP___2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 b.2. LOAD 1 527217 b.3. TOKIO_TP 2 69.0 KV 526971 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEAGRAVES__2__WELLMAN____2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 b.2. WELLMAN 2 69.0 KV 526985 TO LG-WELLMAN 2 69.0 KV 526993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEAGRAVES__3__YOAKUM_____3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 b.2. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL7__MUSKOGE7 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SLAUGHTER__2__SLAUGTER_TP2 | 3 Phase fault on SLAUGHTER 2 (526409) 69 kV Bus a. Apply fault at the SLAUGHTER 2 (526409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLAUGHTER 2 69.0 KV 526409 TO SLAUGTER_TP2 69.0 KV 526416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SOUTHEAST__3__RANDALL____3 | 3 Phase fault on SOUTHEAST 3 (524338) 115 kV Bus a. Apply fault at the SOUTHEAST 3 (524338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHEAST 3 115.0 KV 524338 TO RANDALL 3 115.0 KV 524364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SP_BECTON__2__ALLMON_____2 | 3 Phase fault on SP-BECTON +2 (525860) 69 kV Bus a. Apply fault at the SP-BECTON +2 (525860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-BECTON +2 69.0 KV 525860 TO ALLMON 2 69.0 KV 525867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SP_ERSKINE_3__CARLISLE___3 | 3 Phase fault on SP-ERSKINE 3 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | STANTON_N__2__STANTON_E__2 | 3 Phase fault on STANTON_N 2 (526073) 69 kV Bus a. Apply fault at the STANTON_N 2 (526073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_N 2 69.0 KV 526073 TO STANTON_E 2 69.0 KV 526075 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | STANTON_N__2__SW_6786_N__2 | 3 Phase fault on STANTON_N 2 (526073) 69 kV Bus a. Apply fault at the STANTON_N 2 (526073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_N 2 69.0 KV 526073 TO SW_6786_N 2 69.0 KV 526086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SULPHUR____2__UNION_TX___2 | 3 Phase fault on SULPHUR 2 (527261) 69 kV Bus a. Apply fault at the SULPHUR 2 (527261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULPHUR 2 69.0 KV 527261 TO LG-FOSTER +2 69.0 KV 527271 CKT 1 b.2. LOAD 1 527271 b.3. UNION_TX 2 69.0 KV 526999 TO LG-FOSTER +2 69.0 KV 527271 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNDOWN____6__YOAKUM_____6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 b.2. LOAD 1 526460 b.3. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4__GEN_2017_167 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO GEN-2017-167 138.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4__LONEGRV4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4__UNIROY_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SWEETWT6__CHISHOLM6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRY_CNTY_2__BROWNFIELD_2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 b.2. LOAD 1 526747 b.3. LG-BROWNFLD2 69.0 KV 526747 TO BROWNFIELD 2 69.0 KV 526754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRY_CNTY_2__SLAUGTER_TP2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 b.2. LG-MEADOW 2 69.0 KV 526499 TO LG-DOCWEBR 2 69.0 KV 526506 CKT 1 b.3. LOAD 1 526506 b.4. SLAUGTER_TP2 69.0 KV 526416 TO LG-MEADOW 2 69.0 KV 526499 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRY_CNTY_3__YOAKUM_____3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 b.2. LOAD 1 526792 b.3. LOAD D1 526792 b.4. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TIERABLANCA3__CANYON_E_TP3 | 3 Phase fault on TIERABLANCA3 (524630) 115 kV Bus a. Apply fault at the TIERABLANCA3 (524630) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 b.2. DS-#25+ 3 115.0 KV 524575 TO PANDAHFD 3 115.0 KV 524597 CKT 1 b.3. LOAD 1 524597 b.4. DAWN 3 115.0 KV 524590 TO PANDAHFD 3 115.0 KV 524597 CKT 1 b.5. LOAD 1 524597 b.6. CANYON_WEST3 115.0 KV 524516 TO DAWN 3 115.0 KV 524590 CKT 1 b.7. LOAD 1 524590 b.8. CANYON_WEST3 115.0 KV 524516 TO HUNSLEY 3 115.0 KV 524520 CKT 1 b.9. LOAD 1 524520 b.10. HUNSLEY 3 115.0 KV 524520 TO CANYON_E_TP3 115.0 KV 524522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TIERABLANCA3__CASTRO_CNTY3 | 3 Phase fault on TIERABLANCA3 (524630) 115 kV Bus a. Apply fault at the TIERABLANCA3 (524630) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 b.2. LOAD 1 524734 b.3. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOKIO_TP___2__LG_SEAGRAVE2 | 3 Phase fault on TOKIO_TP 2 (526971) 69 kV Bus a. Apply fault at the TOKIO_TP 2 (526971) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOKIO_TP 2 69.0 KV 526971 TO LG-SEAGRAVE2 69.0 KV 527189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___2__LH_HALECTR_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 b.2. LOAD 1 525826 b.3. HALECENTER 2 69.0 KV 525738 TO LH-HALECTR 2 69.0 KV 525745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___2__SP_BECTON__2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 b.2. LOAD 1 525853 b.3. LOAD 2 525853 b.4. LH-WIL&ELN+2 69.0 KV 525853 TO SP-BECTON +2 69.0 KV 525860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___2__STANTON_N__2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 b.2. LOAD 1 525885 b.3. SP-NEWDEAL 2 69.0 KV 525885 TO MONROE 2 69.0 KV 525892 CKT 1 b.4. LOAD 1 525892 b.5. WHITEHEAD 2 69.0 KV 525891 TO MONROE 2 69.0 KV 525892 CKT 1 b.6. LOAD 1 525892 b.7. WHITEHEAD 2 69.0 KV 525891 TO SP-SHALLWTR2 69.0 KV 525899 CKT 1 b.8. LOAD 1 525899 b.9. SP-SHALLWTR2 69.0 KV 525899 TO STANTON_N 2 69.0 KV 526073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | W_LITTLFLD_2__LAMB_CNTY__2 | 3 Phase fault on W_LITTLFLD 2 (525613) 69 kV Bus a. Apply fault at the W_LITTLFLD 2 (525613) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WASSON_____2__DENVER_CTY_2 | 3 Phase fault on WASSON 2 (527111) 69 kV Bus a. Apply fault at the WASSON 2 (527111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASSON 2 69.0 KV 527111 TO DENVER_CTY 2 69.0 KV 527125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WELLMAN____2__UNION_TX___2 | 3 Phase fault on WELLMAN 2 (526985) 69 kV Bus a. Apply fault at the WELLMAN 2 (526985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLMAN 2 69.0 KV 526985 TO UNION_TX 2 69.0 KV 526999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WILDOR_WND_6__WILDOR2_JUS6 | 3 Phase fault on WILDOR_WND 6 (524276) 230 kV Bus a. Apply fault at the WILDOR_WND 6 (524276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILDOR_WND 6 230.0 KV 524276 TO WILDOR2_JUS6 230.0 KV 524290 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV7__WWDBORDT | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | XIT_INTG___6__CHAN_TASCOS6 | 3 Phase fault on XIT_INTG 6 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 230.0 KV 523221 TO CHAN+TASCOS6 230.0 KV 523869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | XTO_CORNEL_3__SHELLC3_TP_3 | 3 Phase fault on XTO_CORNEL+3 (527033) 115 kV Bus a. Apply fault at the XTO_CORNEL+3 (527033) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_____3__LG_PLSHILL_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YUMA_INT___3__WOLFFORTH__3 | 3 Phase fault on YUMA_INT 3 (526475) 115 kV Bus a. Apply fault at the YUMA_INT 3 (526475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BAILEYCO___3__525027_0 | 3 Phase fault on BAILEYCO 3 (525028) 115 kV Bus a. Apply fault at the BAILEYCO 3( 525028) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEYCO 3 525028 TO BAILEYCO 2 525027 TO BAILY_TR2 1 525026 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BUSHLAND___6__524266_0 | 3 Phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6( 524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 524267 TO BUSHLAND 3 524266 TO BSHLND_TR1 1 524263 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | C_RIVER7__510946_0 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CASTRO_CNTY3__524745_0 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3( 524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 524746 TO CASTRO_CNTY2 524745 TO CASTRO_TR1 1 524744 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CIMARON4__514901_0 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COULTER____3__524305_0 | 3 Phase fault on COULTER 3 (524306) 115 kV Bus a. Apply fault at the COULTER 3( 524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTER 3 524306 TO COULTER 2 524305 TO COLTER_TR1 1 524304 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | COX________3__525325_0 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3( 525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 525326 TO COX 2 525325 TO COX_TR1 1 525324 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DEAFSMITH__6__524619_0 | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6( 524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 524623 TO DFSMTH_EST 3 524619 TO DEFSMTH_TR21 524621 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DEAFSMITH__6__524622_0 | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6( 524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 524623 TO DFSMTH_WST 3 524622 TO DEFSMTH_TR11 524620 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DIAMONDBACK3__527211_0 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3( 527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 527212 TO DIAMONDBACK2 527211 TO DIMNDBK_TR11 527210 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HEREFORD___3__524604_0 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3( 524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 524606 TO HEREFRD_SB 2 524604 TO HERFRD_TR2 1 524603 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HEREFORD___3__524605_0 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3( 524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 524606 TO HEREFRD_NB 2 524605 TO HERFRD_TR1 1 524602 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7( 523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KRESS_INT__3__525191_0 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3( 525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 525192 TO KRESS_INT 2 525191 TO KRESS_TR1 1 525190 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMB_CNTY__3__525635_0 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3( 525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 525636 TO LAMB_CNTY 2 525635 TO LAMB_TR2 1 525632 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMTON_____3__525413_0 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3( 525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 525414 TO LAMTON 2 525413 TO LAMTON_TR1 1 525412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MCDWL_CREEK6__523322_0 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6( 523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 523323 TO MCDWL_CREEK3 523322 TO MCDWL_CRKTR1 523321 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NE_HEREFORD3__524573_0 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3( 524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 524567 TO NE_HEREFORD2 524573 TO NE_HRFD_TR11 524565 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OKLAUN_7__590003_0 | 3 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLVALLY4__555234_0 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RANDALL____6__524364_0 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6( 524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 524365 TO RANDALL 3 524364 TO RANDAL_TR1 1 524361 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ROLLHILLS__6__524007_0 | 3 Phase fault on ROLLHILLS 6 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6( 524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 524010 TO ROLLHILLS 3 524007 TO ROLHILLS_TR1 524008 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RSHSPR1_COL1__511979_0 | 3 Phase fault on RSHSPR1 (511978) 345 kV Bus a. Apply fault at the RSHSPR1( 511978) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL4__515045_0 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SULPHUR____3__527261_0 | 3 Phase fault on SULPHUR 3 (527262) 115 kV Bus a. Apply fault at the SULPHUR 3( 527262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULPHUR 3 527262 TO SULPHUR 2 527261 TO SLPHUR_TR2 1 527260 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | VALIANT4__510911_0 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BORDER7_345kV_515458 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, b. with stuck breaker near BORDER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BRU_SUB6_230kV_527009 | a. Apply single-phase fault on: a.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, b. with stuck breaker near BRU_SUB 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-239 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2017-239 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | BUSHLAND6_230kV_524267 | a. Apply single-phase fault on: a.1. POTTERCO6 230.0 KV 523959 TO BUSHLAND6 230.0 KV 524267 CKT 1, b. with stuck breaker near BUSHLAND 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CHINA_DRAW7_345kV_528223 | a. Apply single-phase fault on: a.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, b. with stuck breaker near CHINA_DRAW 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CROSSROADS7_345kV_527656 | a. Apply single-phase fault on: a.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1, b. with stuck breaker near CROSSROADS 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. HOBBS_INT 7 345.0 KV 527896 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CUNNINHAM3_115kV_527864 | a. Apply single-phase fault on: a.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, b. with stuck breaker near CUNNINHAM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CUNNINHAM6_230kV_527867 | a. Apply single-phase fault on: a.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, b. with stuck breaker near CUNNIGHM_S 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | CUNNINHAMN6_230kV_527865 | a. Apply single-phase fault on: a.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, b. with stuck breaker near CUNNIGHM_N 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | DEAFSMITH6_230kV_524623 | a. Apply single-phase fault on: a.1. DEAFSMITH6 230.0 KV 524623 TO G17146TAP 230.0 KV 760498 CKT 1, b. with stuck breaker near DEAFSMITH 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | EDDY_CNTY7_345kV_527802 | a. Apply single-phase fault on: a.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, b. with stuck breaker near EDDY_CNTY 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | FLATLAND3_115kV_527257 | a. Apply single-phase fault on: a.1. FLATLAND 3 115.0 KV 527257 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1, b. with stuck breaker near FLATLAND 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. FLATLAND 3 115.0 KV 527257 TO DIAMONDBACK3 115.0 KV 527212 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT3_115kV_527891 | a. Apply single-phase fault on: a.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, b. with stuck breaker near HOBBS_INT 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. HOBBS_INT 3 115.0 KV 527891 TO CUNNINHAM 3 115.0 KV 527864 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT6_230kV_527894 | a. Apply single-phase fault on: a.1. ANDREWS 6 230.0 KV 528604 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, b. with stuck breaker near HOBBS_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOBBS_INT7_345kV_527896 | a. Apply single-phase fault on: a.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, b. with stuck breaker near HOBBS_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. RDRUNNER 7 345.0 KV 528027 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | HOCKLEY3_115kV_526020 | a. Apply single-phase fault on: a.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 a.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, b. with stuck breaker near HOCKLEY 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | INK_BASIN3_115kV_527027 | a. Apply single-phase fault on: a.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, b. with stuck breaker near INK_BASIN 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | INK_BASIN6_230kV_527028 | a. Apply single-phase fault on: a.1. INK_BASIN 6 230.0 KV 527028 TO YOAKUM 6 230.0 KV 526935 CKT 1, b. with stuck breaker near INK_BASIN 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | JONES6_230kV_526337 | a. Apply single-phase fault on: a.1. TUCOINT6 230.0 KV 525830 TO JONES6 230.0 KV 526337 CKT 1, b. with stuck breaker near JONES 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. LUBBCKSTH6 230.0 KV 526269 TO JONES6 230.0 KV 526337 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | KIOWA7_345kV_527965 | a. Apply single-phase fault on: a.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, b. with stuck breaker near KIOWA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMB_CNTY_69kV_525635 | a. Apply single-phase fault on: a.1. LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 a.2. LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, b. with stuck breaker near LAMB_CNTY 2 69 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 c.3. LOAD 1 525613 c.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 c.5. LOAD 1 525606 c.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LAMB_CNTY3_115kV_525636 | a. Apply single-phase fault on: a.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, b. with stuck breaker near LAMB_CNTY 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LES4_138kV_511467 | a. Apply single-phase fault on: a.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 a.2. LOAD 1 511474 a.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, b. with stuck breaker near L.E.S.-4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-4 138.0 KV 511467 TO LWSTAP 4 138.0 KV 511439 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LES7_345kV_511468 | a. Apply single-phase fault on: a.1. L.E.S.-7 345.0 KV 511468 TO O.K.U.-7 345.0 KV 511456 CKT 1, b. with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | LUBBUCK_EST_115kV_526298 | a. Apply single-phase fault on: a.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, b. with stuck breaker near LUBBCK_EST 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | Maddox_115kV_528355 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO Hobbs Int 115KV 527891 CKT 1, b. with stuck breaker near MADDOX 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. Maddox 115KV 528355 TO SANGER_SW 3 115KV 528463 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | MUSTANG6_230kV_527149 | a. Apply single-phase fault on: a.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, b. with stuck breaker near MUSTANG 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | N_LOVING7_345kV_528185 | a. Apply single-phase fault on: a.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, b. with stuck breaker near N_LOVING 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NA_ENRICH3_115kV_528603 | a. Apply single-phase fault on: a.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, b. with stuck breaker near NA_ENRICH 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 c.2. LOAD 1 528605 c.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NEWHART3_115kV_525460 | a. Apply single-phase fault on: a.1. KRESSINT3 115.0 KV 525192 TO NEWHART3 115.0 KV 525460 CKT 1, b. with stuck breaker near NEWHART 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. HARTINDUST3 115.0 KV 525124 TO NEWHART3 115.0 KV 525460 CKT 1 c.2. HARTINDUST3 115.0 KV 525124 TO LAMTON3 115.0 KV 525414 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | NEWHART6_230kV_525461 | a. Apply single-phase fault on: a.1. NEWHART6 230.0 KV 525461 TO PLANTX6 230.0 KV 525481 CKT 1, b. with stuck breaker near NEWHART 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. POTTERCO6 230.0 KV 523959 TO NEWHART6 230.0 KV 525461 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OASIS3_115kV_524874 | a. Apply single-phase fault on: a.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, b. with stuck breaker near OASIS 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 c.2. LOAD 1 524863 c.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OASIS6_230kV_524875 | a. Apply single-phase fault on: a.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, b. with stuck breaker near OASIS 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SN_JUAN_TAP6 230.0 KV 524885 TO OASIS 6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | OKU7_345kV_511456 | a. Apply single-phase fault on: a.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1, b. with stuck breaker near O.K.U.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at Oklaunion due to capacitor banks online. | Switch off capacitor banks at Oklaunion following fault
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PHANTOM7_345kV_528015 | a. Apply single-phase fault on: a.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, b. with stuck breaker near PHANTOM 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANT_X3_115kV_525480 | a. Apply single-phase fault on: a.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1, b. with stuck breaker near PLANT_X 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLANTX_230kV_525481 | a. Apply single-phase fault on: a.1. PLANTX6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 1, b. with stuck breaker near PLANT_X 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLANTX6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNTHILL3_115kV_524768 | a. Apply single-phase fault on: a.1. PLSNTHILL3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1, b. with stuck breaker near PLSNT_HILL 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLSNTHILL3 115.0 KV 524768 TO NORTON 3 115.0 KV 524502 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | PLSNTHILL6_230kV_524770 | a. Apply single-phase fault on: a.1. PLSNTHILL6 230.0 KV 524770 TO ROOSEVELT6 230.0 KV 524909 CKT 1, b. with stuck breaker near PLSNT_HILL 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLSNTHILL6 230.0 KV 524770 TO OASIS6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTER_CO7_345kV_523961 | a. Apply single-phase fault on: a.1. POTTER_CO 7 345.0 KV 523961 TO HITCHLAND 7 345.0 KV 523097 CKT 1, b. with stuck breaker near POTTER_CO 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. SPNSPUR_WND7 345.0 KV 524296 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | POTTERCO6_230kV_523959 | a. Apply single-phase fault on: a.1. POTTERCO6 230.0 KV 523959 TO HARRNG_EST6 230.0 KV 523979 CKT 1, b. with stuck breaker near POTTER_CO 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. POTTERCO6 230.0 KV 523959 TO MCDWL_CREEK6 230.0 KV 523323 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER3_115kV_528025 | a. Apply single-phase fault on: a.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, b. with stuck breaker near RDRUNNER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNER7_345kV_528027 | a. Apply single-phase fault on: a.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, b. with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | RED_BLUFF_115kV_528018 | a. Apply single-phase fault on: a.1. REDBLUFF 115KV 528018 TO WOLFCAMPTP 115KV 528235 CKT 1, b. with stuck breaker near RED_BLUFF 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. REDBLUFF 115KV 528018 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | ROOSEVELT6_230kV_524909 | a. Apply single-phase fault on: a.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, b. with stuck breaker near ROOSEVELT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TOLK 6 230.0 KV 525531 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SEAGRAVES3_115kV_527202 | a. Apply single-phase fault on: a.1. SEAGRAVES3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1, b. with stuck breaker near SEAGRAVES 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSTANG3 115.0 KV 527146 TO SEAGRAVES3 115.0 KV 527202 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SULPHUR2_69kV_527261 | a. Apply single-phase fault on: a.1. ADAIR2 69.0 KV 527253 TO SULPHUR2 69.0 KV 527261 CKT 1, b. with stuck breaker near SULPHUR 2 69 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SULPHUR2 69.0 KV 527261 TO LGFOSTER2 69.0 KV 527271 CKT 1 c.2. UNIONTX2 69.0 KV 526999 TO LGFOSTER2 69.0 KV 527271 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SULPHUR3_115kV_527262 | a. Apply single-phase fault on: a.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR3 115.0 KV 527262 CKT 1, b. with stuck breaker near SULPHUR 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR3 115.0 KV 527262 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNDOWN6_230kV_526435 | a. Apply single-phase fault on: a.1. SUNDOWN 6 230.0 KV 526435 TO PLANT_X 6 230.0 KV 525481 CKT 1, b. with stuck breaker near SUNDOWN 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD7_345kV_515136 | a. Apply single-phase fault on: a.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1, b. with stuck breaker near SUNNYSD7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. G16-063-TAP 3 345.0 KV 560088 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | SWISHER6_230kV_525213 | a. Apply single-phase fault on: a.1. AMASOUTH6 230.0 KV 524415 TO SWISHER6 230.0 KV 525213 CKT 1, b. with stuck breaker near SWISHER 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SWISHER6 230.0 KV 525213 TO TUCO_INT6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRYCNTY3_115kV_526736 | a. Apply single-phase fault on: a.1. TERTRYCNTY3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1, b. with stuck breaker near TERRY_CNTY 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TERTRYCNTY3 115.0 KV 526736 TO DENVERN3 115.0 KV 527130 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7_345kV_511568 | a. Apply single-phase fault on: a.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, b. with stuck breaker near TERRYRD7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 3 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TIERABLANCA3_115kV_524630 | a. Apply single-phase fault on: a.1. DFSMTHEST3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1, b. with stuck breaker near TIERABLANCA3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TOLK6_230kV_525531 | a. Apply single-phase fault on: a.1. TOLK 6 230.0 KV 525531 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, b. with stuck breaker near TOLK 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT6_230kV_525830 | a. Apply single-phase fault on: a.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, b. with stuck breaker near TUCO_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT7_345kV_525832 | a. Apply single-phase fault on: a.1. TUCO_INT 7 345.0 KV 525832 TO BORDER 7 345.0 KV 515458 CKT 1, b. with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM_345kV_526936 | a. Apply single-phase fault on: a.1. YOAKUM_345 345.0 KV 526936 TO TUCO_INT 7 345.0 KV 525832 CKT 1, b. with stuck breaker near YOAKUM_345 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM3_115kV_526934 | a. Apply single-phase fault on: a.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 a.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, b. with stuck breaker near YOAKUM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2017-002 CF | 25W | Transfer | YOAKUM6_230kV_526935 | a. Apply single-phase fault on: a.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, b. with stuck breaker near YOAKUM 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSTANG 6 230.0 KV 527149 TO YOAKUM 6 230.0 KV 526935 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-239 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2017-239 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2017-175 | 01 NORTH | 587760 | GEN-2016-094 | 230 | 9.198 | 9.2023 | 0.0043
GEN-2017-175 | 01 NORTH | 587764 | G16-094-TAP | 230 | 9.3571 | 9.3615 | 0.0044
GEN-2017-175 | 01 NORTH | 588590 | GEN-2017-014 | 230 | 5.6157 | 5.616 | 0.0003
GEN-2017-175 | 01 NORTH | 589320 | GEN-2017-094 | 230 | 8.045 | 8.0477 | 0.0027
GEN-2017-175 | 01 NORTH | 589324 | G17-094-TAP | 230 | 8.045 | 8.0477 | 0.0027
GEN-2017-175 | 01 NORTH | 601006 | SPLT RK3 | 345 | 14.2731 | 14.3111 | 0.038
GEN-2017-175 | 01 NORTH | 602004 | SPLT RK4 | 230 | 13.1332 | 13.2839 | 0.1507
GEN-2017-175 | 01 NORTH | 602005 | SPLT RK5 | 161 | 8.748 | 8.7583 | 0.0103
GEN-2017-175 | 01 NORTH | 603011 | MINEHAH7 | 115 | 13.5113 | 13.5407 | 0.0294
GEN-2017-175 | 01 NORTH | 603012 | LAWRENC7 | 115 | 30.582 | 30.7381 | 0.1561
GEN-2017-175 | 01 NORTH | 603013 | PIPESTN7 | 115 | 9.8007 | 9.8018 | 0.0011
GEN-2017-175 | 01 NORTH | 603016 | SPLT RK7 | 115 | 38.6582 | 38.8536 | 0.1954
GEN-2017-175 | 01 NORTH | 603017 | WSX FLS7 | 115 | 15.2049 | 15.2374 | 0.0325
GEN-2017-175 | 01 NORTH | 603149 | ANSON4 | 115 | 36.6291 | 36.8046 | 0.1755
GEN-2017-175 | 01 NORTH | 603200 | ANSON 7 | 115 | 35.224 | 35.3765 | 0.1525
GEN-2017-175 | 01 NORTH | 603225 | FALLS 7 | 115 | 15.2674 | 15.2992 | 0.0318
GEN-2017-175 | 01 NORTH | 603228 | SPLITRK CAP7 | 115 | 38.0778 | 38.2674 | 0.1896
GEN-2017-175 | 01 NORTH | 603264 | PROSE WIND7 | 115 | 5.09 | 5.0922 | 0.0022
GEN-2017-175 | 01 NORTH | 603265 | PROSE CAP7 | 115 | 36.6889 | 36.8644 | 0.1755
GEN-2017-175 | 01 NORTH | 603274 | RENNER 7 | 115 | 12.4385 | 12.4598 | 0.0213
GEN-2017-175 | 01 NORTH | 605191 | LAWRENC8 | 69 | 16.3999 | 16.4262 | 0.0263
GEN-2017-175 | 01 NORTH | 635223 | PLYMOTH5 | 161 | 20.7459 | 20.7826 | 0.0367
GEN-2017-175 | 01 NORTH | 640126 | E.COL. 4 | 230 | 10.4364 | 10.4389 | 0.0025
GEN-2017-175 | 01 NORTH | 640131 | COLMB.W4 | 230 | 10.2014 | 10.2037 | 0.0023
GEN-2017-175 | 01 NORTH | 640133 | COLMBUS4 | 230 | 11.8908 | 11.8942 | 0.0034
GEN-2017-175 | 01 NORTH | 640134 | KELLY 7 | 115 | 18.4081 | 18.4111 | 0.003
GEN-2017-175 | 01 NORTH | 640305 | ONEILL 7 | 115 | 4.0412 | 4.0424 | 0.0012
GEN-2017-175 | 01 NORTH | 640306 | ONEILL 8 | 69 | 4.3897 | 4.3906 | 0.0009
GEN-2017-175 | 01 NORTH | 640343 | SHELCRK4 | 230 | 11.1675 | 11.1704 | 0.0029
GEN-2017-175 | 01 NORTH | 640349 | SPENCER7 | 115 | 4.738 | 4.7415 | 0.0035
GEN-2017-175 | 01 NORTH | 640386 | TWIN CH4 | 230 | 8.3012 | 8.3119 | 0.0107
GEN-2017-175 | 01 NORTH | 640387 | TWIN CH7 | 115 | 10.6377 | 10.6461 | 0.0084
GEN-2017-175 | 01 NORTH | 640388 | TWIN CH8 | 69 | 7.9529 | 7.9558 | 0.0029
GEN-2017-175 | 01 NORTH | 640424 | S.SIOUXCITY7 | 115 | 7.4133 | 7.4174 | 0.0041
GEN-2017-175 | 01 NORTH | 640425 | S.SIOUXCITY8 | 69 | 4.6475 | 4.6485 | 0.001
GEN-2017-175 | 01 NORTH | 640540 | MEADOWGROVE4 | 230 | 5.7655 | 5.7687 | 0.0032
GEN-2017-175 | 01 NORTH | 640560 | WAKEFIELD 4 | 230 | 6.4097 | 6.4143 | 0.0046
GEN-2017-175 | 01 NORTH | 640561 | RTLSNAKE.W 4 | 230 | 5.4653 | 5.4687 | 0.0034
GEN-2017-175 | 01 NORTH | 648506 | PR BRZ 4 | 230 | 4.3199 | 4.3211 | 0.0012
GEN-2017-175 | 01 NORTH | 652229 | FLANDRU8 | 69 | 3.5557 | 3.5562 | 0.0005
GEN-2017-175 | 01 NORTH | 652235 | SIOUXFL8 | 69 | 4.0786 | 4.0806 | 0.002
GEN-2017-175 | 01 NORTH | 652249 | ARMOUR 8 | 69 | 2.5558 | 2.5565 | 0.0007
GEN-2017-175 | 01 NORTH | 652251 | MTVERNS8 | 69 | 2.383 | 2.3834 | 0.0004
GEN-2017-175 | 01 NORTH | 652254 | BERSFRD8 | 69 | 3.3554 | 3.3564 | 0.001
GEN-2017-175 | 01 NORTH | 652276 | FTTHOMP8 | 69 | 4.6191 | 4.6193 | 0.0002
GEN-2017-175 | 01 NORTH | 652284 | HURON 8 | 69 | 3.8241 | 3.8243 | 0.0002
GEN-2017-175 | 01 NORTH | 652286 | TYNDALL8 | 69 | 2.6155 | 2.6171 | 0.0016
GEN-2017-175 | 01 NORTH | 652398 | VFODNES4 | 230 | 6.9757 | 7.209 | 0.2333
GEN-2017-175 | 01 NORTH | 652474 | AURORA 7 | 115 | 4.7441 | 4.7449 | 0.0008
GEN-2017-175 | 01 NORTH | 652475 | BONESTL7 | 115 | 3.6366 | 3.639 | 0.0024
GEN-2017-175 | 01 NORTH | 652478 | GREGORY7 | 115 | 2.2209 | 2.2215 | 0.0006
GEN-2017-175 | 01 NORTH | 652501 | ARMOUR 7 | 115 | 4.3508 | 4.354 | 0.0032
GEN-2017-175 | 01 NORTH | 652502 | BERSFRD7 | 115 | 4.0387 | 4.041 | 0.0023
GEN-2017-175 | 01 NORTH | 652505 | FLANDRU7 | 115 | 4.4843 | 4.4859 | 0.0016
GEN-2017-175 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 9.1833 | 9.1891 | 0.0058
GEN-2017-175 | 01 NORTH | 652507 | FTTHOMP4 | 230 | 20.2179 | 20.2458 | 0.0279
GEN-2017-175 | 01 NORTH | 652509 | FTRANDL4 | 230 | 11.0631 | 11.1403 | 0.0772
GEN-2017-175 | 01 NORTH | 652510 | FTRANDL7 | 115 | 12.8362 | 12.8738 | 0.0376
GEN-2017-175 | 01 NORTH | 652511 | GAVINS 7 | 115 | 9.3245 | 9.3545 | 0.03
GEN-2017-175 | 01 NORTH | 652513 | HANLON 4 | 230 | 5.7562 | 5.7775 | 0.0213
GEN-2017-175 | 01 NORTH | 652514 | HURON 4 | 230 | 11.5112 | 11.5157 | 0.0045
GEN-2017-175 | 01 NORTH | 652515 | HURON 7 | 115 | 15.6102 | 15.6155 | 0.0053
GEN-2017-175 | 01 NORTH | 652518 | MTVERN 7 | 115 | 4.6167 | 4.6189 | 0.0022
GEN-2017-175 | 01 NORTH | 652519 | OAHE 4 | 230 | 13.5635 | 13.5688 | 0.0053
GEN-2017-175 | 01 NORTH | 652520 | OAHE 7 | 115 | 11.2916 | 11.2929 | 0.0013
GEN-2017-175 | 01 NORTH | 652523 | SIOUXFL4 | 230 | 13.5605 | 13.728 | 0.1675
GEN-2017-175 | 01 NORTH | 652524 | SIOUXFL7 | 115 | 27.1289 | 27.2795 | 0.1506
GEN-2017-175 | 01 NORTH | 652525 | TYNDALL7 | 115 | 3.9469 | 3.953 | 0.0061
GEN-2017-175 | 01 NORTH | 652526 | UTICAJC4 | 230 | 8.1983 | 8.6204 | 0.4221
GEN-2017-175 | 01 NORTH | 652530 | WATERTN4 | 230 | 15.1581 | 15.1604 | 0.0023
GEN-2017-175 | 01 NORTH | 652540 | BIGBND14 | 230 | 12.2627 | 12.2716 | 0.0089
GEN-2017-175 | 01 NORTH | 652541 | BIGBND24 | 230 | 12.1812 | 12.1899 | 0.0087
GEN-2017-175 | 01 NORTH | 652552 | SIOUXCY2 | 230 | 20.0801 | 20.1693 | 0.0892
GEN-2017-175 | 01 NORTH | 652561 | DENISON5 | 161 | 6.241 | 6.2426 | 0.0016
GEN-2017-175 | 01 NORTH | 652563 | SPENCER5 | 161 | 9.9525 | 9.9539 | 0.0014
GEN-2017-175 | 01 NORTH | 652564 | SIOUXCY3 | 345 | 15.3208 | 15.3583 | 0.0375
GEN-2017-175 | 01 NORTH | 652565 | SIOUXCY4 | 230 | 20.0801 | 20.1693 | 0.0892
GEN-2017-175 | 01 NORTH | 652566 | SIOUXCY5 | 161 | 21.196 | 21.2374 | 0.0414
GEN-2017-175 | 01 NORTH | 652567 | DENISON4 | 230 | 5.116 | 5.1178 | 0.0018
GEN-2017-175 | 01 NORTH | 652574 | SIOUXCY8 | 69 | 19.1434 | 19.1561 | 0.0127
GEN-2017-175 | 01 NORTH | 652583 | DENISON8 | 69 | 12.3117 | 12.3141 | 0.0024
GEN-2017-175 | 01 NORTH | 652606 | LETCHER4 | 230 | 4.9157 | 4.9255 | 0.0098
GEN-2017-175 | 01 NORTH | 652607 | WESSINGTON 4 | 230 | 5.8846 | 5.8905 | 0.0059
GEN-2017-175 | 01 NORTH | 652609 | LETCHER7 | 115 | 6.2512 | 6.2597 | 0.0085
GEN-2017-175 | 01 NORTH | 652614 | CARPENTER 4 | 230 | 7.2238 | 7.2252 | 0.0014
GEN-2017-175 | 01 NORTH | 652626 | UTICAJC7 | 115 | 9.0697 | 9.1887 | 0.119
GEN-2017-175 | 01 NORTH | 652630 | WATERTNCAP 4 | 230 | 14.9785 | 14.9808 | 0.0023
GEN-2017-175 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 9.1183 | 9.1239 | 0.0056
GEN-2017-175 | 01 NORTH | 652807 | FTTHOM2-LNX3 | 345 | 9.1833 | 9.1891 | 0.0058
GEN-2017-175 | 01 NORTH | 654454 | PRVLNG13 | 115 | 4.4519 | 4.47 | 0.0181
GEN-2017-175 | 01 NORTH | 654455 | PRVLNG23 | 115 | 6.997 | 7.106 | 0.109
GEN-2017-175 | 01 NORTH | 654457 | PRVLNG16 | 230 | 8.1509 | 8.5676 | 0.4167
GEN-2017-175 | 01 NORTH | 655011 | SW101-ER8 | 69 | 2.5459 | 2.5467 | 0.0008
GEN-2017-175 | 01 NORTH | 655013 | MOS-EROS-ER8 | 69 | 2.4041 | 2.4048 | 0.0007
GEN-2017-175 | 01 NORTH | 655014 | MOS-NMAR-ER8 | 69 | 3.0784 | 3.0802 | 0.0018
GEN-2017-175 | 01 NORTH | 655015 | MOS-SALM-ER8 | 69 | 2.3749 | 2.3759 | 0.001
GEN-2017-175 | 01 NORTH | 655016 | MOS-SPNC-ER8 | 69 | 1.5452 | 1.5456 | 0.0004
GEN-2017-175 | 01 NORTH | 655018 | MOS-MDCY-ER8 | 69 | 1.7127 | 1.7133 | 0.0006
GEN-2017-175 | 01 NORTH | 655019 | SW124-ER8 | 69 | 2.7279 | 2.7293 | 0.0014
GEN-2017-175 | 01 NORTH | 655020 | SW130-ER8 | 69 | 4.1207 | 4.124 | 0.0033
GEN-2017-175 | 01 NORTH | 655021 | MOS-FLDT-ER8 | 69 | 1.3298 | 1.3298 | 0
GEN-2017-175 | 01 NORTH | 655022 | SW-SPENC-ER8 | 69 | 1.6403 | 1.6408 | 0.0005
GEN-2017-175 | 01 NORTH | 655023 | SW145-ER8 | 69 | 2.193 | 2.1939 | 0.0009
GEN-2017-175 | 01 NORTH | 655024 | SW-HOWAR-ER8 | 69 | 0.7657 | 0.7658 | 0.0001
GEN-2017-175 | 01 NORTH | 655025 | SW156-ER8 | 69 | 1.7358 | 1.7364 | 0.0006
GEN-2017-175 | 01 NORTH | 655026 | SW159-ER8 | 69 | 3.3072 | 3.3093 | 0.0021
GEN-2017-175 | 01 NORTH | 655027 | SW162-ER8 | 69 | 2.0203 | 2.0211 | 0.0008
GEN-2017-175 | 01 NORTH | 655028 | SW170-ER8 | 69 | 3.0927 | 3.0946 | 0.0019
GEN-2017-175 | 01 NORTH | 655029 | SW-FEDOR-ER8 | 69 | 1.0356 | 1.0358 | 0.0002
GEN-2017-175 | 01 NORTH | 655030 | MOS-HMPA-ER8 | 69 | 1.7861 | 1.7867 | 0.0006
GEN-2017-175 | 01 NORTH | 655031 | MOS-LTCH-ER8 | 69 | 1.5672 | 1.5674 | 0.0002
GEN-2017-175 | 01 NORTH | 655032 | MOS-PLNO-ER8 | 69 | 1.0248 | 1.0248 | 0
GEN-2017-175 | 01 NORTH | 655033 | SW-EMERY-ER8 | 69 | 0.8175 | 0.8175 | 0
GEN-2017-175 | 01 NORTH | 655036 | SW209-ER8 | 69 | 2.6311 | 2.6314 | 0.0003
GEN-2017-175 | 01 NORTH | 655037 | SW211-ER8 | 69 | 2.0787 | 2.0789 | 0.0002
GEN-2017-175 | 01 NORTH | 655042 | MADISON-ER8 | 69 | 1.4133 | 1.4133 | 0
GEN-2017-175 | 01 NORTH | 655043 | SW234-ER8 | 69 | 3.5457 | 3.5462 | 0.0005
GEN-2017-175 | 01 NORTH | 655048 | LAKECNTY-ER8 | 69 | 1.5182 | 1.5182 | 0
GEN-2017-175 | 01 NORTH | 655049 | MOS-CLMN-ER8 | 69 | 2.2834 | 2.2836 | 0.0002
GEN-2017-175 | 01 NORTH | 655052 | MAD SE-ER8 | 69 | 1.469 | 1.469 | 0
GEN-2017-175 | 01 NORTH | 655053 | MOS-MILR-ER8 | 69 | 2.4857 | 2.4858 | 0.0001
GEN-2017-175 | 01 NORTH | 655055 | SW-YALE-ER8 | 69 | 1.2326 | 1.2326 | 0
GEN-2017-175 | 01 NORTH | 655056 | SW-WILLO-ER8 | 69 | 1.6334 | 1.6334 | 0
GEN-2017-175 | 01 NORTH | 655058 | MOS-HRON-ER8 | 69 | 2.7566 | 2.7567 | 0.0001
GEN-2017-175 | 01 NORTH | 655060 | MOS-POLO-ER8 | 69 | 1.0183 | 1.0183 | 0
GEN-2017-175 | 01 NORTH | 655062 | MOS-YALE-ER8 | 69 | 1.4658 | 1.4658 | 0
GEN-2017-175 | 01 NORTH | 655063 | SW-HURN1-ER8 | 69 | 3.7688 | 3.769 | 0.0002
GEN-2017-175 | 01 NORTH | 655064 | SW-HURN4-ER8 | 69 | 3.7433 | 3.7435 | 0.0002
GEN-2017-175 | 01 NORTH | 655065 | MOS-YLTI-ER8 | 69 | 1.7046 | 1.7047 | 0.0001
GEN-2017-175 | 01 NORTH | 655066 | SW-HURN2-ER8 | 69 | 3.808 | 3.8082 | 0.0002
GEN-2017-175 | 01 NORTH | 655067 | SW-HURN3-ER8 | 69 | 3.812 | 3.8122 | 0.0002
GEN-2017-175 | 01 NORTH | 655069 | MOS-WOLS-ER8 | 69 | 2.2716 | 2.2717 | 0.0001
GEN-2017-175 | 01 NORTH | 655070 | MOS-VRCV-ER8 | 69 | 1.2527 | 1.2527 | 0
GEN-2017-175 | 01 NORTH | 655071 | MOS-DAK-ER8 | 69 | 1.0692 | 1.0692 | 0
GEN-2017-175 | 01 NORTH | 655073 | MOS-CRPN-ER8 | 69 | 2.5535 | 2.5535 | 0
GEN-2017-175 | 01 NORTH | 655074 | SW401-ER8 | 69 | 1.5439 | 1.544 | 0.0001
GEN-2017-175 | 01 NORTH | 655075 | MOS-WHTL-ER8 | 69 | 1.012 | 1.0121 | 0.0001
GEN-2017-175 | 01 NORTH | 655076 | MOS-PLAT-ER8 | 69 | 1.4992 | 1.4994 | 0.0002
GEN-2017-175 | 01 NORTH | 655077 | SW-STORL-ER8 | 69 | 1.8996 | 1.8999 | 0.0003
GEN-2017-175 | 01 NORTH | 655078 | SW412-ER8 | 69 | 0.8316 | 0.8316 | 0
GEN-2017-175 | 01 NORTH | 655079 | MOS-KLKP-ER8 | 69 | 0.806 | 0.8061 | 0.0001
GEN-2017-175 | 01 NORTH | 655080 | MOS-HLTP-ER8 | 69 | 1.3702 | 1.3703 | 0.0001
GEN-2017-175 | 01 NORTH | 655081 | MOS-KMBL-ER8 | 69 | 0.7459 | 0.7459 | 0
GEN-2017-175 | 01 NORTH | 655091 | MOS-AMR1-ER8 | 69 | 2.2626 | 2.2631 | 0.0005
GEN-2017-175 | 01 NORTH | 655092 | MOS-TRIP-ER8 | 69 | 2.1496 | 2.1507 | 0.0011
GEN-2017-175 | 01 NORTH | 655093 | SW-HARSN-ER8 | 69 | 1.089 | 1.0891 | 0.0001
GEN-2017-175 | 01 NORTH | 655094 | MOS-PRKS-ER8 | 69 | 1.5945 | 1.5947 | 0.0002
GEN-2017-175 | 01 NORTH | 655095 | MOS-TABR-ER8 | 69 | 1.8183 | 1.819 | 0.0007
GEN-2017-175 | 01 NORTH | 655096 | SW-TRIPP-ER8 | 69 | 1.2136 | 1.214 | 0.0004
GEN-2017-175 | 01 NORTH | 655097 | SW616-ER8 | 69 | 1.4673 | 1.4678 | 0.0005
GEN-2017-175 | 01 NORTH | 655098 | SW-GEDES-ER8 | 69 | 1.3715 | 1.3716 | 0.0001
GEN-2017-175 | 01 NORTH | 655099 | SW-HILLS-ER8 | 69 | 1.2547 | 1.2548 | 0.0001
GEN-2017-175 | 01 NORTH | 655100 | MOS-WVLN-ER8 | 69 | 1.3608 | 1.3613 | 0.0005
GEN-2017-175 | 01 NORTH | 655101 | MOS-TND1-ER8 | 69 | 2.6125 | 2.6141 | 0.0016
GEN-2017-175 | 01 NORTH | 655102 | MOS-AVON-ER8 | 69 | 2.6013 | 2.6028 | 0.0015
GEN-2017-175 | 01 NORTH | 655103 | PARKSTON-ER8 | 69 | 0.9812 | 0.9813 | 0.0001
GEN-2017-175 | 01 NORTH | 655104 | MOS-NTRP-ER8 | 69 | 1.2271 | 1.2275 | 0.0004
GEN-2017-175 | 01 NORTH | 655105 | MOS-HRLM-ER8 | 69 | 1.0716 | 1.0717 | 0.0001
GEN-2017-175 | 01 NORTH | 655106 | SW640-ER8 | 69 | 0.7922 | 0.7923 | 0.0001
GEN-2017-175 | 01 NORTH | 655126 | MOS-VERM-ER8 | 69 | 2.0205 | 2.0223 | 0.0018
GEN-2017-175 | 01 NORTH | 655127 | MOS-ALCS-ER8 | 69 | 3.1579 | 3.1587 | 0.0008
GEN-2017-175 | 01 NORTH | 655128 | SW804-ER8 | 69 | 2.1479 | 2.1483 | 0.0004
GEN-2017-175 | 01 NORTH | 655129 | SW806-ER8 | 69 | 0.8787 | 0.879 | 0.0003
GEN-2017-175 | 01 NORTH | 655130 | SW808-ER8 | 69 | 2.5391 | 2.5418 | 0.0027
GEN-2017-175 | 01 NORTH | 655131 | SW813-ER8 | 69 | 2.7394 | 2.74 | 0.0006
GEN-2017-175 | 01 NORTH | 655132 | MOS-VBRG-ER8 | 69 | 1.5822 | 1.5824 | 0.0002
GEN-2017-175 | 01 NORTH | 655133 | SW822-ER8 | 69 | 2.1944 | 2.1964 | 0.002
GEN-2017-175 | 01 NORTH | 655134 | SW825-ER8 | 69 | 1.3177 | 1.3178 | 0.0001
GEN-2017-175 | 01 NORTH | 655135 | SW829-ER8 | 69 | 1.9162 | 1.9165 | 0.0003
GEN-2017-175 | 01 NORTH | 655136 | SW832-ER8 | 69 | 2.6213 | 2.6243 | 0.003
GEN-2017-175 | 01 NORTH | 655137 | SW833-ER8 | 69 | 2.0932 | 2.0951 | 0.0019
GEN-2017-175 | 01 NORTH | 655138 | MOS-VOLN-ER8 | 69 | 1.5169 | 1.5171 | 0.0002
GEN-2017-175 | 01 NORTH | 655140 | MOS-EVLN-ER8 | 69 | 1.3877 | 1.3878 | 0.0001
GEN-2017-175 | 01 NORTH | 655141 | SW848-ER8 | 69 | 3.0605 | 3.0613 | 0.0008
GEN-2017-175 | 01 NORTH | 655142 | MOS-CNTN-ER8 | 69 | 1.8206 | 1.8209 | 0.0003
GEN-2017-175 | 01 NORTH | 655143 | MOS-PARK-ER8 | 69 | 1.6917 | 1.6922 | 0.0005
GEN-2017-175 | 01 NORTH | 655145 | SW870-ER8 | 69 | 2.8867 | 2.8903 | 0.0036
GEN-2017-175 | 01 NORTH | 655146 | SW873-ER8 | 69 | 2.8854 | 2.889 | 0.0036
GEN-2017-175 | 01 NORTH | 655147 | MOS-JEFF-ER8 | 69 | 2.5397 | 2.5425 | 0.0028
GEN-2017-175 | 01 NORTH | 655148 | SW879-ER8 | 69 | 1.0944 | 1.0944 | 0
GEN-2017-175 | 01 NORTH | 655150 | MOS-SPMD-ER8 | 69 | 2.3415 | 2.3418 | 0.0003
GEN-2017-175 | 01 NORTH | 655151 | MOS-BGSP-ER8 | 69 | 1.3643 | 1.3651 | 0.0008
GEN-2017-175 | 01 NORTH | 655152 | SW894-ER8 | 69 | 2.0662 | 2.068 | 0.0018
GEN-2017-175 | 01 NORTH | 655153 | MOS-AMES-ER8 | 69 | 4.557 | 4.5572 | 0.0002
GEN-2017-175 | 01 NORTH | 655155 | MOS-SLY1-ER8 | 69 | 2.4637 | 2.4637 | 0
GEN-2017-175 | 01 NORTH | 655158 | MOS-HYDE-ER8 | 69 | 3.6177 | 3.6178 | 0.0001
GEN-2017-175 | 01 NORTH | 655165 | MOS-INDM-ER8 | 69 | 1.4772 | 1.4776 | 0.0004
GEN-2017-175 | 01 NORTH | 655166 | SW1142-ER8 | 69 | 4.8241 | 4.8285 | 0.0044
GEN-2017-175 | 01 NORTH | 655167 | MOS-CRTI-ER7 | 115 | 7.883 | 7.8957 | 0.0127
GEN-2017-175 | 01 NORTH | 655169 | MOS-PRRI-ER8 | 69 | 2.29 | 2.2904 | 0.0004
GEN-2017-175 | 01 NORTH | 655180 | GARTSON-ER8 | 69 | 1.8501 | 1.8505 | 0.0004
GEN-2017-175 | 01 NORTH | 655181 | EROS-ER8 | 69 | 2.1821 | 2.1827 | 0.0006
GEN-2017-175 | 01 NORTH | 655182 | SALEM-ER8 | 69 | 2.3061 | 2.3071 | 0.001
GEN-2017-175 | 01 NORTH | 655183 | MITCHELL-ER8 | 69 | 1.2317 | 1.2318 | 0.0001
GEN-2017-175 | 01 NORTH | 655185 | GRNDMEAD-ER8 | 69 | 2.5994 | 2.6007 | 0.0013
GEN-2017-175 | 01 NORTH | 655186 | COLTON-ER8 | 69 | 2.1039 | 2.1048 | 0.0009
GEN-2017-175 | 01 NORTH | 655187 | MARION-ER8 | 69 | 1.3826 | 1.383 | 0.0004
GEN-2017-175 | 01 NORTH | 655188 | PARKERCI-ER8 | 69 | 1.6146 | 1.6151 | 0.0005
GEN-2017-175 | 01 NORTH | 655189 | FARMER-ER8 | 69 | 0.8352 | 0.8353 | 0.0001
GEN-2017-175 | 01 NORTH | 655190 | MONTROSE-ER8 | 69 | 3.9356 | 3.9385 | 0.0029
GEN-2017-175 | 01 NORTH | 655191 | TRENT-ER8 | 69 | 1.0475 | 1.0477 | 0.0002
GEN-2017-175 | 01 NORTH | 655192 | PARKER-ER8 | 69 | 1.7242 | 1.7247 | 0.0005
GEN-2017-175 | 01 NORTH | 655193 | MTVERNON-ER8 | 69 | 1.8874 | 1.8876 | 0.0002
GEN-2017-175 | 01 NORTH | 655194 | SPENCER-ER8 | 69 | 1.6156 | 1.6161 | 0.0005
GEN-2017-175 | 01 NORTH | 655195 | CHESTER-ER8 | 69 | 1.4787 | 1.4791 | 0.0004
GEN-2017-175 | 01 NORTH | 655196 | HOWARD-ER8 | 69 | 0.7475 | 0.7476 | 0.0001
GEN-2017-175 | 01 NORTH | 655197 | HOWARDCI-ER8 | 69 | 0.8259 | 0.8261 | 0.0002
GEN-2017-175 | 01 NORTH | 655198 | DOLTON-ER8 | 69 | 1.2734 | 1.2737 | 0.0003
GEN-2017-175 | 01 NORTH | 655199 | ORLAND-ER8 | 69 | 1.8322 | 1.8328 | 0.0006
GEN-2017-175 | 01 NORTH | 655200 | WBRANDON-ER7 | 115 | 13.9123 | 13.952 | 0.0397
GEN-2017-175 | 01 NORTH | 655201 | HUMBOLT-ER8 | 69 | 2.7589 | 2.7604 | 0.0015
GEN-2017-175 | 01 NORTH | 655202 | FEDORA-ER8 | 69 | 0.8757 | 0.8759 | 0.0002
GEN-2017-175 | 01 NORTH | 655203 | LYONS-ER8 | 69 | 1.9611 | 1.9618 | 0.0007
GEN-2017-175 | 01 NORTH | 655204 | SPLITRCK-ER7 | 115 | 4.4831 | 4.4871 | 0.004
GEN-2017-175 | 01 NORTH | 655205 | PLANO-ER8 | 69 | 0.8712 | 0.8713 | 0.0001
GEN-2017-175 | 01 NORTH | 655206 | EMERY-ER8 | 69 | 0.7289 | 0.729 | 0.0001
GEN-2017-175 | 01 NORTH | 655210 | EGAN-ER8 | 69 | 2.6224 | 2.6227 | 0.0003
GEN-2017-175 | 01 NORTH | 655211 | DESMET-ER8 | 69 | 1.0999 | 1.0999 | 0
GEN-2017-175 | 01 NORTH | 655216 | WARD-ER8 | 69 | 1.9273 | 1.9275 | 0.0002
GEN-2017-175 | 01 NORTH | 655221 | COLEMAN-ER8 | 69 | 1.9877 | 1.9878 | 0.0001
GEN-2017-175 | 01 NORTH | 655223 | WENTWRTH-ER8 | 69 | 1.8468 | 1.8469 | 0.0001
GEN-2017-175 | 01 NORTH | 655224 | RUTLAND-ER8 | 69 | 1.47 | 1.47 | 0
GEN-2017-175 | 01 NORTH | 655226 | MOS-LKV2-ER8 | 69 | 1.4322 | 1.4322 | 0
GEN-2017-175 | 01 NORTH | 655228 | YALE-ER8 | 69 | 1.2138 | 1.2138 | 0
GEN-2017-175 | 01 NORTH | 655229 | WILLOWLK-ER8 | 69 | 1.1938 | 1.1938 | 0
GEN-2017-175 | 01 NORTH | 655231 | HURON-ER8 | 69 | 2.7535 | 2.7536 | 0.0001
GEN-2017-175 | 01 NORTH | 655233 | POLO-ER8 | 69 | 0.6486 | 0.6487 | 0.0001
GEN-2017-175 | 01 NORTH | 655234 | MILLER-ER8 | 69 | 1.0262 | 1.0262 | 0
GEN-2017-175 | 01 NORTH | 655236 | MORNINGS-ER8 | 69 | 1.9501 | 1.9501 | 0
GEN-2017-175 | 01 NORTH | 655237 | BONILLA-ER8 | 69 | 1.677 | 1.6771 | 0.0001
GEN-2017-175 | 01 NORTH | 655239 | WOLSEY-ER8 | 69 | 1.3491 | 1.3491 | 0
GEN-2017-175 | 01 NORTH | 655240 | HGHMORE-ER8 | 69 | 2.2442 | 2.2442 | 0
GEN-2017-175 | 01 NORTH | 655241 | VIRGIL-ER8 | 69 | 1.8814 | 1.8815 | 0.0001
GEN-2017-175 | 01 NORTH | 655242 | CAVOUR-ER8 | 69 | 1.2043 | 1.2043 | 0
GEN-2017-175 | 01 NORTH | 655244 | DAKOTA-ER8 | 69 | 0.994 | 0.994 | 0
GEN-2017-175 | 01 NORTH | 655247 | PLANKCTY-ER8 | 69 | 1.5775 | 1.5777 | 0.0002
GEN-2017-175 | 01 NORTH | 655248 | STORLA-ER8 | 69 | 1.0753 | 1.0753 | 0
GEN-2017-175 | 01 NORTH | 655249 | WILBUR-ER8 | 69 | 0.8066 | 0.8066 | 0
GEN-2017-175 | 01 NORTH | 655250 | CHMBRLAN-ER8 | 69 | 1.6586 | 1.6588 | 0.0002
GEN-2017-175 | 01 NORTH | 655251 | PLATTE-ER8 | 69 | 2.1759 | 2.1763 | 0.0004
GEN-2017-175 | 01 NORTH | 655252 | RIVERVW-ER8 | 69 | 1.5256 | 1.5258 | 0.0002
GEN-2017-175 | 01 NORTH | 655253 | PUKWANA-ER8 | 69 | 1.1638 | 1.1639 | 0.0001
GEN-2017-175 | 01 NORTH | 655254 | HILLTOP-ER8 | 69 | 1.1671 | 1.1673 | 0.0002
GEN-2017-175 | 01 NORTH | 655255 | KIMBALL-ER8 | 69 | 0.6982 | 0.6982 | 0
GEN-2017-175 | 01 NORTH | 655271 | WAGNER-ER8 | 69 | 1.3158 | 1.3159 | 0.0001
GEN-2017-175 | 01 NORTH | 655272 | TYNDALL-ER8 | 69 | 2.6081 | 2.6097 | 0.0016
GEN-2017-175 | 01 NORTH | 655273 | ARMOUR-ER8 | 69 | 2.1632 | 2.1637 | 0.0005
GEN-2017-175 | 01 NORTH | 655274 | HARRISON-ER8 | 69 | 1.0767 | 1.0768 | 0.0001
GEN-2017-175 | 01 NORTH | 655275 | TABOR-ER8 | 69 | 1.5315 | 1.532 | 0.0005
GEN-2017-175 | 01 NORTH | 655276 | UTICA-ER8 | 69 | 1.1915 | 1.1918 | 0.0003
GEN-2017-175 | 01 NORTH | 655277 | GEDDES-ER8 | 69 | 0.9682 | 0.9683 | 0.0001
GEN-2017-175 | 01 NORTH | 655278 | HILLSIDE-ER8 | 69 | 1.2029 | 1.203 | 0.0001
GEN-2017-175 | 01 NORTH | 655279 | GAVINSPT-ER8 | 69 | 1.1325 | 1.1328 | 0.0003
GEN-2017-175 | 01 NORTH | 655280 | AVON-ER8 | 69 | 1.6508 | 1.6514 | 0.0006
GEN-2017-175 | 01 NORTH | 655281 | SPRNGFLD-ER8 | 69 | 1.7835 | 1.7842 | 0.0007
GEN-2017-175 | 01 NORTH | 655282 | TRIPP-ER8 | 69 | 1.1506 | 1.1509 | 0.0003
GEN-2017-175 | 01 NORTH | 655283 | MENNO-ER8 | 69 | 0.8821 | 0.8823 | 0.0002
GEN-2017-175 | 01 NORTH | 655284 | TRKYRDGE-ER8 | 69 | 0.7792 | 0.7794 | 0.0002
GEN-2017-175 | 01 NORTH | 655285 | BYWATER-ER8 | 69 | 1.2842 | 1.2846 | 0.0004
GEN-2017-175 | 01 NORTH | 655307 | FDAVIS-ER8 | 69 | 1.9205 | 1.9208 | 0.0003
GEN-2017-175 | 01 NORTH | 655308 | ALCESTER-ER8 | 69 | 1.0261 | 1.0266 | 0.0005
GEN-2017-175 | 01 NORTH | 655309 | VERMLLON-ER8 | 69 | 2.5549 | 2.5553 | 0.0004
GEN-2017-175 | 01 NORTH | 655310 | VOLIN-ER8 | 69 | 1.4981 | 1.4983 | 0.0002
GEN-2017-175 | 01 NORTH | 655311 | AKRON-ER8 | 69 | 1.5306 | 1.5316 | 0.001
GEN-2017-175 | 01 NORTH | 655312 | VIBORG-ER8 | 69 | 1.2959 | 1.296 | 0.0001
GEN-2017-175 | 01 NORTH | 655313 | RICHLAND-ER8 | 69 | 2.5307 | 2.5335 | 0.0028
GEN-2017-175 | 01 NORTH | 655314 | ELKPNTCY-ER8 | 69 | 1.9375 | 1.9392 | 0.0017
GEN-2017-175 | 01 NORTH | 655315 | ELKPOINT-ER8 | 69 | 1.9368 | 1.9384 | 0.0016
GEN-2017-175 | 01 NORTH | 655316 | BURBANK-ER8 | 69 | 1.8796 | 1.8811 | 0.0015
GEN-2017-175 | 01 NORTH | 655318 | IRENE-ER8 | 69 | 1.1442 | 1.1443 | 0.0001
GEN-2017-175 | 01 NORTH | 655319 | CNTRVILE-ER8 | 69 | 2.518 | 2.5185 | 0.0005
GEN-2017-175 | 01 NORTH | 655320 | CANTON-ER8 | 69 | 1.3791 | 1.3792 | 0.0001
GEN-2017-175 | 01 NORTH | 655321 | HURLEY-ER8 | 69 | 1.1259 | 1.126 | 0.0001
GEN-2017-175 | 01 NORTH | 655322 | TEA-ER8 | 69 | 1.408 | 1.4082 | 0.0002
GEN-2017-175 | 01 NORTH | 655324 | MISIONHI-ER8 | 69 | 1.0242 | 1.0243 | 0.0001
GEN-2017-175 | 01 NORTH | 655326 | BGSPRING-ER8 | 69 | 1.1806 | 1.1811 | 0.0005
GEN-2017-175 | 01 NORTH | 655327 | UNIONCRK-ER8 | 69 | 2.0005 | 2.0022 | 0.0017
GEN-2017-175 | 01 NORTH | 655328 | BIGBEND-ER8 | 69 | 3.3816 | 3.3818 | 0.0002
GEN-2017-175 | 01 NORTH | 655329 | GANNVALL-ER8 | 69 | 0.9053 | 0.9053 | 0
GEN-2017-175 | 01 NORTH | 655332 | LOGAN-ER8 | 69 | 1.1456 | 1.1456 | 0
GEN-2017-175 | 01 NORTH | 655333 | ONIDA-ER8 | 69 | 1.5822 | 1.5822 | 0
GEN-2017-175 | 01 NORTH | 655334 | OKOBOJO-ER8 | 69 | 2.4672 | 2.4672 | 0
GEN-2017-175 | 01 NORTH | 655346 | INDMARIN-ER8 | 69 | 1.3992 | 1.3995 | 0.0003
GEN-2017-175 | 01 NORTH | 655348 | CORSON-ER7 | 115 | 9.8859 | 9.9058 | 0.0199
GEN-2017-175 | 01 NORTH | 655349 | MOS-FMC-ER7 | 115 | 5.9497 | 5.9567 | 0.007
GEN-2017-175 | 01 NORTH | 655352 | AMES-ER8 | 69 | 1.4035 | 1.4036 | 0.0001
GEN-2017-175 | 01 NORTH | 655358 | PRARIEBE-ER8 | 69 | 1.9298 | 1.93 | 0.0002
GEN-2017-175 | 01 NORTH | 655359 | JEFERSON-ER8 | 69 | 1.6872 | 1.6885 | 0.0013
GEN-2017-175 | 01 NORTH | 655362 | LINCOLN-ER7 | 115 | 3.3043 | 3.33 | 0.0257
GEN-2017-175 | 01 NORTH | 655368 | VLLYSPRG-ER7 | 115 | 5.0039 | 5.009 | 0.0051
GEN-2017-175 | 01 NORTH | 655370 | IRENESUB-ER8 | 69 | 1.1439 | 1.144 | 0.0001
GEN-2017-175 | 01 NORTH | 655372 | LOGANSUB-ER8 | 69 | 1.145 | 1.145 | 0
GEN-2017-175 | 01 NORTH | 655373 | MOS-SLY2-ER8 | 69 | 2.4741 | 2.4741 | 0
GEN-2017-175 | 01 NORTH | 655374 | MOS-TND2-ER8 | 69 | 2.6119 | 2.6135 | 0.0016
GEN-2017-175 | 01 NORTH | 655375 | MOS-WGNR-ER8 | 69 | 1.3164 | 1.3165 | 0.0001
GEN-2017-175 | 01 NORTH | 655376 | MOS-AMR2-ER8 | 69 | 2.3458 | 2.3463 | 0.0005
GEN-2017-175 | 01 NORTH | 655377 | SW1145-ER7 | 115 | 25.8067 | 25.9431 | 0.1364
GEN-2017-175 | 01 NORTH | 655378 | NWPS3680-ER8 | 69 | 1.0436 | 1.0436 | 0
GEN-2017-175 | 01 NORTH | 655379 | AURORAIP-ER7 | 115 | 4.2176 | 4.2182 | 0.0006
GEN-2017-175 | 01 NORTH | 655384 | NWPS8645-ER8 | 69 | 2.284 | 2.284 | 0
GEN-2017-175 | 01 NORTH | 655385 | MOS-LKPL-ER8 | 69 | 4.1894 | 4.1909 | 0.0015
GEN-2017-175 | 01 NORTH | 655386 | MOS-RVR1-ER8 | 69 | 2.1871 | 2.1875 | 0.0004
GEN-2017-175 | 01 NORTH | 655387 | MOS-RVR2-ER8 | 69 | 2.1765 | 2.1769 | 0.0004
GEN-2017-175 | 01 NORTH | 655388 | NWPS7632-ER8 | 69 | 1.5716 | 1.5719 | 0.0003
GEN-2017-175 | 01 NORTH | 655390 | MOS-CLTN-ER8 | 69 | 2.1064 | 2.1072 | 0.0008
GEN-2017-175 | 01 NORTH | 655391 | MOS-CHST-ER8 | 69 | 1.4805 | 1.4809 | 0.0004
GEN-2017-175 | 01 NORTH | 655393 | SWR5123-ER8 | 69 | 0.9787 | 0.9791 | 0.0004
GEN-2017-175 | 01 NORTH | 655394 | SW425-ER8 | 69 | 1.3147 | 1.3148 | 0.0001
GEN-2017-175 | 01 NORTH | 655396 | SW144-ER8 | 69 | 1.855 | 1.8557 | 0.0007
GEN-2017-175 | 01 NORTH | 655397 | XLSW4X1-ER8 | 69 | 2.3605 | 2.3615 | 0.001
GEN-2017-175 | 01 NORTH | 655398 | XLSW4X16-ER8 | 69 | 1.3766 | 1.3768 | 0.0002
GEN-2017-175 | 01 NORTH | 655400 | BRANDON-ER7 | 115 | 11.1501 | 11.1756 | 0.0255
GEN-2017-175 | 01 NORTH | 655401 | ROWENA-ER7 | 115 | 6.4731 | 6.4815 | 0.0084
GEN-2017-175 | 01 NORTH | 655404 | HRRISBRG-ER7 | 115 | 3.3278 | 3.3538 | 0.026
GEN-2017-175 | 01 NORTH | 655405 | SHINDLER-ER7 | 115 | 2.8341 | 2.853 | 0.0189
GEN-2017-175 | 01 NORTH | 655406 | 6MILE RD-ER7 | 115 | 2.6546 | 2.6711 | 0.0165
GEN-2017-175 | 01 NORTH | 655407 | MOS-SPRK-ER7 | 115 | 4.6314 | 4.6357 | 0.0043
GEN-2017-175 | 01 NORTH | 655408 | SXFCHCLR-ER7 | 115 | 3.409 | 3.4361 | 0.0271
GEN-2017-175 | 01 NORTH | 655409 | MAPLE ST-ER7 | 115 | 13.0918 | 13.127 | 0.0352
GEN-2017-175 | 01 NORTH | 655410 | SYCAMORE-ER7 | 115 | 3.0456 | 3.0673 | 0.0217
GEN-2017-175 | 01 NORTH | 655412 | CRPNTR-ER8 | 69 | 2.9541 | 2.9541 | 0
GEN-2017-175 | 01 NORTH | 655413 | SW167 -ER7 | 115 | 14.3477 | 14.3899 | 0.0422
GEN-2017-175 | 01 NORTH | 655414 | SW1116 -ER7 | 115 | 11.866 | 11.8949 | 0.0289
GEN-2017-175 | 01 NORTH | 655417 | ROSWELL-ER7 | 115 | 2.7172 | 2.7188 | 0.0016
GEN-2017-175 | 01 NORTH | 655418 | FREEMAN-ER7 | 115 | 2.6767 | 2.6872 | 0.0105
GEN-2017-175 | 01 NORTH | 655423 | GREYGOOS-ER8 | 69 | 1.58 | 1.58 | 0
GEN-2017-175 | 01 NORTH | 655425 | MOS-BYWT-ER8 | 69 | 1.2842 | 1.2846 | 0.0004
GEN-2017-175 | 01 NORTH | 655426 | MOS-GVPT-ER8 | 69 | 1.2046 | 1.2049 | 0.0003
GEN-2017-175 | 01 NORTH | 655427 | MOS-ALC2-ER8 | 69 | 1.0261 | 1.0266 | 0.0005
GEN-2017-175 | 01 NORTH | 655428 | BIGSPRGS-ER8 | 69 | 1.1806 | 1.1811 | 0.0005
GEN-2017-175 | 01 NORTH | 655437 | LAMESA-ER7 | 115 | 2.0526 | 2.054 | 0.0014
GEN-2017-175 | 01 NORTH | 655438 | HARTFORD-ER7 | 115 | 2.42 | 2.4219 | 0.0019
GEN-2017-175 | 01 NORTH | 655439 | SXFALLS-ER7 | 115 | 3.3322 | 3.3581 | 0.0259
GEN-2017-175 | 01 NORTH | 655440 | MARIONRD-ER7 | 115 | 2.5424 | 2.5576 | 0.0152
GEN-2017-175 | 01 NORTH | 655441 | BUCKSNRT-ER7 | 115 | 3.9152 | 3.9512 | 0.036
GEN-2017-175 | 01 NORTH | 655444 | DELAPRE-ER7 | 115 | 3.618 | 3.6485 | 0.0305
GEN-2017-175 | 01 NORTH | 655445 | SUNDOWN-ER7 | 115 | 3.7276 | 3.7601 | 0.0325
GEN-2017-175 | 01 NORTH | 655446 | SW1109-ER7 | 115 | 3.7849 | 3.8183 | 0.0334
GEN-2017-175 | 01 NORTH | 655447 | WALLLK-ER7 | 115 | 1.9724 | 1.9737 | 0.0013
GEN-2017-175 | 01 NORTH | 655448 | WILOWCRK-ER7 | 115 | 3.4388 | 3.4664 | 0.0276
GEN-2017-175 | 01 NORTH | 655449 | HARTSE-ER7 | 115 | 2.3204 | 2.3222 | 0.0018
GEN-2017-175 | 01 NORTH | 655450 | MOS-ELIS-ER7 | 115 | 3.0646 | 3.0866 | 0.022
GEN-2017-175 | 01 NORTH | 655451 | SW102-ER7 | 115 | 2.9842 | 2.987 | 0.0028
GEN-2017-175 | 01 NORTH | 655452 | MOS-MRRD-ER7 | 115 | 2.8838 | 2.9033 | 0.0195
GEN-2017-175 | 01 NORTH | 655453 | MOS-LAME-ER7 | 115 | 2.1961 | 2.1976 | 0.0015
GEN-2017-175 | 01 NORTH | 655468 | VFODNES-ER7 | 115 | 5.1131 | 5.1739 | 0.0608
GEN-2017-175 | 01 NORTH | 655469 | VFODNES-ER8 | 69 | 4.3678 | 4.3942 | 0.0264
GEN-2017-175 | 01 NORTH | 655475 | LAKPLAT-ER4 | 230 | 5.8062 | 5.8157 | 0.0095
GEN-2017-175 | 01 NORTH | 655476 | LAKPLAT-ER8 | 69 | 4.2046 | 4.2061 | 0.0015
GEN-2017-175 | 01 NORTH | 655478 | MANNING-ER7 | 115 | 5.1924 | 5.1954 | 0.003
GEN-2017-175 | 01 NORTH | 655479 | MANNING-ER8 | 69 | 2.8723 | 2.8729 | 0.0006
GEN-2017-175 | 01 NORTH | 655484 | RASMUSN-ER4 | 230 | 6.8847 | 6.9537 | 0.069
GEN-2017-175 | 01 NORTH | 655485 | RASMUSN-ER8 | 69 | 3.3159 | 3.3206 | 0.0047
GEN-2017-175 | 01 NORTH | 655487 | SULLYBT-ER4 | 230 | 6.3733 | 6.3742 | 0.0009
GEN-2017-175 | 01 NORTH | 655488 | SULLYBT-ER8 | 69 | 2.4779 | 2.4779 | 0
GEN-2017-175 | 01 NORTH | 655490 | WHTSWAN-ER7 | 115 | 12.5211 | 12.5571 | 0.036
GEN-2017-175 | 01 NORTH | 655493 | HANLON-ER7 | 115 | 4.0173 | 4.0224 | 0.0051
GEN-2017-175 | 01 NORTH | 655494 | HANLON1-ER8 | 69 | 5.3743 | 5.3798 | 0.0055
GEN-2017-175 | 01 NORTH | 655495 | HANLON2-ER8 | 69 | 5.3743 | 5.3798 | 0.0055
GEN-2017-175 | 01 NORTH | 655499 | CARPENTR-ER8 | 69 | 3.3311 | 3.3312 | 0.0001
GEN-2017-175 | 01 NORTH | 655504 | YANKTON-ER8 | 69 | 1.258 | 1.2584 | 0.0004
GEN-2017-175 | 01 NORTH | 655505 | SW660-ER8 | 69 | 1.3055 | 1.3059 | 0.0004
GEN-2017-175 | 01 NORTH | 655506 | SXFALLS2-ER7 | 115 | 3.4778 | 3.5062 | 0.0284
GEN-2017-175 | 01 NORTH | 655509 | SW-MILRC-ER8 | 69 | 1.0555 | 1.0555 | 0
GEN-2017-175 | 01 NORTH | 655517 | WORTHING-ER8 | 69 | 1.5883 | 1.5885 | 0.0002
GEN-2017-175 | 01 NORTH | 655518 | DAYTON__-ER7 | 115 | 3.581 | 3.6111 | 0.0301
GEN-2017-175 | 01 NORTH | 658030 | DENISONWEST8 | 69 | 6.9487 | 6.9495 | 0.0008
GEN-2017-175 | 01 NORTH | 658031 | DENSOUMAIN8 | 69 | 7.1182 | 7.119 | 0.0008
GEN-2017-175 | 01 NORTH | 658122 | ROCKRPDMUNI8 | 69 | 2.8442 | 2.8458 | 0.0016
GEN-2017-175 | 01 NORTH | 658124 | LUVERNEMUNW8 | 69 | 1.8249 | 1.8256 | 0.0007
GEN-2017-175 | 01 NORTH | 658126 | LUVERNEMUNE8 | 69 | 1.7278 | 1.7284 | 0.0006
GEN-2017-175 | 01 NORTH | 658128 | LUVERNEMUNS8 | 69 | 1.8306 | 1.8313 | 0.0007
GEN-2017-175 | 01 NORTH | 659122 | STORLA__-BE4 | 230 | 5.5698 | 5.5766 | 0.0068
GEN-2017-175 | 01 NORTH | 659123 | STORLA__-BE7 | 115 | 6.7863 | 6.7904 | 0.0041
GEN-2017-175 | 01 NORTH | 659188 | PHILIP_T-BE4 | 230 | 5.6157 | 5.616 | 0.0003
GEN-2017-175 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.4407 | 10.4442 | 0.0035
GEN-2017-175 | 01 NORTH | 659295 | SD.PW1__-BE4 | 230 | 4.5791 | 4.5825 | 0.0034
GEN-2017-175 | 01 NORTH | 659311 | PAHOJA__-BE4 | 230 | 7.6032 | 7.6408 | 0.0376
GEN-2017-175 | 01 NORTH | 659708 | LITLRCKT-LO8 | 69 | 1.9718 | 1.9726 | 0.0008
GEN-2017-175 | 01 NORTH | 659709 | LITLRCK -LO8 | 69 | 1.9309 | 1.9316 | 0.0007
GEN-2017-175 | 01 NORTH | 659710 | GEORGETP-LO8 | 69 | 2.3886 | 2.3897 | 0.0011
GEN-2017-175 | 01 NORTH | 659711 | GEORGE -LO8 | 69 | 2.3269 | 2.3279 | 0.001
GEN-2017-175 | 01 NORTH | 659712 | RKRMUNTP-LO8 | 69 | 3.3874 | 3.3897 | 0.0023
GEN-2017-175 | 01 NORTH | 659714 | RKRPDTAP-LO8 | 69 | 3.6017 | 3.6042 | 0.0025
GEN-2017-175 | 01 NORTH | 659715 | ROCKRPDS-LO8 | 69 | 3.4456 | 3.4479 | 0.0023
GEN-2017-175 | 01 NORTH | 659716 | MAPLETAP-LO7 | 115 | 13.1366 | 13.172 | 0.0354
GEN-2017-175 | 01 NORTH | 659717 | STATELIN-LO7 | 115 | 3.9883 | 3.9914 | 0.0031
GEN-2017-175 | 01 NORTH | 659718 | LRCHWDTP-LO7 | 115 | 3.163 | 3.165 | 0.002
GEN-2017-175 | 01 NORTH | 659719 | LARCHW0D-LO7 | 115 | 3.0945 | 3.0964 | 0.0019
GEN-2017-175 | 01 NORTH | 659720 | WESTLYON-LO7 | 115 | 2.5717 | 2.573 | 0.0013
GEN-2017-175 | 01 NORTH | 659721 | LESTERSS-LO7 | 115 | 2.1828 | 2.1838 | 0.001
GEN-2017-175 | 01 NORTH | 659722 | LESTERSS-LO8 | 69 | 2.2102 | 2.2108 | 0.0006
GEN-2017-175 | 01 NORTH | 659724 | LESTER -LO8 | 69 | 2.157 | 2.1576 | 0.0006
GEN-2017-175 | 01 NORTH | 659726 | STEEN -LO8 | 69 | 2.3465 | 2.3476 | 0.0011
GEN-2017-175 | 01 NORTH | 659727 | LUVERNE -LO8 | 69 | 1.8639 | 1.8646 | 0.0007
GEN-2017-175 | 01 NORTH | 659729 | HARDWICK-LO8 | 69 | 1.1281 | 1.1282 | 0.0001
GEN-2017-175 | 01 NORTH | 659730 | TROSKY -LO8 | 69 | 1.3532 | 1.3533 | 0.0001
GEN-2017-175 | 01 NORTH | 659731 | PIPESTON-LO8 | 69 | 1.715 | 1.7151 | 0.0001
GEN-2017-175 | 01 NORTH | 659732 | HOLLAND -LO8 | 69 | 2.4333 | 2.4335 | 0.0002
GEN-2017-175 | 01 NORTH | 659733 | HOLLAND -LO7 | 115 | 2.1591 | 2.1595 | 0.0004
GEN-2017-175 | 01 NORTH | 659735 | CLEVELND-LO4 | 230 | 5.0833 | 5.1 | 0.0167
GEN-2017-175 | 01 NORTH | 659736 | CLEVELND-LO8 | 69 | 4.4407 | 4.4445 | 0.0038
GEN-2017-175 | 01 NORTH | 659900 | EAGLE___-NI4 | 230 | 7.4595 | 7.4823 | 0.0228
GEN-2017-175 | 01 NORTH | 659901 | EAGLE___-NI8 | 69 | 14.3555 | 14.3767 | 0.0212
GEN-2017-175 | 01 NORTH | 660004 | MITCHELL 7 | 115 | 5.9762 | 5.9846 | 0.0084
GEN-2017-175 | 01 NORTH | 660005 | TRIPP JCT 7 | 115 | 4.1353 | 4.1481 | 0.0128
GEN-2017-175 | 01 NORTH | 660006 | YANKTON JCT7 | 115 | 8.7345 | 8.7739 | 0.0394
GEN-2017-175 | 01 NORTH | 660007 | MENNO JCT 7 | 115 | 6.7537 | 6.8134 | 0.0597
GEN-2017-175 | 01 NORTH | 660018 | SCHROEDER 7 | 115 | 3.4179 | 3.4261 | 0.0082
GEN-2017-175 | 01 NORTH | 660026 | NAPA JCT 7 | 115 | 8.2722 | 8.3161 | 0.0439
GEN-2017-175 | 01 NORTH | 660036 | YANKTONEAST7 | 115 | 4.2003 | 4.2116 | 0.0113
GEN-2017-175 | 01 NORTH | 660057 | AURORA CY T | 69 | 2.4506 | 2.4507 | 0.0001
GEN-2017-175 | 01 NORTH | 660067 | BRULE CY T | 69 | 2.1214 | 2.1215 | 0.0001
GEN-2017-175 | 01 NORTH | 660230 | STICKNEY JCT | 69 | 2.7532 | 2.7535 | 0.0003
GEN-2017-175 | 01 NORTH | 660231 | MT.VERNON T | 69 | 3.1693 | 3.1697 | 0.0004
GEN-2017-175 | 01 NORTH | 660232 | MT.VERNON | 69 | 2.8376 | 2.838 | 0.0004
GEN-2017-175 | 01 NORTH | 660233 | WHITE LAKE | 69 | 2.4414 | 2.4415 | 0.0001
GEN-2017-175 | 01 NORTH | 660234 | KIMBALL | 69 | 1.8639 | 1.864 | 0.0001
GEN-2017-175 | 01 NORTH | 660236 | CHB MO.VIEWT | 69 | 1.0701 | 1.0701 | 0
GEN-2017-175 | 01 NORTH | 660237 | CHB MO.VIEW | 69 | 1.0646 | 1.0646 | 0
GEN-2017-175 | 01 NORTH | 660238 | CHB CITY | 69 | 1.043 | 1.043 | 0
GEN-2017-175 | 01 NORTH | 660252 | MT VERNON 8 | 69 | 3.4157 | 3.4162 | 0.0005
GEN-2017-175 | 01 NORTH | 760515 | GEN-2017-222 | 230 | 3.7152 | 3.7161 | 0.0009
GEN-2017-175 | 01 NORTH | 762237 | G17-175TAP | 230 | 6.4262 | 7.0916 | 0.6654
GEN-2017-175 | 01 NORTH | 762238 | GEN-2017-175 | 230 | 6.2111 | 6.8789 | 0.6678
GEN-2017-214 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.6278 | 7.6319 | 0.0041
GEN-2017-214 | 01 NORTH | 587050 | GEN-2016-007 | 115 | 4.1176 | 4.1177 | 0.0001
GEN-2017-214 | 01 NORTH | 587720 | GEN-2016-087 | 230 | 4.0525 | 4.0526 | 0.0001
GEN-2017-214 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 12.7653 | 12.7766 | 0.0113
GEN-2017-214 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 4.6388 | 4.6413 | 0.0025
GEN-2017-214 | 01 NORTH | 602006 | SHEYNNE4 | 230 | 11.0546 | 11.0548 | 0.0002
GEN-2017-214 | 01 NORTH | 602052 | MAGIC CITY 4 | 230 | 4.4696 | 4.4739 | 0.0043
GEN-2017-214 | 01 NORTH | 603022 | SOURIS 7 | 115 | 9.0411 | 9.0768 | 0.0357
GEN-2017-214 | 01 NORTH | 603023 | MALLARD7 | 115 | 11.2768 | 11.3574 | 0.0806
GEN-2017-214 | 01 NORTH | 603270 | MAGIC CITY 7 | 115 | 9.1803 | 9.1995 | 0.0192
GEN-2017-214 | 01 NORTH | 605634 | VELVA TAP | 115 | 8.2663 | 8.2781 | 0.0118
GEN-2017-214 | 01 NORTH | 608597 | SQBP1DC4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-214 | 01 NORTH | 608599 | SQBP2DC4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-214 | 01 NORTH | 608600 | BISONMP4 | 230 | 8.0987 | 8.0989 | 0.0002
GEN-2017-214 | 01 NORTH | 608602 | SQBEAST4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-214 | 01 NORTH | 608603 | TRICNTY4 | 230 | 5.8686 | 5.8687 | 0.0001
GEN-2017-214 | 01 NORTH | 615145 | NEW FRONT W | 115 | 4.6101 | 4.6124 | 0.0023
GEN-2017-214 | 01 NORTH | 615347 | GRE-MCHENRY4 | 230 | 6.5247 | 6.5299 | 0.0052
GEN-2017-214 | 01 NORTH | 615348 | GRE-MCHENRY7 | 115 | 8.6371 | 8.6465 | 0.0094
GEN-2017-214 | 01 NORTH | 615600 | GRE-COAL CR4 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-214 | 01 NORTH | 615601 | GRE-COAL FM8 | 69 | 9.0417 | 9.042 | 0.0003
GEN-2017-214 | 01 NORTH | 615604 | GRE-COALFB14 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-214 | 01 NORTH | 615605 | GRE-COALFB24 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-214 | 01 NORTH | 615606 | GRE-COALFB34 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-214 | 01 NORTH | 615900 | GRE-COAL TP4 | 230 | 16.1372 | 16.1415 | 0.0043
GEN-2017-214 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.0179 | 18.0226 | 0.0047
GEN-2017-214 | 01 NORTH | 615903 | GRE-BALTA 4 | 230 | 6.6895 | 6.6927 | 0.0032
GEN-2017-214 | 01 NORTH | 615904 | GRE-BALTACB4 | 230 | 6.6895 | 6.6927 | 0.0032
GEN-2017-214 | 01 NORTH | 620276 | NHARVEY7 | 115 | 3.2677 | 3.268 | 0.0003
GEN-2017-214 | 01 NORTH | 620277 | SELZ 7 | 115 | 1.6645 | 1.6647 | 0.0002
GEN-2017-214 | 01 NORTH | 620278 | ESMDOTP7 | 115 | 2.3918 | 2.3922 | 0.0004
GEN-2017-214 | 01 NORTH | 620290 | HARVEY 4 | 230 | 5.0626 | 5.064 | 0.0014
GEN-2017-214 | 01 NORTH | 620368 | RGBYWND4 | 230 | 4.7915 | 4.7931 | 0.0016
GEN-2017-214 | 01 NORTH | 620369 | JAMESTN3 | 345 | 5.7007 | 5.7008 | 0.0001
GEN-2017-214 | 01 NORTH | 620379 | RUGBY 4 | 230 | 5.9509 | 5.9537 | 0.0028
GEN-2017-214 | 01 NORTH | 620381 | UNDERWD4 | 230 | 15.1013 | 15.1042 | 0.0029
GEN-2017-214 | 01 NORTH | 652204 | VALLEYC8 | 69 | 2.6481 | 2.6481 | 0
GEN-2017-214 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.8255 | 6.8268 | 0.0013
GEN-2017-214 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1039 | 1.104 | 0.0001
GEN-2017-214 | 01 NORTH | 652296 | WARD 4 | 230 | 14.4965 | 14.4988 | 0.0023
GEN-2017-214 | 01 NORTH | 652391 | WILLISTON27 | 115 | 18.677 | 18.6835 | 0.0065
GEN-2017-214 | 01 NORTH | 652400 | WILISTN4 | 230 | 11.3969 | 11.4032 | 0.0063
GEN-2017-214 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.6762 | 8.677 | 0.0008
GEN-2017-214 | 01 NORTH | 652421 | WILISTN7 | 115 | 18.669 | 18.6755 | 0.0065
GEN-2017-214 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.81 | 6.8111 | 0.0011
GEN-2017-214 | 01 NORTH | 652426 | BISMARK4 | 230 | 14.6065 | 14.6095 | 0.003
GEN-2017-214 | 01 NORTH | 652427 | BISMARK7 | 115 | 16.2245 | 16.226 | 0.0015
GEN-2017-214 | 01 NORTH | 652428 | CARNGTN7 | 115 | 2.7238 | 2.7239 | 0.0001
GEN-2017-214 | 01 NORTH | 652432 | EDGELEY7 | 115 | 4.2185 | 4.2185 | 0
GEN-2017-214 | 01 NORTH | 652435 | FARGO 4 | 230 | 10.2287 | 10.2289 | 0.0002
GEN-2017-214 | 01 NORTH | 652436 | FARGO 7 | 115 | 11.2495 | 11.2497 | 0.0002
GEN-2017-214 | 01 NORTH | 652437 | GRNDFKS4 | 230 | 7.0646 | 7.0649 | 0.0003
GEN-2017-214 | 01 NORTH | 652440 | NELSON 7 | 115 | 7.4474 | 7.4694 | 0.022
GEN-2017-214 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.2322 | 12.2384 | 0.0062
GEN-2017-214 | 01 NORTH | 652442 | GARRISN7 | 115 | 15.6788 | 15.6888 | 0.01
GEN-2017-214 | 01 NORTH | 652444 | JAMESTN4 | 230 | 8.631 | 8.6316 | 0.0006
GEN-2017-214 | 01 NORTH | 652445 | JAMESTN7 | 115 | 10.4229 | 10.4233 | 0.0004
GEN-2017-214 | 01 NORTH | 652446 | PLEASANT LK7 | 115 | 6.0482 | 6.0509 | 0.0027
GEN-2017-214 | 01 NORTH | 652447 | LEEDS 7 | 115 | 3.997 | 3.9978 | 0.0008
GEN-2017-214 | 01 NORTH | 652452 | RUGBY 7 | 115 | 8.2656 | 8.2711 | 0.0055
GEN-2017-214 | 01 NORTH | 652453 | TOWNER 7 | 115 | 4.7955 | 4.7985 | 0.003
GEN-2017-214 | 01 NORTH | 652454 | VALLEYC7 | 115 | 4.5544 | 4.5545 | 0.0001
GEN-2017-214 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.6888 | 10.6952 | 0.0064
GEN-2017-214 | 01 NORTH | 652464 | DENBIGH TAP7 | 115 | 4.6187 | 4.6215 | 0.0028
GEN-2017-214 | 01 NORTH | 652466 | HILKEN 4 | 230 | 7.6536 | 7.6549 | 0.0013
GEN-2017-214 | 01 NORTH | 652496 | WINCHESTER4 | 230 | 4.5613 | 4.5614 | 0.0001
GEN-2017-214 | 01 NORTH | 652499 | CAMPBELL 4 | 230 | 4.0525 | 4.0526 | 0.0001
GEN-2017-214 | 01 NORTH | 652590 | SNAKECR7 | 115 | 5.8316 | 5.8334 | 0.0018
GEN-2017-214 | 01 NORTH | 655609 | ROLETTE_-CP7 | 115 | 2.7853 | 2.786 | 0.0007
GEN-2017-214 | 01 NORTH | 655612 | HARVEY -CP7 | 115 | 3.8409 | 3.8413 | 0.0004
GEN-2017-214 | 01 NORTH | 655633 | NPESMOND-CP8 | 69 | 1.2695 | 1.2695 | 0
GEN-2017-214 | 01 NORTH | 655638 | ESMOND -CP7 | 115 | 2.0373 | 2.0377 | 0.0004
GEN-2017-214 | 01 NORTH | 655640 | ESMOND -CP8 | 69 | 1.5115 | 1.5116 | 0.0001
GEN-2017-214 | 01 NORTH | 655641 | BERTHOLD-CP7 | 115 | 6.3887 | 6.4051 | 0.0164
GEN-2017-214 | 01 NORTH | 655643 | VOLTAIR -CP7 | 115 | 8.5744 | 8.5836 | 0.0092
GEN-2017-214 | 01 NORTH | 655647 | WARD -CP7 | 115 | 8.3606 | 8.361 | 0.0004
GEN-2017-214 | 01 NORTH | 655650 | BOTINU.W-CP7 | 115 | 2.5858 | 2.5877 | 0.0019
GEN-2017-214 | 01 NORTH | 655651 | BOTNU.SE-CP7 | 115 | 2.6765 | 2.6783 | 0.0018
GEN-2017-214 | 01 NORTH | 655652 | E.BISMRK-CP7 | 115 | 15.7587 | 15.7601 | 0.0014
GEN-2017-214 | 01 NORTH | 655654 | RUGBY -CP7 | 115 | 8.2272 | 8.2327 | 0.0055
GEN-2017-214 | 01 NORTH | 655655 | E.RUTHVL-CP7 | 115 | 6.7955 | 6.8247 | 0.0292
GEN-2017-214 | 01 NORTH | 655656 | DUNNING -CP7 | 115 | 2.7438 | 2.7469 | 0.0031
GEN-2017-214 | 01 NORTH | 655657 | SW.MINOT-CP7 | 115 | 8.1371 | 8.188 | 0.0509
GEN-2017-214 | 01 NORTH | 655658 | RUTHVILL-CP7 | 115 | 6.3106 | 6.3358 | 0.0252
GEN-2017-214 | 01 NORTH | 655659 | BOTTINEU-CP7 | 115 | 2.5608 | 2.5625 | 0.0017
GEN-2017-214 | 01 NORTH | 655660 | RUGBY_RB-CP7 | 115 | 8.5814 | 8.5866 | 0.0052
GEN-2017-214 | 01 NORTH | 655661 | DOUGLS.C-CP7 | 115 | 4.1068 | 4.1079 | 0.0011
GEN-2017-214 | 01 NORTH | 655664 | MAKOTI -CP7 | 115 | 6.0167 | 6.0207 | 0.004
GEN-2017-214 | 01 NORTH | 655665 | RUGBY TP-CP7 | 115 | 8.2656 | 8.2711 | 0.0055
GEN-2017-214 | 01 NORTH | 655676 | HARAM -CP7 | 115 | 2.0732 | 2.0744 | 0.0012
GEN-2017-214 | 01 NORTH | 655690 | MAX_____-CP7 | 115 | 6.1588 | 6.1667 | 0.0079
GEN-2017-214 | 01 NORTH | 655693 | WARD_SPR-CP7 | 115 | 3.1355 | 3.1355 | 0
GEN-2017-214 | 01 NORTH | 655696 | ESMOND J-CP7 | 115 | 2.0652 | 2.0655 | 0.0003
GEN-2017-214 | 01 NORTH | 655701 | ROLETTE__CP8 | 69 | 2.7019 | 2.7023 | 0.0004
GEN-2017-214 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9756 | 0.9756 | 0
GEN-2017-214 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9027 | 0.9027 | 0
GEN-2017-214 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9095 | 0.9095 | 0
GEN-2017-214 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6894 | 0.6894 | 0
GEN-2017-214 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6176 | 0.6177 | 0.0001
GEN-2017-214 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1102 | 1.1102 | 0
GEN-2017-214 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1161 | 1.1161 | 0
GEN-2017-214 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.107 | 1.1071 | 0.0001
GEN-2017-214 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5133 | 1.5134 | 0.0001
GEN-2017-214 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.023 | 1.023 | 0
GEN-2017-214 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9904 | 0.9905 | 0.0001
GEN-2017-214 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9909 | 0.9909 | 0
GEN-2017-214 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5509 | 1.551 | 0.0001
GEN-2017-214 | 01 NORTH | 655780 | NORMANLK-BD7 | 115 | 3.2045 | 3.2051 | 0.0006
GEN-2017-214 | 01 NORTH | 655781 | LARSON -BD7 | 115 | 2.2089 | 2.2092 | 0.0003
GEN-2017-214 | 01 NORTH | 655782 | LIGNIBRD-BD7 | 115 | 1.5468 | 1.5469 | 0.0001
GEN-2017-214 | 01 NORTH | 655783 | HAWKEYE -BD7 | 115 | 1.4765 | 1.4766 | 0.0001
GEN-2017-214 | 01 NORTH | 655784 | AMBROSE -BD7 | 115 | 1.2492 | 1.2493 | 0.0001
GEN-2017-214 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.0081 | 6.0088 | 0.0007
GEN-2017-214 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.1866 | 4.1868 | 0.0002
GEN-2017-214 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0571 | 4.0573 | 0.0002
GEN-2017-214 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 7.9647 | 7.9655 | 0.0008
GEN-2017-214 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.0782 | 14.0803 | 0.0021
GEN-2017-214 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.9353 | 6.9358 | 0.0005
GEN-2017-214 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.126 | 3.1261 | 0.0001
GEN-2017-214 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.5486 | 5.549 | 0.0004
GEN-2017-214 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.6574 | 3.6576 | 0.0002
GEN-2017-214 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.065 | 4.0652 | 0.0002
GEN-2017-214 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.6762 | 8.677 | 0.0008
GEN-2017-214 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.7218 | 6.7221 | 0.0003
GEN-2017-214 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2677 | 3.2678 | 0.0001
GEN-2017-214 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.2411 | 5.2414 | 0.0003
GEN-2017-214 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.6474 | 4.6476 | 0.0002
GEN-2017-214 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.1671 | 4.1673 | 0.0002
GEN-2017-214 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3155 | 4.3158 | 0.0003
GEN-2017-214 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.7291 | 5.7295 | 0.0004
GEN-2017-214 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 9.7975 | 9.7988 | 0.0013
GEN-2017-214 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.4694 | 3.4696 | 0.0002
GEN-2017-214 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9166 | 2.9167 | 0.0001
GEN-2017-214 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5693 | 3.5694 | 0.0001
GEN-2017-214 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.3805 | 8.3814 | 0.0009
GEN-2017-214 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5245 | 3.5247 | 0.0002
GEN-2017-214 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.7883 | 4.7886 | 0.0003
GEN-2017-214 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.4975 | 6.498 | 0.0005
GEN-2017-214 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.5887 | 2.5888 | 0.0001
GEN-2017-214 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3474 | 4.3476 | 0.0002
GEN-2017-214 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.735 | 3.7352 | 0.0002
GEN-2017-214 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3191 | 2.3192 | 0.0001
GEN-2017-214 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1297 | 3.1298 | 0.0001
GEN-2017-214 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.7428 | 5.7433 | 0.0005
GEN-2017-214 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.8895 | 5.89 | 0.0005
GEN-2017-214 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.065 | 4.0652 | 0.0002
GEN-2017-214 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.989 | 2.9892 | 0.0002
GEN-2017-214 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7557 | 2.7558 | 0.0001
GEN-2017-214 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6554 | 2.6555 | 0.0001
GEN-2017-214 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9184 | 3.9186 | 0.0002
GEN-2017-214 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.532 | 4.5323 | 0.0003
GEN-2017-214 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 6.9468 | 6.9475 | 0.0007
GEN-2017-214 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.3452 | 6.3457 | 0.0005
GEN-2017-214 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.5956 | 7.5962 | 0.0006
GEN-2017-214 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.3443 | 8.345 | 0.0007
GEN-2017-214 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.2478 | 5.2481 | 0.0003
GEN-2017-214 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9133 | 3.9135 | 0.0002
GEN-2017-214 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.683 | 4.6832 | 0.0002
GEN-2017-214 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.7617 | 5.7622 | 0.0005
GEN-2017-214 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.0374 | 13.0397 | 0.0023
GEN-2017-214 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 9.8467 | 9.848 | 0.0013
GEN-2017-214 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.764 | 7.7648 | 0.0008
GEN-2017-214 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.4286 | 5.429 | 0.0004
GEN-2017-214 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2383 | 4.2386 | 0.0003
GEN-2017-214 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.0475 | 5.0479 | 0.0004
GEN-2017-214 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4474 | 3.4475 | 0.0001
GEN-2017-214 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.2366 | 6.2371 | 0.0005
GEN-2017-214 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.0116 | 4.0118 | 0.0002
GEN-2017-214 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.2655 | 6.266 | 0.0005
GEN-2017-214 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5502 | 3.5504 | 0.0002
GEN-2017-214 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.2871 | 4.2873 | 0.0002
GEN-2017-214 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4519 | 3.452 | 0.0001
GEN-2017-214 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.2939 | 5.2943 | 0.0004
GEN-2017-214 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1068 | 3.1069 | 0.0001
GEN-2017-214 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.3863 | 6.3869 | 0.0006
GEN-2017-214 | 01 NORTH | 655903 | ROSS -MW7 | 115 | 9.2404 | 9.2435 | 0.0031
GEN-2017-214 | 01 NORTH | 655904 | BELDEN -MW7 | 115 | 10.0639 | 10.0727 | 0.0088
GEN-2017-214 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 10.4936 | 10.5011 | 0.0075
GEN-2017-214 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 20.4384 | 20.4614 | 0.023
GEN-2017-214 | 01 NORTH | 655908 | PARSHALL-MW7 | 115 | 8.4159 | 8.4219 | 0.006
GEN-2017-214 | 01 NORTH | 655909 | HESS GAS-MW7 | 115 | 11.8369 | 11.8455 | 0.0086
GEN-2017-214 | 01 NORTH | 655910 | LINDAHLS-MW7 | 115 | 5.8842 | 5.886 | 0.0018
GEN-2017-214 | 01 NORTH | 655911 | SIMPSON -MW7 | 115 | 3.9752 | 3.976 | 0.0008
GEN-2017-214 | 01 NORTH | 655912 | AUSTIN -MW7 | 115 | 6.7037 | 6.7076 | 0.0039
GEN-2017-214 | 01 NORTH | 655914 | NE.ROSS_-MW7 | 115 | 4.3163 | 4.3197 | 0.0034
GEN-2017-214 | 01 NORTH | 655916 | PALERMO -MW7 | 115 | 7.3945 | 7.4073 | 0.0128
GEN-2017-214 | 01 NORTH | 655917 | STANLEY -MW7 | 115 | 7.1618 | 7.171 | 0.0092
GEN-2017-214 | 01 NORTH | 655918 | PALGASPL-MW7 | 115 | 6.2211 | 6.2302 | 0.0091
GEN-2017-214 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 12.1484 | 12.1565 | 0.0081
GEN-2017-214 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 13.5388 | 13.5502 | 0.0114
GEN-2017-214 | 01 NORTH | 655921 | LOSTWOOD-MW7 | 115 | 3.5449 | 3.5472 | 0.0023
GEN-2017-214 | 01 NORTH | 655930 | WHTEARTH-MW7 | 115 | 12.8308 | 12.8409 | 0.0101
GEN-2017-214 | 01 NORTH | 655944 | PLAZA -MW7 | 115 | 6.9876 | 6.9932 | 0.0056
GEN-2017-214 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 8.9905 | 8.9939 | 0.0034
GEN-2017-214 | 01 NORTH | 655946 | POWERSLK-MW7 | 115 | 4.9097 | 4.911 | 0.0013
GEN-2017-214 | 01 NORTH | 655947 | PWRSLKTP-MW7 | 115 | 7.7194 | 7.7228 | 0.0034
GEN-2017-214 | 01 NORTH | 655948 | LIBERTY -MW7 | 115 | 6.9717 | 6.9743 | 0.0026
GEN-2017-214 | 01 NORTH | 655949 | BLAISDEL-MW7 | 115 | 9.0185 | 9.0439 | 0.0254
GEN-2017-214 | 01 NORTH | 655950 | LOSTWD_T-MW7 | 115 | 5.8492 | 5.8554 | 0.0062
GEN-2017-214 | 01 NORTH | 655951 | NE.ROS_T-MW7 | 115 | 4.8505 | 4.8547 | 0.0042
GEN-2017-214 | 01 NORTH | 655952 | TIOGA.N_-MW7 | 115 | 11.8827 | 11.8913 | 0.0086
GEN-2017-214 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.6612 | 6.6629 | 0.0017
GEN-2017-214 | 01 NORTH | 657741 | ROUGHRIDER 4 | 230 | 15.8797 | 15.8812 | 0.0015
GEN-2017-214 | 01 NORTH | 657742 | OLIVERWND3 4 | 230 | 11.1597 | 11.1604 | 0.0007
GEN-2017-214 | 01 NORTH | 657751 | CENTER 4 | 230 | 20.5113 | 20.5134 | 0.0021
GEN-2017-214 | 01 NORTH | 657756 | SQBUTTE4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-214 | 01 NORTH | 657759 | PICKERT4 | 230 | 4.3986 | 4.3988 | 0.0002
GEN-2017-214 | 01 NORTH | 657791 | CENTER 3 | 345 | 12.3806 | 12.3816 | 0.001
GEN-2017-214 | 01 NORTH | 657804 | MPC-VCY8 | 69 | 2.6481 | 2.6481 | 0
GEN-2017-214 | 01 NORTH | 657848 | YNG2 4 | 230 | 18.8868 | 18.8884 | 0.0016
GEN-2017-214 | 01 NORTH | 657923 | PICKERT8 | 69 | 3.2672 | 3.2673 | 0.0001
GEN-2017-214 | 01 NORTH | 657951 | CNTSHNT3 | 345 | 12.3806 | 12.3816 | 0.001
GEN-2017-214 | 01 NORTH | 658209 | MOORHDW4 | 230 | 7.0931 | 7.0932 | 0.0001
GEN-2017-214 | 01 NORTH | 659060 | FINSTAD345 | 345 | 7.3099 | 7.3184 | 0.0085
GEN-2017-214 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 20.174 | 20.1868 | 0.0128
GEN-2017-214 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 19.5126 | 19.5394 | 0.0268
GEN-2017-214 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 25.3399 | 25.3914 | 0.0515
GEN-2017-214 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.259 | 6.4555 | 0.1965
GEN-2017-214 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.4183 | 5.4195 | 0.0012
GEN-2017-214 | 01 NORTH | 659128 | HERBERTW-KM4 | 230 | 5.0722 | 5.0725 | 0.0003
GEN-2017-214 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.5219 | 6.5221 | 0.0002
GEN-2017-214 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.9421 | 12.9679 | 0.0258
GEN-2017-214 | 01 NORTH | 659139 | NESET___-BE7 | 115 | 13.5379 | 13.5492 | 0.0113
GEN-2017-214 | 01 NORTH | 659140 | NRTSHORE-BE4 | 230 | 6.0272 | 6.0317 | 0.0045
GEN-2017-214 | 01 NORTH | 659141 | NRTSHORE-BE7 | 115 | 17.4983 | 17.5092 | 0.0109
GEN-2017-214 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.1809 | 6.2256 | 0.0447
GEN-2017-214 | 01 NORTH | 659144 | BLAISDEL-BE7 | 115 | 9.3274 | 9.355 | 0.0276
GEN-2017-214 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.5218 | 6.522 | 0.0002
GEN-2017-214 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 11.047 | 11.1631 | 0.1161
GEN-2017-214 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.3245 | 6.3246 | 0.0001
GEN-2017-214 | 01 NORTH | 659178 | BALTA___-CP7 | 115 | 3.7326 | 3.7337 | 0.0011
GEN-2017-214 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.2002 | 14.2024 | 0.0022
GEN-2017-214 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.9287 | 10.9328 | 0.0041
GEN-2017-214 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7391 | 3.7393 | 0.0002
GEN-2017-214 | 01 NORTH | 659190 | ND.PW1__-BE7 | 115 | 7.4474 | 7.4694 | 0.022
GEN-2017-214 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 22.9829 | 23.0251 | 0.0422
GEN-2017-214 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 19.0757 | 19.0872 | 0.0115
GEN-2017-214 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 20.174 | 20.1868 | 0.0128
GEN-2017-214 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.8663 | 9.8669 | 0.0006
GEN-2017-214 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.6778 | 7.679 | 0.0012
GEN-2017-214 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.3997 | 7.4001 | 0.0004
GEN-2017-214 | 01 NORTH | 659280 | POMONA__-PP7 | 115 | 3.4308 | 3.4309 | 0.0001
GEN-2017-214 | 01 NORTH | 659284 | ECKLUND_-PP4 | 230 | 6.4452 | 6.4461 | 0.0009
GEN-2017-214 | 01 NORTH | 659300 | STANTN.T-BE7 | 115 | 7.8801 | 7.8816 | 0.0015
GEN-2017-214 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.7527 | 11.7559 | 0.0032
GEN-2017-214 | 01 NORTH | 659308 | KENASTON-BE7 | 115 | 3.4719 | 3.475 | 0.0031
GEN-2017-214 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 11.33 | 11.3363 | 0.0063
GEN-2017-214 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.7624 | 8.7748 | 0.0124
GEN-2017-214 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.7595 | 12.7836 | 0.0241
GEN-2017-214 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.5168 | 6.517 | 0.0002
GEN-2017-214 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.2682 | 12.2696 | 0.0014
GEN-2017-214 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.2683 | 12.2697 | 0.0014
GEN-2017-214 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.8025 | 7.8083 | 0.0058
GEN-2017-214 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.2013 | 9.2048 | 0.0035
GEN-2017-214 | 01 NORTH | 659365 | BALDWIN_-PP4 | 230 | 6.4452 | 6.4461 | 0.0009
GEN-2017-214 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.9265 | 9.93 | 0.0035
GEN-2017-214 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.0306 | 12.0324 | 0.0018
GEN-2017-214 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.5045 | 7.5067 | 0.0022
GEN-2017-214 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 14.4549 | 14.4577 | 0.0028
GEN-2017-214 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.988 | 8.9917 | 0.0037
GEN-2017-214 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 18.0987 | 18.103 | 0.0043
GEN-2017-214 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.8222 | 4.8257 | 0.0035
GEN-2017-214 | 01 NORTH | 659408 | CAMPBL._-PP4 | 230 | 3.7476 | 3.7477 | 0.0001
GEN-2017-214 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 20.174 | 20.1868 | 0.0128
GEN-2017-214 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.8084 | 4.8085 | 0.0001
GEN-2017-214 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 19.5126 | 19.5394 | 0.0268
GEN-2017-214 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.3245 | 6.3246 | 0.0001
GEN-2017-214 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 19.5126 | 19.5394 | 0.0268
GEN-2017-214 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.7624 | 8.7748 | 0.0124
GEN-2017-214 | 01 NORTH | 659428 | CC.LS-LO-BE3 | 345 | 6.4903 | 6.4905 | 0.0002
GEN-2017-214 | 01 NORTH | 659433 | TRIPLEH__UA3 | 345 | 6.4603 | 6.4605 | 0.0002
GEN-2017-214 | 01 NORTH | 659454 | LINDAHLWND 7 | 115 | 5.4162 | 5.4177 | 0.0015
GEN-2017-214 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 18.0011 | 18.0053 | 0.0042
GEN-2017-214 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 18.0127 | 18.0169 | 0.0042
GEN-2017-214 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.2196 | 6.2255 | 0.0059
GEN-2017-214 | 01 NORTH | 659543 | PICKCITY-RR7 | 115 | 10.1394 | 10.1428 | 0.0034
GEN-2017-214 | 01 NORTH | 659576 | BEPCPRXCC1 3 | 345 | 19.3328 | 19.3443 | 0.0115
GEN-2017-214 | 01 NORTH | 659580 | BEPCPRXCC2 7 | 115 | 17.4606 | 17.4712 | 0.0106
GEN-2017-214 | 01 NORTH | 659584 | BEPCPRXCC3 7 | 115 | 14.2081 | 14.2108 | 0.0027
GEN-2017-214 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.7542 | 6.7554 | 0.0012
GEN-2017-214 | 01 NORTH | 661011 | BEULAH27 | 115 | 9.479 | 9.4799 | 0.0009
GEN-2017-214 | 01 NORTH | 661016 | COYOTE 3 | 345 | 8.52 | 8.5205 | 0.0005
GEN-2017-214 | 01 NORTH | 661029 | ESTBMRK7 | 115 | 16.1972 | 16.1987 | 0.0015
GEN-2017-214 | 01 NORTH | 661052 | KENMARE7 | 115 | 3.3936 | 3.3964 | 0.0028
GEN-2017-214 | 01 NORTH | 661053 | MANDAN 4 | 230 | 16.2457 | 16.2479 | 0.0022
GEN-2017-214 | 01 NORTH | 661060 | LINTON 7 | 115 | 1.399 | 1.399 | 0
GEN-2017-214 | 01 NORTH | 661080 | STANLEY7 | 115 | 3.9574 | 3.9595 | 0.0021
GEN-2017-214 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.9421 | 12.9679 | 0.0258
GEN-2017-214 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.4819 | 13.4933 | 0.0114
GEN-2017-214 | 01 NORTH | 661086 | TIOGA7 7 | 115 | 10.3194 | 10.3257 | 0.0063
GEN-2017-214 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.8489 | 5.8505 | 0.0016
GEN-2017-214 | 01 NORTH | 661281 | LIGNITE7 | 115 | 1.5905 | 1.5911 | 0.0006
GEN-2017-214 | 01 NORTH | 672601 | BD 4 | 230 | 15.6039 | 15.6043 | 0.0004
GEN-2017-214 | 01 NORTH | 672602 | BDX 4 | 230 | 5.029 | 5.0302 | 0.0012
GEN-2017-214 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0278 | 5.029 | 0.0012
GEN-2017-214 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 2.9208 | 3.1445 | 0.2237
GEN-2017-215 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.6278 | 7.6319 | 0.0041
GEN-2017-215 | 01 NORTH | 587050 | GEN-2016-007 | 115 | 4.1176 | 4.1177 | 0.0001
GEN-2017-215 | 01 NORTH | 587720 | GEN-2016-087 | 230 | 4.0525 | 4.0526 | 0.0001
GEN-2017-215 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 12.7653 | 12.7766 | 0.0113
GEN-2017-215 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 4.6388 | 4.6413 | 0.0025
GEN-2017-215 | 01 NORTH | 602006 | SHEYNNE4 | 230 | 11.0546 | 11.0548 | 0.0002
GEN-2017-215 | 01 NORTH | 602052 | MAGIC CITY 4 | 230 | 4.4696 | 4.4739 | 0.0043
GEN-2017-215 | 01 NORTH | 603022 | SOURIS 7 | 115 | 9.0411 | 9.0768 | 0.0357
GEN-2017-215 | 01 NORTH | 603023 | MALLARD7 | 115 | 11.2768 | 11.3574 | 0.0806
GEN-2017-215 | 01 NORTH | 603270 | MAGIC CITY 7 | 115 | 9.1803 | 9.1995 | 0.0192
GEN-2017-215 | 01 NORTH | 605634 | VELVA TAP | 115 | 8.2663 | 8.2781 | 0.0118
GEN-2017-215 | 01 NORTH | 608597 | SQBP1DC4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-215 | 01 NORTH | 608599 | SQBP2DC4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-215 | 01 NORTH | 608600 | BISONMP4 | 230 | 8.0987 | 8.0989 | 0.0002
GEN-2017-215 | 01 NORTH | 608602 | SQBEAST4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-215 | 01 NORTH | 608603 | TRICNTY4 | 230 | 5.8686 | 5.8687 | 0.0001
GEN-2017-215 | 01 NORTH | 615145 | NEW FRONT W | 115 | 4.6101 | 4.6124 | 0.0023
GEN-2017-215 | 01 NORTH | 615347 | GRE-MCHENRY4 | 230 | 6.5247 | 6.5299 | 0.0052
GEN-2017-215 | 01 NORTH | 615348 | GRE-MCHENRY7 | 115 | 8.6371 | 8.6465 | 0.0094
GEN-2017-215 | 01 NORTH | 615600 | GRE-COAL CR4 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-215 | 01 NORTH | 615601 | GRE-COAL FM8 | 69 | 9.0417 | 9.042 | 0.0003
GEN-2017-215 | 01 NORTH | 615604 | GRE-COALFB14 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-215 | 01 NORTH | 615605 | GRE-COALFB24 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-215 | 01 NORTH | 615606 | GRE-COALFB34 | 230 | 19.1886 | 19.193 | 0.0044
GEN-2017-215 | 01 NORTH | 615900 | GRE-COAL TP4 | 230 | 16.1372 | 16.1415 | 0.0043
GEN-2017-215 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.0179 | 18.0226 | 0.0047
GEN-2017-215 | 01 NORTH | 615903 | GRE-BALTA 4 | 230 | 6.6895 | 6.6927 | 0.0032
GEN-2017-215 | 01 NORTH | 615904 | GRE-BALTACB4 | 230 | 6.6895 | 6.6927 | 0.0032
GEN-2017-215 | 01 NORTH | 620276 | NHARVEY7 | 115 | 3.2677 | 3.268 | 0.0003
GEN-2017-215 | 01 NORTH | 620277 | SELZ 7 | 115 | 1.6645 | 1.6647 | 0.0002
GEN-2017-215 | 01 NORTH | 620278 | ESMDOTP7 | 115 | 2.3918 | 2.3922 | 0.0004
GEN-2017-215 | 01 NORTH | 620290 | HARVEY 4 | 230 | 5.0626 | 5.064 | 0.0014
GEN-2017-215 | 01 NORTH | 620368 | RGBYWND4 | 230 | 4.7915 | 4.7931 | 0.0016
GEN-2017-215 | 01 NORTH | 620369 | JAMESTN3 | 345 | 5.7007 | 5.7008 | 0.0001
GEN-2017-215 | 01 NORTH | 620379 | RUGBY 4 | 230 | 5.9509 | 5.9537 | 0.0028
GEN-2017-215 | 01 NORTH | 620381 | UNDERWD4 | 230 | 15.1013 | 15.1042 | 0.0029
GEN-2017-215 | 01 NORTH | 652204 | VALLEYC8 | 69 | 2.6481 | 2.6481 | 0
GEN-2017-215 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.8255 | 6.8268 | 0.0013
GEN-2017-215 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1039 | 1.104 | 0.0001
GEN-2017-215 | 01 NORTH | 652296 | WARD 4 | 230 | 14.4965 | 14.4988 | 0.0023
GEN-2017-215 | 01 NORTH | 652391 | WILLISTON27 | 115 | 18.677 | 18.6835 | 0.0065
GEN-2017-215 | 01 NORTH | 652400 | WILISTN4 | 230 | 11.3969 | 11.4032 | 0.0063
GEN-2017-215 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.6762 | 8.677 | 0.0008
GEN-2017-215 | 01 NORTH | 652421 | WILISTN7 | 115 | 18.669 | 18.6755 | 0.0065
GEN-2017-215 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.81 | 6.8111 | 0.0011
GEN-2017-215 | 01 NORTH | 652426 | BISMARK4 | 230 | 14.6065 | 14.6095 | 0.003
GEN-2017-215 | 01 NORTH | 652427 | BISMARK7 | 115 | 16.2245 | 16.226 | 0.0015
GEN-2017-215 | 01 NORTH | 652428 | CARNGTN7 | 115 | 2.7238 | 2.7239 | 0.0001
GEN-2017-215 | 01 NORTH | 652432 | EDGELEY7 | 115 | 4.2185 | 4.2185 | 0
GEN-2017-215 | 01 NORTH | 652435 | FARGO 4 | 230 | 10.2287 | 10.2289 | 0.0002
GEN-2017-215 | 01 NORTH | 652436 | FARGO 7 | 115 | 11.2495 | 11.2497 | 0.0002
GEN-2017-215 | 01 NORTH | 652437 | GRNDFKS4 | 230 | 7.0646 | 7.0649 | 0.0003
GEN-2017-215 | 01 NORTH | 652440 | NELSON 7 | 115 | 7.4474 | 7.4694 | 0.022
GEN-2017-215 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.2322 | 12.2384 | 0.0062
GEN-2017-215 | 01 NORTH | 652442 | GARRISN7 | 115 | 15.6788 | 15.6888 | 0.01
GEN-2017-215 | 01 NORTH | 652444 | JAMESTN4 | 230 | 8.631 | 8.6316 | 0.0006
GEN-2017-215 | 01 NORTH | 652445 | JAMESTN7 | 115 | 10.4229 | 10.4233 | 0.0004
GEN-2017-215 | 01 NORTH | 652446 | PLEASANT LK7 | 115 | 6.0482 | 6.0509 | 0.0027
GEN-2017-215 | 01 NORTH | 652447 | LEEDS 7 | 115 | 3.997 | 3.9978 | 0.0008
GEN-2017-215 | 01 NORTH | 652452 | RUGBY 7 | 115 | 8.2656 | 8.2711 | 0.0055
GEN-2017-215 | 01 NORTH | 652453 | TOWNER 7 | 115 | 4.7955 | 4.7985 | 0.003
GEN-2017-215 | 01 NORTH | 652454 | VALLEYC7 | 115 | 4.5544 | 4.5545 | 0.0001
GEN-2017-215 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.6888 | 10.6952 | 0.0064
GEN-2017-215 | 01 NORTH | 652464 | DENBIGH TAP7 | 115 | 4.6187 | 4.6215 | 0.0028
GEN-2017-215 | 01 NORTH | 652466 | HILKEN 4 | 230 | 7.6536 | 7.6549 | 0.0013
GEN-2017-215 | 01 NORTH | 652496 | WINCHESTER4 | 230 | 4.5613 | 4.5614 | 0.0001
GEN-2017-215 | 01 NORTH | 652499 | CAMPBELL 4 | 230 | 4.0525 | 4.0526 | 0.0001
GEN-2017-215 | 01 NORTH | 652590 | SNAKECR7 | 115 | 5.8316 | 5.8334 | 0.0018
GEN-2017-215 | 01 NORTH | 655609 | ROLETTE_-CP7 | 115 | 2.7853 | 2.786 | 0.0007
GEN-2017-215 | 01 NORTH | 655612 | HARVEY -CP7 | 115 | 3.8409 | 3.8413 | 0.0004
GEN-2017-215 | 01 NORTH | 655633 | NPESMOND-CP8 | 69 | 1.2695 | 1.2695 | 0
GEN-2017-215 | 01 NORTH | 655638 | ESMOND -CP7 | 115 | 2.0373 | 2.0377 | 0.0004
GEN-2017-215 | 01 NORTH | 655640 | ESMOND -CP8 | 69 | 1.5115 | 1.5116 | 0.0001
GEN-2017-215 | 01 NORTH | 655641 | BERTHOLD-CP7 | 115 | 6.3887 | 6.4051 | 0.0164
GEN-2017-215 | 01 NORTH | 655643 | VOLTAIR -CP7 | 115 | 8.5744 | 8.5836 | 0.0092
GEN-2017-215 | 01 NORTH | 655647 | WARD -CP7 | 115 | 8.3606 | 8.361 | 0.0004
GEN-2017-215 | 01 NORTH | 655650 | BOTINU.W-CP7 | 115 | 2.5858 | 2.5877 | 0.0019
GEN-2017-215 | 01 NORTH | 655651 | BOTNU.SE-CP7 | 115 | 2.6765 | 2.6783 | 0.0018
GEN-2017-215 | 01 NORTH | 655652 | E.BISMRK-CP7 | 115 | 15.7587 | 15.7601 | 0.0014
GEN-2017-215 | 01 NORTH | 655654 | RUGBY -CP7 | 115 | 8.2272 | 8.2327 | 0.0055
GEN-2017-215 | 01 NORTH | 655655 | E.RUTHVL-CP7 | 115 | 6.7955 | 6.8247 | 0.0292
GEN-2017-215 | 01 NORTH | 655656 | DUNNING -CP7 | 115 | 2.7438 | 2.7469 | 0.0031
GEN-2017-215 | 01 NORTH | 655657 | SW.MINOT-CP7 | 115 | 8.1371 | 8.188 | 0.0509
GEN-2017-215 | 01 NORTH | 655658 | RUTHVILL-CP7 | 115 | 6.3106 | 6.3358 | 0.0252
GEN-2017-215 | 01 NORTH | 655659 | BOTTINEU-CP7 | 115 | 2.5608 | 2.5625 | 0.0017
GEN-2017-215 | 01 NORTH | 655660 | RUGBY_RB-CP7 | 115 | 8.5814 | 8.5866 | 0.0052
GEN-2017-215 | 01 NORTH | 655661 | DOUGLS.C-CP7 | 115 | 4.1068 | 4.1079 | 0.0011
GEN-2017-215 | 01 NORTH | 655664 | MAKOTI -CP7 | 115 | 6.0167 | 6.0207 | 0.004
GEN-2017-215 | 01 NORTH | 655665 | RUGBY TP-CP7 | 115 | 8.2656 | 8.2711 | 0.0055
GEN-2017-215 | 01 NORTH | 655676 | HARAM -CP7 | 115 | 2.0732 | 2.0744 | 0.0012
GEN-2017-215 | 01 NORTH | 655690 | MAX_____-CP7 | 115 | 6.1588 | 6.1667 | 0.0079
GEN-2017-215 | 01 NORTH | 655693 | WARD_SPR-CP7 | 115 | 3.1355 | 3.1355 | 0
GEN-2017-215 | 01 NORTH | 655696 | ESMOND J-CP7 | 115 | 2.0652 | 2.0655 | 0.0003
GEN-2017-215 | 01 NORTH | 655701 | ROLETTE__CP8 | 69 | 2.7019 | 2.7023 | 0.0004
GEN-2017-215 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9756 | 0.9756 | 0
GEN-2017-215 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9027 | 0.9027 | 0
GEN-2017-215 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9095 | 0.9095 | 0
GEN-2017-215 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6894 | 0.6894 | 0
GEN-2017-215 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6176 | 0.6177 | 0.0001
GEN-2017-215 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1102 | 1.1102 | 0
GEN-2017-215 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1161 | 1.1161 | 0
GEN-2017-215 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.107 | 1.1071 | 0.0001
GEN-2017-215 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5133 | 1.5134 | 0.0001
GEN-2017-215 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.023 | 1.023 | 0
GEN-2017-215 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9904 | 0.9905 | 0.0001
GEN-2017-215 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9909 | 0.9909 | 0
GEN-2017-215 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5509 | 1.551 | 0.0001
GEN-2017-215 | 01 NORTH | 655780 | NORMANLK-BD7 | 115 | 3.2045 | 3.2051 | 0.0006
GEN-2017-215 | 01 NORTH | 655781 | LARSON -BD7 | 115 | 2.2089 | 2.2092 | 0.0003
GEN-2017-215 | 01 NORTH | 655782 | LIGNIBRD-BD7 | 115 | 1.5468 | 1.5469 | 0.0001
GEN-2017-215 | 01 NORTH | 655783 | HAWKEYE -BD7 | 115 | 1.4765 | 1.4766 | 0.0001
GEN-2017-215 | 01 NORTH | 655784 | AMBROSE -BD7 | 115 | 1.2492 | 1.2493 | 0.0001
GEN-2017-215 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.0081 | 6.0088 | 0.0007
GEN-2017-215 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.1866 | 4.1868 | 0.0002
GEN-2017-215 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0571 | 4.0573 | 0.0002
GEN-2017-215 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 7.9647 | 7.9655 | 0.0008
GEN-2017-215 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.0782 | 14.0803 | 0.0021
GEN-2017-215 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.9353 | 6.9358 | 0.0005
GEN-2017-215 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.126 | 3.1261 | 0.0001
GEN-2017-215 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.5486 | 5.549 | 0.0004
GEN-2017-215 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.6574 | 3.6576 | 0.0002
GEN-2017-215 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.065 | 4.0652 | 0.0002
GEN-2017-215 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.6762 | 8.677 | 0.0008
GEN-2017-215 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.7218 | 6.7221 | 0.0003
GEN-2017-215 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2677 | 3.2678 | 0.0001
GEN-2017-215 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.2411 | 5.2414 | 0.0003
GEN-2017-215 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.6474 | 4.6476 | 0.0002
GEN-2017-215 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.1671 | 4.1673 | 0.0002
GEN-2017-215 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3155 | 4.3158 | 0.0003
GEN-2017-215 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.7291 | 5.7295 | 0.0004
GEN-2017-215 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 9.7975 | 9.7988 | 0.0013
GEN-2017-215 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.4694 | 3.4696 | 0.0002
GEN-2017-215 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9166 | 2.9167 | 0.0001
GEN-2017-215 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5693 | 3.5694 | 0.0001
GEN-2017-215 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.3805 | 8.3814 | 0.0009
GEN-2017-215 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5245 | 3.5247 | 0.0002
GEN-2017-215 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.7883 | 4.7886 | 0.0003
GEN-2017-215 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.4975 | 6.498 | 0.0005
GEN-2017-215 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.5887 | 2.5888 | 0.0001
GEN-2017-215 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3474 | 4.3476 | 0.0002
GEN-2017-215 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.735 | 3.7352 | 0.0002
GEN-2017-215 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3191 | 2.3192 | 0.0001
GEN-2017-215 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1297 | 3.1298 | 0.0001
GEN-2017-215 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.7428 | 5.7433 | 0.0005
GEN-2017-215 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.8895 | 5.89 | 0.0005
GEN-2017-215 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.065 | 4.0652 | 0.0002
GEN-2017-215 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.989 | 2.9892 | 0.0002
GEN-2017-215 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7557 | 2.7558 | 0.0001
GEN-2017-215 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6554 | 2.6555 | 0.0001
GEN-2017-215 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9184 | 3.9186 | 0.0002
GEN-2017-215 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.532 | 4.5323 | 0.0003
GEN-2017-215 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 6.9468 | 6.9475 | 0.0007
GEN-2017-215 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.3452 | 6.3457 | 0.0005
GEN-2017-215 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.5956 | 7.5962 | 0.0006
GEN-2017-215 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.3443 | 8.345 | 0.0007
GEN-2017-215 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.2478 | 5.2481 | 0.0003
GEN-2017-215 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9133 | 3.9135 | 0.0002
GEN-2017-215 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.683 | 4.6832 | 0.0002
GEN-2017-215 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.7617 | 5.7622 | 0.0005
GEN-2017-215 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.0374 | 13.0397 | 0.0023
GEN-2017-215 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 9.8467 | 9.848 | 0.0013
GEN-2017-215 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.764 | 7.7648 | 0.0008
GEN-2017-215 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.4286 | 5.429 | 0.0004
GEN-2017-215 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2383 | 4.2386 | 0.0003
GEN-2017-215 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.0475 | 5.0479 | 0.0004
GEN-2017-215 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4474 | 3.4475 | 0.0001
GEN-2017-215 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.2366 | 6.2371 | 0.0005
GEN-2017-215 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.0116 | 4.0118 | 0.0002
GEN-2017-215 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.2655 | 6.266 | 0.0005
GEN-2017-215 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5502 | 3.5504 | 0.0002
GEN-2017-215 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.2871 | 4.2873 | 0.0002
GEN-2017-215 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4519 | 3.452 | 0.0001
GEN-2017-215 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.2939 | 5.2943 | 0.0004
GEN-2017-215 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1068 | 3.1069 | 0.0001
GEN-2017-215 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.3863 | 6.3869 | 0.0006
GEN-2017-215 | 01 NORTH | 655903 | ROSS -MW7 | 115 | 9.2404 | 9.2435 | 0.0031
GEN-2017-215 | 01 NORTH | 655904 | BELDEN -MW7 | 115 | 10.0639 | 10.0727 | 0.0088
GEN-2017-215 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 10.4936 | 10.5011 | 0.0075
GEN-2017-215 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 20.4384 | 20.4614 | 0.023
GEN-2017-215 | 01 NORTH | 655908 | PARSHALL-MW7 | 115 | 8.4159 | 8.4219 | 0.006
GEN-2017-215 | 01 NORTH | 655909 | HESS GAS-MW7 | 115 | 11.8369 | 11.8455 | 0.0086
GEN-2017-215 | 01 NORTH | 655910 | LINDAHLS-MW7 | 115 | 5.8842 | 5.886 | 0.0018
GEN-2017-215 | 01 NORTH | 655911 | SIMPSON -MW7 | 115 | 3.9752 | 3.976 | 0.0008
GEN-2017-215 | 01 NORTH | 655912 | AUSTIN -MW7 | 115 | 6.7037 | 6.7076 | 0.0039
GEN-2017-215 | 01 NORTH | 655914 | NE.ROSS_-MW7 | 115 | 4.3163 | 4.3197 | 0.0034
GEN-2017-215 | 01 NORTH | 655916 | PALERMO -MW7 | 115 | 7.3945 | 7.4073 | 0.0128
GEN-2017-215 | 01 NORTH | 655917 | STANLEY -MW7 | 115 | 7.1618 | 7.171 | 0.0092
GEN-2017-215 | 01 NORTH | 655918 | PALGASPL-MW7 | 115 | 6.2211 | 6.2302 | 0.0091
GEN-2017-215 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 12.1484 | 12.1565 | 0.0081
GEN-2017-215 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 13.5388 | 13.5502 | 0.0114
GEN-2017-215 | 01 NORTH | 655921 | LOSTWOOD-MW7 | 115 | 3.5449 | 3.5472 | 0.0023
GEN-2017-215 | 01 NORTH | 655930 | WHTEARTH-MW7 | 115 | 12.8308 | 12.8409 | 0.0101
GEN-2017-215 | 01 NORTH | 655944 | PLAZA -MW7 | 115 | 6.9876 | 6.9932 | 0.0056
GEN-2017-215 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 8.9905 | 8.9939 | 0.0034
GEN-2017-215 | 01 NORTH | 655946 | POWERSLK-MW7 | 115 | 4.9097 | 4.911 | 0.0013
GEN-2017-215 | 01 NORTH | 655947 | PWRSLKTP-MW7 | 115 | 7.7194 | 7.7228 | 0.0034
GEN-2017-215 | 01 NORTH | 655948 | LIBERTY -MW7 | 115 | 6.9717 | 6.9743 | 0.0026
GEN-2017-215 | 01 NORTH | 655949 | BLAISDEL-MW7 | 115 | 9.0185 | 9.0439 | 0.0254
GEN-2017-215 | 01 NORTH | 655950 | LOSTWD_T-MW7 | 115 | 5.8492 | 5.8554 | 0.0062
GEN-2017-215 | 01 NORTH | 655951 | NE.ROS_T-MW7 | 115 | 4.8505 | 4.8547 | 0.0042
GEN-2017-215 | 01 NORTH | 655952 | TIOGA.N_-MW7 | 115 | 11.8827 | 11.8913 | 0.0086
GEN-2017-215 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.6612 | 6.6629 | 0.0017
GEN-2017-215 | 01 NORTH | 657741 | ROUGHRIDER 4 | 230 | 15.8797 | 15.8812 | 0.0015
GEN-2017-215 | 01 NORTH | 657742 | OLIVERWND3 4 | 230 | 11.1597 | 11.1604 | 0.0007
GEN-2017-215 | 01 NORTH | 657751 | CENTER 4 | 230 | 20.5113 | 20.5134 | 0.0021
GEN-2017-215 | 01 NORTH | 657756 | SQBUTTE4 | 230 | 23.0765 | 23.0792 | 0.0027
GEN-2017-215 | 01 NORTH | 657759 | PICKERT4 | 230 | 4.3986 | 4.3988 | 0.0002
GEN-2017-215 | 01 NORTH | 657791 | CENTER 3 | 345 | 12.3806 | 12.3816 | 0.001
GEN-2017-215 | 01 NORTH | 657804 | MPC-VCY8 | 69 | 2.6481 | 2.6481 | 0
GEN-2017-215 | 01 NORTH | 657848 | YNG2 4 | 230 | 18.8868 | 18.8884 | 0.0016
GEN-2017-215 | 01 NORTH | 657923 | PICKERT8 | 69 | 3.2672 | 3.2673 | 0.0001
GEN-2017-215 | 01 NORTH | 657951 | CNTSHNT3 | 345 | 12.3806 | 12.3816 | 0.001
GEN-2017-215 | 01 NORTH | 658209 | MOORHDW4 | 230 | 7.0931 | 7.0932 | 0.0001
GEN-2017-215 | 01 NORTH | 659060 | FINSTAD345 | 345 | 7.3099 | 7.3184 | 0.0085
GEN-2017-215 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 20.174 | 20.1868 | 0.0128
GEN-2017-215 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 19.5126 | 19.5394 | 0.0268
GEN-2017-215 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 25.3399 | 25.3914 | 0.0515
GEN-2017-215 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.259 | 6.4555 | 0.1965
GEN-2017-215 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.4183 | 5.4195 | 0.0012
GEN-2017-215 | 01 NORTH | 659128 | HERBERTW-KM4 | 230 | 5.0722 | 5.0725 | 0.0003
GEN-2017-215 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.5219 | 6.5221 | 0.0002
GEN-2017-215 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.9421 | 12.9679 | 0.0258
GEN-2017-215 | 01 NORTH | 659139 | NESET___-BE7 | 115 | 13.5379 | 13.5492 | 0.0113
GEN-2017-215 | 01 NORTH | 659140 | NRTSHORE-BE4 | 230 | 6.0272 | 6.0317 | 0.0045
GEN-2017-215 | 01 NORTH | 659141 | NRTSHORE-BE7 | 115 | 17.4983 | 17.5092 | 0.0109
GEN-2017-215 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.1809 | 6.2256 | 0.0447
GEN-2017-215 | 01 NORTH | 659144 | BLAISDEL-BE7 | 115 | 9.3274 | 9.355 | 0.0276
GEN-2017-215 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.5218 | 6.522 | 0.0002
GEN-2017-215 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 11.047 | 11.1631 | 0.1161
GEN-2017-215 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.3245 | 6.3246 | 0.0001
GEN-2017-215 | 01 NORTH | 659178 | BALTA___-CP7 | 115 | 3.7326 | 3.7337 | 0.0011
GEN-2017-215 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.2002 | 14.2024 | 0.0022
GEN-2017-215 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.9287 | 10.9328 | 0.0041
GEN-2017-215 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7391 | 3.7393 | 0.0002
GEN-2017-215 | 01 NORTH | 659190 | ND.PW1__-BE7 | 115 | 7.4474 | 7.4694 | 0.022
GEN-2017-215 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 22.9829 | 23.0251 | 0.0422
GEN-2017-215 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 19.0757 | 19.0872 | 0.0115
GEN-2017-215 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 20.174 | 20.1868 | 0.0128
GEN-2017-215 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.8663 | 9.8669 | 0.0006
GEN-2017-215 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.6778 | 7.679 | 0.0012
GEN-2017-215 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.3997 | 7.4001 | 0.0004
GEN-2017-215 | 01 NORTH | 659280 | POMONA__-PP7 | 115 | 3.4308 | 3.4309 | 0.0001
GEN-2017-215 | 01 NORTH | 659284 | ECKLUND_-PP4 | 230 | 6.4452 | 6.4461 | 0.0009
GEN-2017-215 | 01 NORTH | 659300 | STANTN.T-BE7 | 115 | 7.8801 | 7.8816 | 0.0015
GEN-2017-215 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.7527 | 11.7559 | 0.0032
GEN-2017-215 | 01 NORTH | 659308 | KENASTON-BE7 | 115 | 3.4719 | 3.475 | 0.0031
GEN-2017-215 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 11.33 | 11.3363 | 0.0063
GEN-2017-215 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.7624 | 8.7748 | 0.0124
GEN-2017-215 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.7595 | 12.7836 | 0.0241
GEN-2017-215 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.5168 | 6.517 | 0.0002
GEN-2017-215 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.2682 | 12.2696 | 0.0014
GEN-2017-215 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.2683 | 12.2697 | 0.0014
GEN-2017-215 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.8025 | 7.8083 | 0.0058
GEN-2017-215 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.2013 | 9.2048 | 0.0035
GEN-2017-215 | 01 NORTH | 659365 | BALDWIN_-PP4 | 230 | 6.4452 | 6.4461 | 0.0009
GEN-2017-215 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.9265 | 9.93 | 0.0035
GEN-2017-215 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.0306 | 12.0324 | 0.0018
GEN-2017-215 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.5045 | 7.5067 | 0.0022
GEN-2017-215 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 14.4549 | 14.4577 | 0.0028
GEN-2017-215 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.988 | 8.9917 | 0.0037
GEN-2017-215 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 18.0987 | 18.103 | 0.0043
GEN-2017-215 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.8222 | 4.8257 | 0.0035
GEN-2017-215 | 01 NORTH | 659408 | CAMPBL._-PP4 | 230 | 3.7476 | 3.7477 | 0.0001
GEN-2017-215 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 20.174 | 20.1868 | 0.0128
GEN-2017-215 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.8084 | 4.8085 | 0.0001
GEN-2017-215 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 19.5126 | 19.5394 | 0.0268
GEN-2017-215 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.3245 | 6.3246 | 0.0001
GEN-2017-215 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 19.5126 | 19.5394 | 0.0268
GEN-2017-215 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.7624 | 8.7748 | 0.0124
GEN-2017-215 | 01 NORTH | 659428 | CC.LS-LO-BE3 | 345 | 6.4903 | 6.4905 | 0.0002
GEN-2017-215 | 01 NORTH | 659433 | TRIPLEH__UA3 | 345 | 6.4603 | 6.4605 | 0.0002
GEN-2017-215 | 01 NORTH | 659454 | LINDAHLWND 7 | 115 | 5.4162 | 5.4177 | 0.0015
GEN-2017-215 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 18.0011 | 18.0053 | 0.0042
GEN-2017-215 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 18.0127 | 18.0169 | 0.0042
GEN-2017-215 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.2196 | 6.2255 | 0.0059
GEN-2017-215 | 01 NORTH | 659543 | PICKCITY-RR7 | 115 | 10.1394 | 10.1428 | 0.0034
GEN-2017-215 | 01 NORTH | 659576 | BEPCPRXCC1 3 | 345 | 19.3328 | 19.3443 | 0.0115
GEN-2017-215 | 01 NORTH | 659580 | BEPCPRXCC2 7 | 115 | 17.4606 | 17.4712 | 0.0106
GEN-2017-215 | 01 NORTH | 659584 | BEPCPRXCC3 7 | 115 | 14.2081 | 14.2108 | 0.0027
GEN-2017-215 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.7542 | 6.7554 | 0.0012
GEN-2017-215 | 01 NORTH | 661011 | BEULAH27 | 115 | 9.479 | 9.4799 | 0.0009
GEN-2017-215 | 01 NORTH | 661016 | COYOTE 3 | 345 | 8.52 | 8.5205 | 0.0005
GEN-2017-215 | 01 NORTH | 661029 | ESTBMRK7 | 115 | 16.1972 | 16.1987 | 0.0015
GEN-2017-215 | 01 NORTH | 661052 | KENMARE7 | 115 | 3.3936 | 3.3964 | 0.0028
GEN-2017-215 | 01 NORTH | 661053 | MANDAN 4 | 230 | 16.2457 | 16.2479 | 0.0022
GEN-2017-215 | 01 NORTH | 661060 | LINTON 7 | 115 | 1.399 | 1.399 | 0
GEN-2017-215 | 01 NORTH | 661080 | STANLEY7 | 115 | 3.9574 | 3.9595 | 0.0021
GEN-2017-215 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.9421 | 12.9679 | 0.0258
GEN-2017-215 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.4819 | 13.4933 | 0.0114
GEN-2017-215 | 01 NORTH | 661086 | TIOGA7 7 | 115 | 10.3194 | 10.3257 | 0.0063
GEN-2017-215 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.8489 | 5.8505 | 0.0016
GEN-2017-215 | 01 NORTH | 661281 | LIGNITE7 | 115 | 1.5905 | 1.5911 | 0.0006
GEN-2017-215 | 01 NORTH | 672601 | BD 4 | 230 | 15.6039 | 15.6043 | 0.0004
GEN-2017-215 | 01 NORTH | 672602 | BDX 4 | 230 | 5.029 | 5.0302 | 0.0012
GEN-2017-215 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0278 | 5.029 | 0.0012
GEN-2017-215 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 2.9208 | 3.1445 | 0.2237
GEN-2017-222 | 01 NORTH | 87486 | J748GENTIE | 345 | 11.2575 | 11.2601 | 0.0026
GEN-2017-222 | 01 NORTH | 87487 | J748POI | 345 | 12.4356 | 12.4389 | 0.0033
GEN-2017-222 | 01 NORTH | 300097 | 5MARYVB2 | 161 | 11.7307 | 11.7315 | 0.0008
GEN-2017-222 | 01 NORTH | 301556 | 5CLEARCK | 161 | 7.8735 | 7.8738 | 0.0003
GEN-2017-222 | 01 NORTH | 587150 | GEN-2016-021 | 345 | 7.443 | 7.4448 | 0.0018
GEN-2017-222 | 01 NORTH | 587760 | GEN-2016-094 | 230 | 9.2021 | 9.2023 | 0.0002
GEN-2017-222 | 01 NORTH | 587764 | G16-094-TAP | 230 | 9.3614 | 9.3615 | 0.0001
GEN-2017-222 | 01 NORTH | 588306 | ASGI1706 | 161 | 8.2695 | 8.2698 | 0.0003
GEN-2017-222 | 01 NORTH | 588590 | GEN-2017-014 | 230 | 5.616 | 5.616 | 0
GEN-2017-222 | 01 NORTH | 589320 | GEN-2017-094 | 230 | 8.0476 | 8.0477 | 0.0001
GEN-2017-222 | 01 NORTH | 589324 | G17-094-TAP | 230 | 8.0476 | 8.0477 | 0.0001
GEN-2017-222 | 01 NORTH | 601006 | SPLT RK3 | 345 | 14.3057 | 14.3111 | 0.0054
GEN-2017-222 | 01 NORTH | 628909 | HD HV 5 | 161 | 3.0056 | 3.0101 | 0.0045
GEN-2017-222 | 01 NORTH | 628910 | HD WIND 5 | 161 | 5.5439 | 5.5594 | 0.0155
GEN-2017-222 | 01 NORTH | 630009 | ANITA 8 | 69 | 7.8655 | 7.8801 | 0.0146
GEN-2017-222 | 01 NORTH | 630028 | EVERLYN8 | 69 | 7.4699 | 7.4702 | 0.0003
GEN-2017-222 | 01 NORTH | 631069 | ANTA TP5 | 161 | 7.5824 | 7.6245 | 0.0421
GEN-2017-222 | 01 NORTH | 631070 | ANITA 5 | 161 | 6.7189 | 6.7481 | 0.0292
GEN-2017-222 | 01 NORTH | 631164 | G298_WF5 | 161 | 8.9132 | 8.914 | 0.0008
GEN-2017-222 | 01 NORTH | 631183 | CAYLER5 | 161 | 8.9547 | 8.9555 | 0.0008
GEN-2017-222 | 01 NORTH | 635056 | ADAMS 5 | 161 | 6.1481 | 6.1495 | 0.0014
GEN-2017-222 | 01 NORTH | 635200 | RAUN 3 | 345 | 25.8222 | 25.8608 | 0.0386
GEN-2017-222 | 01 NORTH | 635201 | RAUN 5 | 161 | 27.3123 | 27.3529 | 0.0406
GEN-2017-222 | 01 NORTH | 635221 | KELLOGG5 | 161 | 17.4991 | 17.524 | 0.0249
GEN-2017-222 | 01 NORTH | 635223 | PLYMOTH5 | 161 | 20.7266 | 20.7826 | 0.056
GEN-2017-222 | 01 NORTH | 635224 | PLYMOTH8 | 69 | 22.1055 | 22.1323 | 0.0268
GEN-2017-222 | 01 NORTH | 635225 | MORNSD 5 | 161 | 11.1853 | 11.1982 | 0.0129
GEN-2017-222 | 01 NORTH | 635226 | LEEDS 5 | 161 | 16.2097 | 16.2354 | 0.0257
GEN-2017-222 | 01 NORTH | 635235 | SALIX 5 | 161 | 15.0041 | 15.0214 | 0.0173
GEN-2017-222 | 01 NORTH | 635248 | JAMES 8 | 69 | 14.2996 | 14.3101 | 0.0105
GEN-2017-222 | 01 NORTH | 635252 | J412 POI 3 | 345 | 9.7549 | 9.7578 | 0.0029
GEN-2017-222 | 01 NORTH | 635260 | LEMARST5 | 161 | 10.0913 | 10.1033 | 0.012
GEN-2017-222 | 01 NORTH | 635261 | LEMARS S 5 | 161 | 6.1244 | 6.1289 | 0.0045
GEN-2017-222 | 01 NORTH | 635265 | LEMARSINDT 8 | 69 | 7.784 | 7.7872 | 0.0032
GEN-2017-222 | 01 NORTH | 635280 | BVISTA 5 | 161 | 7.7201 | 7.7216 | 0.0015
GEN-2017-222 | 01 NORTH | 635322 | CAROL S8 | 69 | 7.9015 | 7.9103 | 0.0088
GEN-2017-222 | 01 NORTH | 635325 | TEMPLTN8 | 69 | 6.3696 | 6.3825 | 0.0129
GEN-2017-222 | 01 NORTH | 635360 | LTL SIOUX 5 | 161 | 6.671 | 6.6746 | 0.0036
GEN-2017-222 | 01 NORTH | 635385 | HUDSON 8 | 69 | 6.2435 | 6.2451 | 0.0016
GEN-2017-222 | 01 NORTH | 635386 | SXRIVER8 | 69 | 3.4115 | 3.4119 | 0.0004
GEN-2017-222 | 01 NORTH | 635387 | ALCESTR8 | 69 | 1.6686 | 1.6687 | 0.0001
GEN-2017-222 | 01 NORTH | 635390 | IRETON 8 | 69 | 2.8967 | 2.897 | 0.0003
GEN-2017-222 | 01 NORTH | 635391 | IRETONT8 | 69 | 6.0749 | 6.0764 | 0.0015
GEN-2017-222 | 01 NORTH | 635392 | CRAIG 8 | 69 | 1.9935 | 1.9937 | 0.0002
GEN-2017-222 | 01 NORTH | 635393 | MERRIL 8 | 69 | 6.1102 | 6.1122 | 0.002
GEN-2017-222 | 01 NORTH | 635421 | TEMPLTNCAWF8 | 69 | 6.3696 | 6.3825 | 0.0129
GEN-2017-222 | 01 NORTH | 635645 | MCKSBRG 5 | 161 | 8.506 | 8.509 | 0.003
GEN-2017-222 | 01 NORTH | 640070 | BANCRFT7 | 115 | 5.2222 | 5.2229 | 0.0007
GEN-2017-222 | 01 NORTH | 640080 | BELDEN 7 | 115 | 6.2073 | 6.2082 | 0.0009
GEN-2017-222 | 01 NORTH | 640081 | BELDEN 8 | 69 | 3.8696 | 3.8698 | 0.0002
GEN-2017-222 | 01 NORTH | 640126 | E.COL. 4 | 230 | 10.4381 | 10.4389 | 0.0008
GEN-2017-222 | 01 NORTH | 640131 | COLMB.W4 | 230 | 10.203 | 10.2037 | 0.0007
GEN-2017-222 | 01 NORTH | 640133 | COLMBUS4 | 230 | 11.8933 | 11.8942 | 0.0009
GEN-2017-222 | 01 NORTH | 640134 | KELLY 7 | 115 | 18.4099 | 18.4111 | 0.0012
GEN-2017-222 | 01 NORTH | 640163 | EMERSON7 | 115 | 5.587 | 5.5886 | 0.0016
GEN-2017-222 | 01 NORTH | 640164 | EMERSONG | 69 | 3.9035 | 3.904 | 0.0005
GEN-2017-222 | 01 NORTH | 640212 | HARTGTN7 | 115 | 5.4667 | 5.4672 | 0.0005
GEN-2017-222 | 01 NORTH | 640213 | HARTGTN8 | 69 | 3.6807 | 3.6808 | 0.0001
GEN-2017-222 | 01 NORTH | 640226 | HOSKINS3 | 345 | 11.2326 | 11.237 | 0.0044
GEN-2017-222 | 01 NORTH | 640227 | HOSKINS4 | 230 | 9.3632 | 9.3667 | 0.0035
GEN-2017-222 | 01 NORTH | 640228 | HOSKINS7 | 115 | 17.4868 | 17.4912 | 0.0044
GEN-2017-222 | 01 NORTH | 640305 | ONEILL 7 | 115 | 4.0423 | 4.0424 | 0.0001
GEN-2017-222 | 01 NORTH | 640306 | ONEILL 8 | 69 | 4.3906 | 4.3906 | 0
GEN-2017-222 | 01 NORTH | 640343 | SHELCRK4 | 230 | 11.1695 | 11.1704 | 0.0009
GEN-2017-222 | 01 NORTH | 640349 | SPENCER7 | 115 | 4.7413 | 4.7415 | 0.0002
GEN-2017-222 | 01 NORTH | 640386 | TWIN CH4 | 230 | 8.2999 | 8.3119 | 0.012
GEN-2017-222 | 01 NORTH | 640387 | TWIN CH7 | 115 | 10.6381 | 10.6461 | 0.008
GEN-2017-222 | 01 NORTH | 640388 | TWIN CH8 | 69 | 7.9531 | 7.9558 | 0.0027
GEN-2017-222 | 01 NORTH | 640424 | S.SIOUXCITY7 | 115 | 7.4135 | 7.4174 | 0.0039
GEN-2017-222 | 01 NORTH | 640425 | S.SIOUXCITY8 | 69 | 4.6476 | 4.6485 | 0.0009
GEN-2017-222 | 01 NORTH | 640540 | MEADOWGROVE4 | 230 | 5.7685 | 5.7687 | 0.0002
GEN-2017-222 | 01 NORTH | 640560 | WAKEFIELD 4 | 230 | 6.4096 | 6.4143 | 0.0047
GEN-2017-222 | 01 NORTH | 640561 | RTLSNAKE.W 4 | 230 | 5.4652 | 5.4687 | 0.0035
GEN-2017-222 | 01 NORTH | 640588 | TURTLE.CRK 3 | 345 | 9.7442 | 9.7474 | 0.0032
GEN-2017-222 | 01 NORTH | 640589 | SHOLES.W 3 | 345 | 8.3074 | 8.3096 | 0.0022
GEN-2017-222 | 01 NORTH | 643271 | PLUMBCR.W 3 | 345 | 9.5607 | 9.5638 | 0.0031
GEN-2017-222 | 01 NORTH | 645451 | S3451 3 | 345 | 21.4697 | 21.4741 | 0.0044
GEN-2017-222 | 01 NORTH | 648506 | PR BRZ 4 | 230 | 4.321 | 4.3211 | 0.0001
GEN-2017-222 | 01 NORTH | 652249 | ARMOUR 8 | 69 | 2.5564 | 2.5565 | 0.0001
GEN-2017-222 | 01 NORTH | 652251 | MTVERNS8 | 69 | 2.3833 | 2.3834 | 0.0001
GEN-2017-222 | 01 NORTH | 652276 | FTTHOMP8 | 69 | 4.6193 | 4.6193 | 0
GEN-2017-222 | 01 NORTH | 652284 | HURON 8 | 69 | 3.8243 | 3.8243 | 0
GEN-2017-222 | 01 NORTH | 652286 | TYNDALL8 | 69 | 2.6171 | 2.6171 | 0
GEN-2017-222 | 01 NORTH | 652398 | VFODNES4 | 230 | 7.2074 | 7.209 | 0.0016
GEN-2017-222 | 01 NORTH | 652475 | BONESTL7 | 115 | 3.6389 | 3.639 | 0.0001
GEN-2017-222 | 01 NORTH | 652478 | GREGORY7 | 115 | 2.2215 | 2.2215 | 0
GEN-2017-222 | 01 NORTH | 652501 | ARMOUR 7 | 115 | 4.3539 | 4.354 | 0.0001
GEN-2017-222 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 9.1889 | 9.1891 | 0.0002
GEN-2017-222 | 01 NORTH | 652507 | FTTHOMP4 | 230 | 20.2449 | 20.2458 | 0.0009
GEN-2017-222 | 01 NORTH | 652509 | FTRANDL4 | 230 | 11.1378 | 11.1403 | 0.0025
GEN-2017-222 | 01 NORTH | 652510 | FTRANDL7 | 115 | 12.8726 | 12.8738 | 0.0012
GEN-2017-222 | 01 NORTH | 652514 | HURON 4 | 230 | 11.5155 | 11.5157 | 0.0002
GEN-2017-222 | 01 NORTH | 652515 | HURON 7 | 115 | 15.6154 | 15.6155 | 0.0001
GEN-2017-222 | 01 NORTH | 652518 | MTVERN 7 | 115 | 4.6188 | 4.6189 | 0.0001
GEN-2017-222 | 01 NORTH | 652519 | OAHE 4 | 230 | 13.5686 | 13.5688 | 0.0002
GEN-2017-222 | 01 NORTH | 652520 | OAHE 7 | 115 | 11.2928 | 11.2929 | 0.0001
GEN-2017-222 | 01 NORTH | 652523 | SIOUXFL4 | 230 | 13.7228 | 13.728 | 0.0052
GEN-2017-222 | 01 NORTH | 652525 | TYNDALL7 | 115 | 3.9528 | 3.953 | 0.0002
GEN-2017-222 | 01 NORTH | 652526 | UTICAJC4 | 230 | 8.6169 | 8.6204 | 0.0035
GEN-2017-222 | 01 NORTH | 652530 | WATERTN4 | 230 | 15.1602 | 15.1604 | 0.0002
GEN-2017-222 | 01 NORTH | 652540 | BIGBND14 | 230 | 12.2713 | 12.2716 | 0.0003
GEN-2017-222 | 01 NORTH | 652541 | BIGBND24 | 230 | 12.1896 | 12.1899 | 0.0003
GEN-2017-222 | 01 NORTH | 652552 | SIOUXCY2 | 230 | 20.0452 | 20.1693 | 0.1241
GEN-2017-222 | 01 NORTH | 652560 | CRESTON5 | 161 | 10.3777 | 10.3854 | 0.0077
GEN-2017-222 | 01 NORTH | 652561 | DENISON5 | 161 | 5.9108 | 6.2426 | 0.3318
GEN-2017-222 | 01 NORTH | 652563 | SPENCER5 | 161 | 9.9522 | 9.9539 | 0.0017
GEN-2017-222 | 01 NORTH | 652564 | SIOUXCY3 | 345 | 15.3171 | 15.3583 | 0.0412
GEN-2017-222 | 01 NORTH | 652565 | SIOUXCY4 | 230 | 20.0452 | 20.1693 | 0.1241
GEN-2017-222 | 01 NORTH | 652566 | SIOUXCY5 | 161 | 21.1752 | 21.2374 | 0.0622
GEN-2017-222 | 01 NORTH | 652567 | DENISON4 | 230 | 4.7398 | 5.1178 | 0.378
GEN-2017-222 | 01 NORTH | 652569 | CRESTON8 | 69 | 17.1162 | 17.1228 | 0.0066
GEN-2017-222 | 01 NORTH | 652574 | SIOUXCY8 | 69 | 19.1344 | 19.1561 | 0.0217
GEN-2017-222 | 01 NORTH | 652581 | SPENCER8 | 69 | 15.8691 | 15.8703 | 0.0012
GEN-2017-222 | 01 NORTH | 652583 | DENISON8 | 69 | 11.8723 | 12.3141 | 0.4418
GEN-2017-222 | 01 NORTH | 652603 | EXIRA 5 | 161 | 7.5892 | 7.6469 | 0.0577
GEN-2017-222 | 01 NORTH | 652606 | LETCHER4 | 230 | 4.9252 | 4.9255 | 0.0003
GEN-2017-222 | 01 NORTH | 652607 | WESSINGTON 4 | 230 | 5.8904 | 5.8905 | 0.0001
GEN-2017-222 | 01 NORTH | 652609 | LETCHER7 | 115 | 6.2595 | 6.2597 | 0.0002
GEN-2017-222 | 01 NORTH | 652614 | CARPENTER 4 | 230 | 7.2251 | 7.2252 | 0.0001
GEN-2017-222 | 01 NORTH | 652626 | UTICAJC7 | 115 | 9.1873 | 9.1887 | 0.0014
GEN-2017-222 | 01 NORTH | 652630 | WATERTNCAP 4 | 230 | 14.9806 | 14.9808 | 0.0002
GEN-2017-222 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 9.1237 | 9.1239 | 0.0002
GEN-2017-222 | 01 NORTH | 652807 | FTTHOM2-LNX3 | 345 | 9.1889 | 9.1891 | 0.0002
GEN-2017-222 | 01 NORTH | 652864 | SIOUXCY-LNX3 | 345 | 15.1439 | 15.1839 | 0.04
GEN-2017-222 | 01 NORTH | 654454 | PRVLNG13 | 115 | 4.4698 | 4.47 | 0.0002
GEN-2017-222 | 01 NORTH | 654455 | PRVLNG23 | 115 | 7.1051 | 7.106 | 0.0009
GEN-2017-222 | 01 NORTH | 654457 | PRVLNG16 | 230 | 8.5641 | 8.5676 | 0.0035
GEN-2017-222 | 01 NORTH | 655031 | MOS-LTCH-ER8 | 69 | 1.5674 | 1.5674 | 0
GEN-2017-222 | 01 NORTH | 655032 | MOS-PLNO-ER8 | 69 | 1.0248 | 1.0248 | 0
GEN-2017-222 | 01 NORTH | 655033 | SW-EMERY-ER8 | 69 | 0.8175 | 0.8175 | 0
GEN-2017-222 | 01 NORTH | 655053 | MOS-MILR-ER8 | 69 | 2.4858 | 2.4858 | 0
GEN-2017-222 | 01 NORTH | 655055 | SW-YALE-ER8 | 69 | 1.2326 | 1.2326 | 0
GEN-2017-222 | 01 NORTH | 655056 | SW-WILLO-ER8 | 69 | 1.6334 | 1.6334 | 0
GEN-2017-222 | 01 NORTH | 655058 | MOS-HRON-ER8 | 69 | 2.7567 | 2.7567 | 0
GEN-2017-222 | 01 NORTH | 655060 | MOS-POLO-ER8 | 69 | 1.0183 | 1.0183 | 0
GEN-2017-222 | 01 NORTH | 655062 | MOS-YALE-ER8 | 69 | 1.4658 | 1.4658 | 0
GEN-2017-222 | 01 NORTH | 655063 | SW-HURN1-ER8 | 69 | 3.769 | 3.769 | 0
GEN-2017-222 | 01 NORTH | 655064 | SW-HURN4-ER8 | 69 | 3.7435 | 3.7435 | 0
GEN-2017-222 | 01 NORTH | 655065 | MOS-YLTI-ER8 | 69 | 1.7047 | 1.7047 | 0
GEN-2017-222 | 01 NORTH | 655066 | SW-HURN2-ER8 | 69 | 3.8082 | 3.8082 | 0
GEN-2017-222 | 01 NORTH | 655067 | SW-HURN3-ER8 | 69 | 3.8122 | 3.8122 | 0
GEN-2017-222 | 01 NORTH | 655069 | MOS-WOLS-ER8 | 69 | 2.2717 | 2.2717 | 0
GEN-2017-222 | 01 NORTH | 655070 | MOS-VRCV-ER8 | 69 | 1.2527 | 1.2527 | 0
GEN-2017-222 | 01 NORTH | 655071 | MOS-DAK-ER8 | 69 | 1.0692 | 1.0692 | 0
GEN-2017-222 | 01 NORTH | 655073 | MOS-CRPN-ER8 | 69 | 2.5535 | 2.5535 | 0
GEN-2017-222 | 01 NORTH | 655074 | SW401-ER8 | 69 | 1.544 | 1.544 | 0
GEN-2017-222 | 01 NORTH | 655075 | MOS-WHTL-ER8 | 69 | 1.0121 | 1.0121 | 0
GEN-2017-222 | 01 NORTH | 655076 | MOS-PLAT-ER8 | 69 | 1.4994 | 1.4994 | 0
GEN-2017-222 | 01 NORTH | 655077 | SW-STORL-ER8 | 69 | 1.8998 | 1.8999 | 0.0001
GEN-2017-222 | 01 NORTH | 655078 | SW412-ER8 | 69 | 0.8316 | 0.8316 | 0
GEN-2017-222 | 01 NORTH | 655079 | MOS-KLKP-ER8 | 69 | 0.8061 | 0.8061 | 0
GEN-2017-222 | 01 NORTH | 655080 | MOS-HLTP-ER8 | 69 | 1.3703 | 1.3703 | 0
GEN-2017-222 | 01 NORTH | 655081 | MOS-KMBL-ER8 | 69 | 0.7459 | 0.7459 | 0
GEN-2017-222 | 01 NORTH | 655091 | MOS-AMR1-ER8 | 69 | 2.2631 | 2.2631 | 0
GEN-2017-222 | 01 NORTH | 655092 | MOS-TRIP-ER8 | 69 | 2.1507 | 2.1507 | 0
GEN-2017-222 | 01 NORTH | 655093 | SW-HARSN-ER8 | 69 | 1.0891 | 1.0891 | 0
GEN-2017-222 | 01 NORTH | 655094 | MOS-PRKS-ER8 | 69 | 1.5947 | 1.5947 | 0
GEN-2017-222 | 01 NORTH | 655095 | MOS-TABR-ER8 | 69 | 1.819 | 1.819 | 0
GEN-2017-222 | 01 NORTH | 655096 | SW-TRIPP-ER8 | 69 | 1.2139 | 1.214 | 0.0001
GEN-2017-222 | 01 NORTH | 655097 | SW616-ER8 | 69 | 1.4678 | 1.4678 | 0
GEN-2017-222 | 01 NORTH | 655098 | SW-GEDES-ER8 | 69 | 1.3716 | 1.3716 | 0
GEN-2017-222 | 01 NORTH | 655099 | SW-HILLS-ER8 | 69 | 1.2548 | 1.2548 | 0
GEN-2017-222 | 01 NORTH | 655100 | MOS-WVLN-ER8 | 69 | 1.3613 | 1.3613 | 0
GEN-2017-222 | 01 NORTH | 655101 | MOS-TND1-ER8 | 69 | 2.6141 | 2.6141 | 0
GEN-2017-222 | 01 NORTH | 655102 | MOS-AVON-ER8 | 69 | 2.6028 | 2.6028 | 0
GEN-2017-222 | 01 NORTH | 655103 | PARKSTON-ER8 | 69 | 0.9813 | 0.9813 | 0
GEN-2017-222 | 01 NORTH | 655104 | MOS-NTRP-ER8 | 69 | 1.2275 | 1.2275 | 0
GEN-2017-222 | 01 NORTH | 655106 | SW640-ER8 | 69 | 0.7923 | 0.7923 | 0
GEN-2017-222 | 01 NORTH | 655126 | MOS-VERM-ER8 | 69 | 2.022 | 2.0223 | 0.0003
GEN-2017-222 | 01 NORTH | 655129 | SW806-ER8 | 69 | 0.879 | 0.879 | 0
GEN-2017-222 | 01 NORTH | 655130 | SW808-ER8 | 69 | 2.5415 | 2.5418 | 0.0003
GEN-2017-222 | 01 NORTH | 655133 | SW822-ER8 | 69 | 2.1962 | 2.1964 | 0.0002
GEN-2017-222 | 01 NORTH | 655136 | SW832-ER8 | 69 | 2.6239 | 2.6243 | 0.0004
GEN-2017-222 | 01 NORTH | 655137 | SW833-ER8 | 69 | 2.0949 | 2.0951 | 0.0002
GEN-2017-222 | 01 NORTH | 655145 | SW870-ER8 | 69 | 2.8899 | 2.8903 | 0.0004
GEN-2017-222 | 01 NORTH | 655146 | SW873-ER8 | 69 | 2.8886 | 2.889 | 0.0004
GEN-2017-222 | 01 NORTH | 655147 | MOS-JEFF-ER8 | 69 | 2.5422 | 2.5425 | 0.0003
GEN-2017-222 | 01 NORTH | 655151 | MOS-BGSP-ER8 | 69 | 1.365 | 1.3651 | 0.0001
GEN-2017-222 | 01 NORTH | 655152 | SW894-ER8 | 69 | 2.0678 | 2.068 | 0.0002
GEN-2017-222 | 01 NORTH | 655153 | MOS-AMES-ER8 | 69 | 4.5572 | 4.5572 | 0
GEN-2017-222 | 01 NORTH | 655155 | MOS-SLY1-ER8 | 69 | 2.4637 | 2.4637 | 0
GEN-2017-222 | 01 NORTH | 655158 | MOS-HYDE-ER8 | 69 | 3.6178 | 3.6178 | 0
GEN-2017-222 | 01 NORTH | 655183 | MITCHELL-ER8 | 69 | 1.2318 | 1.2318 | 0
GEN-2017-222 | 01 NORTH | 655189 | FARMER-ER8 | 69 | 0.8353 | 0.8353 | 0
GEN-2017-222 | 01 NORTH | 655193 | MTVERNON-ER8 | 69 | 1.8876 | 1.8876 | 0
GEN-2017-222 | 01 NORTH | 655205 | PLANO-ER8 | 69 | 0.8713 | 0.8713 | 0
GEN-2017-222 | 01 NORTH | 655206 | EMERY-ER8 | 69 | 0.729 | 0.729 | 0
GEN-2017-222 | 01 NORTH | 655211 | DESMET-ER8 | 69 | 1.0999 | 1.0999 | 0
GEN-2017-222 | 01 NORTH | 655228 | YALE-ER8 | 69 | 1.2138 | 1.2138 | 0
GEN-2017-222 | 01 NORTH | 655229 | WILLOWLK-ER8 | 69 | 1.1938 | 1.1938 | 0
GEN-2017-222 | 01 NORTH | 655231 | HURON-ER8 | 69 | 2.7536 | 2.7536 | 0
GEN-2017-222 | 01 NORTH | 655233 | POLO-ER8 | 69 | 0.6487 | 0.6487 | 0
GEN-2017-222 | 01 NORTH | 655234 | MILLER-ER8 | 69 | 1.0262 | 1.0262 | 0
GEN-2017-222 | 01 NORTH | 655236 | MORNINGS-ER8 | 69 | 1.9501 | 1.9501 | 0
GEN-2017-222 | 01 NORTH | 655237 | BONILLA-ER8 | 69 | 1.677 | 1.6771 | 0.0001
GEN-2017-222 | 01 NORTH | 655239 | WOLSEY-ER8 | 69 | 1.3491 | 1.3491 | 0
GEN-2017-222 | 01 NORTH | 655240 | HGHMORE-ER8 | 69 | 2.2442 | 2.2442 | 0
GEN-2017-222 | 01 NORTH | 655241 | VIRGIL-ER8 | 69 | 1.8815 | 1.8815 | 0
GEN-2017-222 | 01 NORTH | 655242 | CAVOUR-ER8 | 69 | 1.2043 | 1.2043 | 0
GEN-2017-222 | 01 NORTH | 655244 | DAKOTA-ER8 | 69 | 0.994 | 0.994 | 0
GEN-2017-222 | 01 NORTH | 655247 | PLANKCTY-ER8 | 69 | 1.5776 | 1.5777 | 0.0001
GEN-2017-222 | 01 NORTH | 655248 | STORLA-ER8 | 69 | 1.0753 | 1.0753 | 0
GEN-2017-222 | 01 NORTH | 655249 | WILBUR-ER8 | 69 | 0.8066 | 0.8066 | 0
GEN-2017-222 | 01 NORTH | 655250 | CHMBRLAN-ER8 | 69 | 1.6588 | 1.6588 | 0
GEN-2017-222 | 01 NORTH | 655251 | PLATTE-ER8 | 69 | 2.1763 | 2.1763 | 0
GEN-2017-222 | 01 NORTH | 655252 | RIVERVW-ER8 | 69 | 1.5258 | 1.5258 | 0
GEN-2017-222 | 01 NORTH | 655253 | PUKWANA-ER8 | 69 | 1.1639 | 1.1639 | 0
GEN-2017-222 | 01 NORTH | 655254 | HILLTOP-ER8 | 69 | 1.1673 | 1.1673 | 0
GEN-2017-222 | 01 NORTH | 655255 | KIMBALL-ER8 | 69 | 0.6982 | 0.6982 | 0
GEN-2017-222 | 01 NORTH | 655271 | WAGNER-ER8 | 69 | 1.3159 | 1.3159 | 0
GEN-2017-222 | 01 NORTH | 655272 | TYNDALL-ER8 | 69 | 2.6096 | 2.6097 | 0.0001
GEN-2017-222 | 01 NORTH | 655273 | ARMOUR-ER8 | 69 | 2.1636 | 2.1637 | 0.0001
GEN-2017-222 | 01 NORTH | 655274 | HARRISON-ER8 | 69 | 1.0768 | 1.0768 | 0
GEN-2017-222 | 01 NORTH | 655275 | TABOR-ER8 | 69 | 1.532 | 1.532 | 0
GEN-2017-222 | 01 NORTH | 655276 | UTICA-ER8 | 69 | 1.1918 | 1.1918 | 0
GEN-2017-222 | 01 NORTH | 655277 | GEDDES-ER8 | 69 | 0.9683 | 0.9683 | 0
GEN-2017-222 | 01 NORTH | 655278 | HILLSIDE-ER8 | 69 | 1.203 | 1.203 | 0
GEN-2017-222 | 01 NORTH | 655279 | GAVINSPT-ER8 | 69 | 1.1328 | 1.1328 | 0
GEN-2017-222 | 01 NORTH | 655280 | AVON-ER8 | 69 | 1.6514 | 1.6514 | 0
GEN-2017-222 | 01 NORTH | 655281 | SPRNGFLD-ER8 | 69 | 1.7842 | 1.7842 | 0
GEN-2017-222 | 01 NORTH | 655282 | TRIPP-ER8 | 69 | 1.1509 | 1.1509 | 0
GEN-2017-222 | 01 NORTH | 655283 | MENNO-ER8 | 69 | 0.8823 | 0.8823 | 0
GEN-2017-222 | 01 NORTH | 655284 | TRKYRDGE-ER8 | 69 | 0.7794 | 0.7794 | 0
GEN-2017-222 | 01 NORTH | 655285 | BYWATER-ER8 | 69 | 1.2846 | 1.2846 | 0
GEN-2017-222 | 01 NORTH | 655308 | ALCESTER-ER8 | 69 | 1.0265 | 1.0266 | 0.0001
GEN-2017-222 | 01 NORTH | 655311 | AKRON-ER8 | 69 | 1.5315 | 1.5316 | 0.0001
GEN-2017-222 | 01 NORTH | 655313 | RICHLAND-ER8 | 69 | 2.5331 | 2.5335 | 0.0004
GEN-2017-222 | 01 NORTH | 655314 | ELKPNTCY-ER8 | 69 | 1.939 | 1.9392 | 0.0002
GEN-2017-222 | 01 NORTH | 655315 | ELKPOINT-ER8 | 69 | 1.9382 | 1.9384 | 0.0002
GEN-2017-222 | 01 NORTH | 655316 | BURBANK-ER8 | 69 | 1.8809 | 1.8811 | 0.0002
GEN-2017-222 | 01 NORTH | 655326 | BGSPRING-ER8 | 69 | 1.1811 | 1.1811 | 0
GEN-2017-222 | 01 NORTH | 655327 | UNIONCRK-ER8 | 69 | 2.002 | 2.0022 | 0.0002
GEN-2017-222 | 01 NORTH | 655328 | BIGBEND-ER8 | 69 | 3.3818 | 3.3818 | 0
GEN-2017-222 | 01 NORTH | 655329 | GANNVALL-ER8 | 69 | 0.9053 | 0.9053 | 0
GEN-2017-222 | 01 NORTH | 655332 | LOGAN-ER8 | 69 | 1.1456 | 1.1456 | 0
GEN-2017-222 | 01 NORTH | 655333 | ONIDA-ER8 | 69 | 1.5822 | 1.5822 | 0
GEN-2017-222 | 01 NORTH | 655334 | OKOBOJO-ER8 | 69 | 2.4672 | 2.4672 | 0
GEN-2017-222 | 01 NORTH | 655352 | AMES-ER8 | 69 | 1.4036 | 1.4036 | 0
GEN-2017-222 | 01 NORTH | 655359 | JEFERSON-ER8 | 69 | 1.6883 | 1.6885 | 0.0002
GEN-2017-222 | 01 NORTH | 655362 | LINCOLN-ER7 | 115 | 3.3298 | 3.33 | 0.0002
GEN-2017-222 | 01 NORTH | 655372 | LOGANSUB-ER8 | 69 | 1.145 | 1.145 | 0
GEN-2017-222 | 01 NORTH | 655373 | MOS-SLY2-ER8 | 69 | 2.4741 | 2.4741 | 0
GEN-2017-222 | 01 NORTH | 655374 | MOS-TND2-ER8 | 69 | 2.6134 | 2.6135 | 0.0001
GEN-2017-222 | 01 NORTH | 655375 | MOS-WGNR-ER8 | 69 | 1.3165 | 1.3165 | 0
GEN-2017-222 | 01 NORTH | 655376 | MOS-AMR2-ER8 | 69 | 2.3463 | 2.3463 | 0
GEN-2017-222 | 01 NORTH | 655378 | NWPS3680-ER8 | 69 | 1.0436 | 1.0436 | 0
GEN-2017-222 | 01 NORTH | 655384 | NWPS8645-ER8 | 69 | 2.284 | 2.284 | 0
GEN-2017-222 | 01 NORTH | 655385 | MOS-LKPL-ER8 | 69 | 4.1908 | 4.1909 | 0.0001
GEN-2017-222 | 01 NORTH | 655386 | MOS-RVR1-ER8 | 69 | 2.1875 | 2.1875 | 0
GEN-2017-222 | 01 NORTH | 655387 | MOS-RVR2-ER8 | 69 | 2.1769 | 2.1769 | 0
GEN-2017-222 | 01 NORTH | 655388 | NWPS7632-ER8 | 69 | 1.5718 | 1.5719 | 0.0001
GEN-2017-222 | 01 NORTH | 655393 | SWR5123-ER8 | 69 | 0.9791 | 0.9791 | 0
GEN-2017-222 | 01 NORTH | 655394 | SW425-ER8 | 69 | 1.3148 | 1.3148 | 0
GEN-2017-222 | 01 NORTH | 655404 | HRRISBRG-ER7 | 115 | 3.3537 | 3.3538 | 0.0001
GEN-2017-222 | 01 NORTH | 655405 | SHINDLER-ER7 | 115 | 2.8529 | 2.853 | 0.0001
GEN-2017-222 | 01 NORTH | 655406 | 6MILE RD-ER7 | 115 | 2.671 | 2.6711 | 0.0001
GEN-2017-222 | 01 NORTH | 655408 | SXFCHCLR-ER7 | 115 | 3.4359 | 3.4361 | 0.0002
GEN-2017-222 | 01 NORTH | 655410 | SYCAMORE-ER7 | 115 | 3.0672 | 3.0673 | 0.0001
GEN-2017-222 | 01 NORTH | 655412 | CRPNTR-ER8 | 69 | 2.9541 | 2.9541 | 0
GEN-2017-222 | 01 NORTH | 655417 | ROSWELL-ER7 | 115 | 2.7188 | 2.7188 | 0
GEN-2017-222 | 01 NORTH | 655418 | FREEMAN-ER7 | 115 | 2.687 | 2.6872 | 0.0002
GEN-2017-222 | 01 NORTH | 655423 | GREYGOOS-ER8 | 69 | 1.58 | 1.58 | 0
GEN-2017-222 | 01 NORTH | 655425 | MOS-BYWT-ER8 | 69 | 1.2846 | 1.2846 | 0
GEN-2017-222 | 01 NORTH | 655426 | MOS-GVPT-ER8 | 69 | 1.2049 | 1.2049 | 0
GEN-2017-222 | 01 NORTH | 655427 | MOS-ALC2-ER8 | 69 | 1.0265 | 1.0266 | 0.0001
GEN-2017-222 | 01 NORTH | 655428 | BIGSPRGS-ER8 | 69 | 1.1811 | 1.1811 | 0
GEN-2017-222 | 01 NORTH | 655439 | SXFALLS-ER7 | 115 | 3.3579 | 3.3581 | 0.0002
GEN-2017-222 | 01 NORTH | 655440 | MARIONRD-ER7 | 115 | 2.5575 | 2.5576 | 0.0001
GEN-2017-222 | 01 NORTH | 655441 | BUCKSNRT-ER7 | 115 | 3.9509 | 3.9512 | 0.0003
GEN-2017-222 | 01 NORTH | 655444 | DELAPRE-ER7 | 115 | 3.6483 | 3.6485 | 0.0002
GEN-2017-222 | 01 NORTH | 655445 | SUNDOWN-ER7 | 115 | 3.7599 | 3.7601 | 0.0002
GEN-2017-222 | 01 NORTH | 655446 | SW1109-ER7 | 115 | 3.8181 | 3.8183 | 0.0002
GEN-2017-222 | 01 NORTH | 655448 | WILOWCRK-ER7 | 115 | 3.4663 | 3.4664 | 0.0001
GEN-2017-222 | 01 NORTH | 655450 | MOS-ELIS-ER7 | 115 | 3.0864 | 3.0866 | 0.0002
GEN-2017-222 | 01 NORTH | 655452 | MOS-MRRD-ER7 | 115 | 2.9032 | 2.9033 | 0.0001
GEN-2017-222 | 01 NORTH | 655468 | VFODNES-ER7 | 115 | 5.1735 | 5.1739 | 0.0004
GEN-2017-222 | 01 NORTH | 655469 | VFODNES-ER8 | 69 | 4.3941 | 4.3942 | 0.0001
GEN-2017-222 | 01 NORTH | 655475 | LAKPLAT-ER4 | 230 | 5.8154 | 5.8157 | 0.0003
GEN-2017-222 | 01 NORTH | 655476 | LAKPLAT-ER8 | 69 | 4.2061 | 4.2061 | 0
GEN-2017-222 | 01 NORTH | 655484 | RASMUSN-ER4 | 230 | 6.9447 | 6.9537 | 0.009
GEN-2017-222 | 01 NORTH | 655485 | RASMUSN-ER8 | 69 | 3.32 | 3.3206 | 0.0006
GEN-2017-222 | 01 NORTH | 655487 | SULLYBT-ER4 | 230 | 6.3742 | 6.3742 | 0
GEN-2017-222 | 01 NORTH | 655488 | SULLYBT-ER8 | 69 | 2.4779 | 2.4779 | 0
GEN-2017-222 | 01 NORTH | 655490 | WHTSWAN-ER7 | 115 | 12.5559 | 12.5571 | 0.0012
GEN-2017-222 | 01 NORTH | 655499 | CARPENTR-ER8 | 69 | 3.3312 | 3.3312 | 0
GEN-2017-222 | 01 NORTH | 655504 | YANKTON-ER8 | 69 | 1.2584 | 1.2584 | 0
GEN-2017-222 | 01 NORTH | 655505 | SW660-ER8 | 69 | 1.3058 | 1.3059 | 0.0001
GEN-2017-222 | 01 NORTH | 655506 | SXFALLS2-ER7 | 115 | 3.506 | 3.5062 | 0.0002
GEN-2017-222 | 01 NORTH | 655509 | SW-MILRC-ER8 | 69 | 1.0555 | 1.0555 | 0
GEN-2017-222 | 01 NORTH | 655518 | DAYTON__-ER7 | 115 | 3.6109 | 3.6111 | 0.0002
GEN-2017-222 | 01 NORTH | 656233 | CAROLTON8 | 69 | 5.2115 | 5.2167 | 0.0052
GEN-2017-222 | 01 NORTH | 656237 | COONRPDS G | 69 | 3.223 | 3.2248 | 0.0018
GEN-2017-222 | 01 NORTH | 656243 | TCE8 | 69 | 2.5152 | 2.5163 | 0.0011
GEN-2017-222 | 01 NORTH | 656245 | TCE TAP8 | 69 | 3.0731 | 3.0748 | 0.0017
GEN-2017-222 | 01 NORTH | 656247 | TEMPLTON8 | 69 | 6.3185 | 6.3337 | 0.0152
GEN-2017-222 | 01 NORTH | 656249 | TOYNE8 | 69 | 6.9026 | 6.9179 | 0.0153
GEN-2017-222 | 01 NORTH | 656267 | MANNINGTAP 8 | 69 | 4.6445 | 4.6676 | 0.0231
GEN-2017-222 | 01 NORTH | 656527 | OSGOOD5 | 161 | 5.9649 | 5.9652 | 0.0003
GEN-2017-222 | 01 NORTH | 656555 | SPNCRSJCT8 | 69 | 9.395 | 9.3953 | 0.0003
GEN-2017-222 | 01 NORTH | 656570 | WISDOM5 | 161 | 10.1232 | 10.125 | 0.0018
GEN-2017-222 | 01 NORTH | 656573 | WISDOM G | 69 | 16.0192 | 16.0202 | 0.001
GEN-2017-222 | 01 NORTH | 658030 | DENISONWEST8 | 69 | 6.8053 | 6.9495 | 0.1442
GEN-2017-222 | 01 NORTH | 658031 | DENSOUMAIN8 | 69 | 6.9679 | 7.119 | 0.1511
GEN-2017-222 | 01 NORTH | 658122 | ROCKRPDMUNI8 | 69 | 2.8456 | 2.8458 | 0.0002
GEN-2017-222 | 01 NORTH | 658124 | LUVERNEMUNW8 | 69 | 1.8255 | 1.8256 | 0.0001
GEN-2017-222 | 01 NORTH | 658126 | LUVERNEMUNE8 | 69 | 1.7283 | 1.7284 | 0.0001
GEN-2017-222 | 01 NORTH | 658128 | LUVERNEMUNS8 | 69 | 1.8312 | 1.8313 | 0.0001
GEN-2017-222 | 01 NORTH | 658130 | LAKEPARKMUN8 | 69 | 1.6751 | 1.6751 | 0
GEN-2017-222 | 01 NORTH | 659122 | STORLA__-BE4 | 230 | 5.5764 | 5.5766 | 0.0002
GEN-2017-222 | 01 NORTH | 659188 | PHILIP_T-BE4 | 230 | 5.616 | 5.616 | 0
GEN-2017-222 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.4441 | 10.4442 | 0.0001
GEN-2017-222 | 01 NORTH | 659295 | SD.PW1__-BE4 | 230 | 4.5824 | 4.5825 | 0.0001
GEN-2017-222 | 01 NORTH | 659311 | PAHOJA__-BE4 | 230 | 7.6367 | 7.6408 | 0.0041
GEN-2017-222 | 01 NORTH | 659700 | LAKPRKTP-LO8 | 69 | 2.1321 | 2.1321 | 0
GEN-2017-222 | 01 NORTH | 659702 | ALLISNTP-LO8 | 69 | 1.6564 | 1.6564 | 0
GEN-2017-222 | 01 NORTH | 659703 | ALLISON -LO8 | 69 | 1.5612 | 1.5612 | 0
GEN-2017-222 | 01 NORTH | 659704 | MAYCITY -LO8 | 69 | 1.597 | 1.597 | 0
GEN-2017-222 | 01 NORTH | 659705 | ALLDRFTP-LO8 | 69 | 1.2721 | 1.2721 | 0
GEN-2017-222 | 01 NORTH | 659706 | ALLENDRF-LO8 | 69 | 1.2542 | 1.2542 | 0
GEN-2017-222 | 01 NORTH | 659707 | SIBLEY -LO8 | 69 | 1.0781 | 1.0782 | 0.0001
GEN-2017-222 | 01 NORTH | 659708 | LITLRCKT-LO8 | 69 | 1.9725 | 1.9726 | 0.0001
GEN-2017-222 | 01 NORTH | 659709 | LITLRCK -LO8 | 69 | 1.9316 | 1.9316 | 0
GEN-2017-222 | 01 NORTH | 659710 | GEORGETP-LO8 | 69 | 2.3896 | 2.3897 | 0.0001
GEN-2017-222 | 01 NORTH | 659711 | GEORGE -LO8 | 69 | 2.3278 | 2.3279 | 0.0001
GEN-2017-222 | 01 NORTH | 659712 | RKRMUNTP-LO8 | 69 | 3.3894 | 3.3897 | 0.0003
GEN-2017-222 | 01 NORTH | 659714 | RKRPDTAP-LO8 | 69 | 3.6039 | 3.6042 | 0.0003
GEN-2017-222 | 01 NORTH | 659715 | ROCKRPDS-LO8 | 69 | 3.4476 | 3.4479 | 0.0003
GEN-2017-222 | 01 NORTH | 659726 | STEEN -LO8 | 69 | 2.3474 | 2.3476 | 0.0002
GEN-2017-222 | 01 NORTH | 659727 | LUVERNE -LO8 | 69 | 1.8645 | 1.8646 | 0.0001
GEN-2017-222 | 01 NORTH | 659735 | CLEVELND-LO4 | 230 | 5.0982 | 5.1 | 0.0018
GEN-2017-222 | 01 NORTH | 659736 | CLEVELND-LO8 | 69 | 4.4441 | 4.4445 | 0.0004
GEN-2017-222 | 01 NORTH | 659852 | K126MEC -NI8 | 69 | 3.9368 | 3.9478 | 0.011
GEN-2017-222 | 01 NORTH | 659853 | K125DUNL-NI8 | 69 | 4.0559 | 4.0689 | 0.013
GEN-2017-222 | 01 NORTH | 659854 | K335AMAI-NI8 | 69 | 9.0558 | 9.2313 | 0.1755
GEN-2017-222 | 01 NORTH | 659855 | K318MEC -NI8 | 69 | 5.3373 | 5.3833 | 0.046
GEN-2017-222 | 01 NORTH | 659862 | K307DENI-NI8 | 69 | 6.6399 | 6.7289 | 0.089
GEN-2017-222 | 01 NORTH | 659863 | K313HALB-NI8 | 69 | 3.7114 | 3.7304 | 0.019
GEN-2017-222 | 01 NORTH | 659867 | K319EWOL-NI8 | 69 | 2.7633 | 2.7713 | 0.008
GEN-2017-222 | 01 NORTH | 659868 | L9 MANNI-NI8 | 69 | 2.6873 | 2.6949 | 0.0076
GEN-2017-222 | 01 NORTH | 659885 | K306SCHL-NI8 | 69 | 4.4162 | 4.4458 | 0.0296
GEN-2017-222 | 01 NORTH | 659886 | K326OTTE-NI8 | 69 | 4.2631 | 4.2895 | 0.0264
GEN-2017-222 | 01 NORTH | 659887 | K333SCHL-NI8 | 69 | 4.1289 | 4.1526 | 0.0237
GEN-2017-222 | 01 NORTH | 659895 | PERRY___-NI8 | 69 | 10.9639 | 10.9702 | 0.0063
GEN-2017-222 | 01 NORTH | 659897 | K338WTCT-NI8 | 69 | 8.6496 | 8.8077 | 0.1581
GEN-2017-222 | 01 NORTH | 659899 | K225ADAV-NI8 | 69 | 6.0018 | 6.0036 | 0.0018
GEN-2017-222 | 01 NORTH | 659900 | EAGLE___-NI4 | 230 | 7.4742 | 7.4823 | 0.0081
GEN-2017-222 | 01 NORTH | 659901 | EAGLE___-NI8 | 69 | 14.3681 | 14.3767 | 0.0086
GEN-2017-222 | 01 NORTH | 659906 | K317MANN-NI8 | 69 | 3.3627 | 3.3745 | 0.0118
GEN-2017-222 | 01 NORTH | 659907 | J1CENTER-NI8 | 69 | 9.7851 | 9.7891 | 0.004
GEN-2017-222 | 01 NORTH | 659912 | J6BOYER_-NI8 | 69 | 10.0749 | 10.2973 | 0.2224
GEN-2017-222 | 01 NORTH | 659918 | J12_____-NI8 | 69 | 5.4271 | 5.4587 | 0.0316
GEN-2017-222 | 01 NORTH | 659921 | J15_____-NI8 | 69 | 6.9164 | 6.9183 | 0.0019
GEN-2017-222 | 01 NORTH | 659942 | K217HWDN-NI8 | 69 | 8.5201 | 8.5232 | 0.0031
GEN-2017-222 | 01 NORTH | 659946 | K216LIBE-NI8 | 69 | 7.8875 | 7.8909 | 0.0034
GEN-2017-222 | 01 NORTH | 659953 | K412HTNM-NI8 | 69 | 12.394 | 12.4032 | 0.0092
GEN-2017-222 | 01 NORTH | 659954 | K401UNIO-NI8 | 69 | 7.7304 | 7.7341 | 0.0037
GEN-2017-222 | 01 NORTH | 659971 | K301HINT-NI8 | 69 | 10.6574 | 10.665 | 0.0076
GEN-2017-222 | 01 NORTH | 659972 | K334KING-NI8 | 69 | 2.9703 | 2.9716 | 0.0013
GEN-2017-222 | 01 NORTH | 659979 | K144LWTN-NI8 | 69 | 6.7685 | 6.7709 | 0.0024
GEN-2017-222 | 01 NORTH | 659980 | K135CONC-NI8 | 69 | 6.9641 | 6.9668 | 0.0027
GEN-2017-222 | 01 NORTH | 659998 | K105UTE_-NI8 | 69 | 4.4626 | 4.4775 | 0.0149
GEN-2017-222 | 01 NORTH | 659999 | K106CHAR-NI8 | 69 | 5.1593 | 5.1866 | 0.0273
GEN-2017-222 | 01 NORTH | 660007 | MENNO JCT 7 | 115 | 6.8127 | 6.8134 | 0.0007
GEN-2017-222 | 01 NORTH | 660026 | NAPA JCT 7 | 115 | 8.3153 | 8.3161 | 0.0008
GEN-2017-222 | 01 NORTH | 660036 | YANKTONEAST7 | 115 | 4.2114 | 4.2116 | 0.0002
GEN-2017-222 | 01 NORTH | 660057 | AURORA CY T | 69 | 2.4507 | 2.4507 | 0
GEN-2017-222 | 01 NORTH | 660067 | BRULE CY T | 69 | 2.1215 | 2.1215 | 0
GEN-2017-222 | 01 NORTH | 660230 | STICKNEY JCT | 69 | 2.7534 | 2.7535 | 0.0001
GEN-2017-222 | 01 NORTH | 660231 | MT.VERNON T | 69 | 3.1697 | 3.1697 | 0
GEN-2017-222 | 01 NORTH | 660232 | MT.VERNON | 69 | 2.838 | 2.838 | 0
GEN-2017-222 | 01 NORTH | 660233 | WHITE LAKE | 69 | 2.4415 | 2.4415 | 0
GEN-2017-222 | 01 NORTH | 660234 | KIMBALL | 69 | 1.864 | 1.864 | 0
GEN-2017-222 | 01 NORTH | 660236 | CHB MO.VIEWT | 69 | 1.0701 | 1.0701 | 0
GEN-2017-222 | 01 NORTH | 660237 | CHB MO.VIEW | 69 | 1.0646 | 1.0646 | 0
GEN-2017-222 | 01 NORTH | 660238 | CHB CITY | 69 | 1.043 | 1.043 | 0
GEN-2017-222 | 01 NORTH | 660252 | MT VERNON 8 | 69 | 3.4162 | 3.4162 | 0
GEN-2017-222 | 01 NORTH | 760515 | GEN-2017-222 | 230 | 3.3236 | 3.7161 | 0.3925
GEN-2017-222 | 01 NORTH | 760788 | GEN-2017-201 | 345 | 7.6496 | 7.6515 | 0.0019
GEN-2017-222 | 01 NORTH | 762237 | G17-175TAP | 230 | 7.0897 | 7.0916 | 0.0019
GEN-2017-222 | 01 NORTH | 762238 | GEN-2017-175 | 230 | 6.8771 | 6.8789 | 0.0018
GEN-2017-105 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 11.301 | 11.3023 | 0.0013
GEN-2017-105 | 02 NEBRASKA | 87487 | J748POI | 345 | 12.489 | 12.4907 | 0.0017
GEN-2017-105 | 02 NEBRASKA | 587150 | GEN-2016-021 | 345 | 9.3359 | 9.3372 | 0.0013
GEN-2017-105 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.3172 | 14.318 | 0.0008
GEN-2017-105 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 26.5485 | 26.5717 | 0.0232
GEN-2017-105 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.6841 | 27.7322 | 0.0481
GEN-2017-105 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.9556 | 22.9865 | 0.0309
GEN-2017-105 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.2062 | 26.2489 | 0.0427
GEN-2017-105 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2145 | 10.2171 | 0.0026
GEN-2017-105 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.4059 | 9.4071 | 0.0012
GEN-2017-105 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.0044 | 9.0054 | 0.001
GEN-2017-105 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.0362 | 15.0477 | 0.0115
GEN-2017-105 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.6807 | 17.6951 | 0.0144
GEN-2017-105 | 02 NEBRASKA | 635223 | PLYMOTH5 | 161 | 21.0587 | 21.07 | 0.0113
GEN-2017-105 | 02 NEBRASKA | 635225 | MORNSD 5 | 161 | 11.2674 | 11.272 | 0.0046
GEN-2017-105 | 02 NEBRASKA | 635226 | LEEDS 5 | 161 | 16.3814 | 16.3916 | 0.0102
GEN-2017-105 | 02 NEBRASKA | 635227 | SBRIDGE T8 | 69 | 8.9229 | 8.9248 | 0.0019
GEN-2017-105 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.5362 | 17.553 | 0.0168
GEN-2017-105 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 25.5271 | 25.5674 | 0.0403
GEN-2017-105 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.1271 | 15.1387 | 0.0116
GEN-2017-105 | 02 NEBRASKA | 635236 | SALIX 8 | 69 | 13.8173 | 13.8208 | 0.0035
GEN-2017-105 | 02 NEBRASKA | 635237 | SLOAN 8 | 69 | 4.9006 | 4.901 | 0.0004
GEN-2017-105 | 02 NEBRASKA | 635240 | STSTEEL8 | 69 | 8.4833 | 8.4847 | 0.0014
GEN-2017-105 | 02 NEBRASKA | 635242 | SC WTRWRKS 8 | 69 | 13.7287 | 13.732 | 0.0033
GEN-2017-105 | 02 NEBRASKA | 635243 | KNOX 8 | 69 | 8.0128 | 8.0143 | 0.0015
GEN-2017-105 | 02 NEBRASKA | 635246 | DIVISON8 | 69 | 15.9066 | 15.911 | 0.0044
GEN-2017-105 | 02 NEBRASKA | 635247 | EASTSID8 | 69 | 14.6756 | 14.6791 | 0.0035
GEN-2017-105 | 02 NEBRASKA | 635249 | LAWTON8 | 69 | 4.8627 | 4.8631 | 0.0004
GEN-2017-105 | 02 NEBRASKA | 635250 | MOVILLE8 | 69 | 2.8491 | 2.8493 | 0.0002
GEN-2017-105 | 02 NEBRASKA | 635251 | KINGS 8 | 69 | 2.0747 | 2.0748 | 0.0001
GEN-2017-105 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.8022 | 9.8037 | 0.0015
GEN-2017-105 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.6971 | 5.698 | 0.0009
GEN-2017-105 | 02 NEBRASKA | 635301 | MONONA 8 | 69 | 4.7232 | 4.7234 | 0.0002
GEN-2017-105 | 02 NEBRASKA | 635302 | MAPLTN 8 | 69 | 3.1825 | 3.1825 | 0
GEN-2017-105 | 02 NEBRASKA | 635303 | SMITHLD8 | 69 | 2.4727 | 2.4727 | 0
GEN-2017-105 | 02 NEBRASKA | 635304 | DANBURY8 | 69 | 4.1548 | 4.1549 | 0.0001
GEN-2017-105 | 02 NEBRASKA | 635310 | VICTORY5 | 161 | 5.2085 | 5.2088 | 0.0003
GEN-2017-105 | 02 NEBRASKA | 635330 | CRWFRD 5 | 161 | 5.0929 | 5.0934 | 0.0005
GEN-2017-105 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 12.5622 | 12.5638 | 0.0016
GEN-2017-105 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 13.1903 | 13.1913 | 0.001
GEN-2017-105 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 12.4053 | 12.4068 | 0.0015
GEN-2017-105 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 8.9352 | 8.9361 | 0.0009
GEN-2017-105 | 02 NEBRASKA | 640070 | BANCRFT7 | 115 | 5.2849 | 5.2936 | 0.0087
GEN-2017-105 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6131 | 4.6182 | 0.0051
GEN-2017-105 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.3608 | 6.3613 | 0.0005
GEN-2017-105 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.9049 | 3.905 | 0.0001
GEN-2017-105 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6727 | 10.6739 | 0.0012
GEN-2017-105 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7144 | 5.7177 | 0.0033
GEN-2017-105 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9402 | 3.9411 | 0.0009
GEN-2017-105 | 02 NEBRASKA | 640173 | FREMONT7 | 115 | 6.3465 | 6.3511 | 0.0046
GEN-2017-105 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.7932 | 13.7966 | 0.0034
GEN-2017-105 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.6356 | 10.6375 | 0.0019
GEN-2017-105 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 19.1627 | 19.1673 | 0.0046
GEN-2017-105 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.9591 | 13.9613 | 0.0022
GEN-2017-105 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 13.0909 | 13.0928 | 0.0019
GEN-2017-105 | 02 NEBRASKA | 640300 | OAKLAND7 | 115 | 7.8964 | 7.9259 | 0.0295
GEN-2017-105 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9491 | 10.9505 | 0.0014
GEN-2017-105 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.5268 | 11.5277 | 0.0009
GEN-2017-105 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.341 | 7.3434 | 0.0024
GEN-2017-105 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.0765 | 9.2762 | 0.1997
GEN-2017-105 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.4997 | 8.5789 | 0.0792
GEN-2017-105 | 02 NEBRASKA | 640400 | W.POINT7 | 115 | 5.2154 | 5.2246 | 0.0092
GEN-2017-105 | 02 NEBRASKA | 640409 | WINSLOW7 | 115 | 5.5971 | 5.606 | 0.0089
GEN-2017-105 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 7.0391 | 7.0398 | 0.0007
GEN-2017-105 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 16.5899 | 16.5908 | 0.0009
GEN-2017-105 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.5032 | 5.5033 | 0.0001
GEN-2017-105 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3534 | 8.3548 | 0.0014
GEN-2017-105 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4599 | 7.4609 | 0.001
GEN-2017-105 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 12.187 | 12.1894 | 0.0024
GEN-2017-105 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.9164 | 9.9179 | 0.0015
GEN-2017-105 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 15.8681 | 15.869 | 0.0009
GEN-2017-105 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.9363 | 11.9385 | 0.0022
GEN-2017-105 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.2897 | 29.3302 | 0.0405
GEN-2017-105 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.5702 | 21.5916 | 0.0214
GEN-2017-105 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.836 | 28.8501 | 0.0141
GEN-2017-105 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 31.9307 | 31.9469 | 0.0162
GEN-2017-105 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.4632 | 34.4808 | 0.0176
GEN-2017-105 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.0623 | 25.0785 | 0.0162
GEN-2017-105 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.882 | 22.8881 | 0.0061
GEN-2017-105 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 46.6913 | 46.7214 | 0.0301
GEN-2017-105 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 24.7646 | 24.8373 | 0.0727
GEN-2017-105 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 33.8479 | 33.8659 | 0.018
GEN-2017-105 | 02 NEBRASKA | 646236 | S1236 5 | 161 | 24.4368 | 24.449 | 0.0122
GEN-2017-105 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 21.8313 | 21.8465 | 0.0152
GEN-2017-105 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 31.7859 | 31.8336 | 0.0477
GEN-2017-105 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 29.6141 | 29.6365 | 0.0224
GEN-2017-105 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 27.4751 | 27.4886 | 0.0135
GEN-2017-105 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.4512 | 32.461 | 0.0098
GEN-2017-105 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1349 | 7.1398 | 0.0049
GEN-2017-105 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 18.9236 | 18.9337 | 0.0101
GEN-2017-105 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 29.0816 | 29.1311 | 0.0495
GEN-2017-105 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 27.681 | 27.7245 | 0.0435
GEN-2017-105 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 26.949 | 26.9887 | 0.0397
GEN-2017-105 | 02 NEBRASKA | 646345 | S1345 5 | 161 | 22.5174 | 22.5319 | 0.0145
GEN-2017-105 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 32.7381 | 32.7578 | 0.0197
GEN-2017-105 | 02 NEBRASKA | 646367 | S1367 5 | 161 | 21.6625 | 21.6738 | 0.0113
GEN-2017-105 | 02 NEBRASKA | 647291 | S991 E 8 | 69 | 12.8006 | 12.8057 | 0.0051
GEN-2017-105 | 02 NEBRASKA | 647422 | FREM B 8 | 69 | 15.2589 | 15.2646 | 0.0057
GEN-2017-105 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.2938 | 21.2967 | 0.0029
GEN-2017-105 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.7674 | 20.7766 | 0.0092
GEN-2017-105 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.6496 | 15.6563 | 0.0067
GEN-2017-105 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.7674 | 20.7766 | 0.0092
GEN-2017-105 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.4668 | 15.4733 | 0.0065
GEN-2017-105 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5111 | 7.5117 | 0.0006
GEN-2017-105 | 02 NEBRASKA | 659922 | K10215A_-NI8 | 69 | 10.3201 | 10.3219 | 0.0018
GEN-2017-105 | 02 NEBRASKA | 659923 | K10225A_-NI8 | 69 | 9.7464 | 9.748 | 0.0016
GEN-2017-105 | 02 NEBRASKA | 659990 | K121MPLM-NI8 | 69 | 4.2517 | 4.2518 | 0.0001
GEN-2017-105 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.9801 | 8.9813 | 0.0012
GEN-2017-105 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.467 | 8.699 | 0.232
GEN-2017-105 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.467 | 8.699 | 0.232
GEN-2017-144 | 02 NEBRASKA | 531429 | MINGO 3 | 115 | 12.5445 | 12.5452 | 0.0007
GEN-2017-144 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.3618 | 6.3624 | 0.0006
GEN-2017-144 | 02 NEBRASKA | 531465 | SETAB 7 | 345 | 6.9449 | 6.9452 | 0.0003
GEN-2017-144 | 02 NEBRASKA | 531623 | EASTFORK3 | 115 | 9.7789 | 9.7794 | 0.0005
GEN-2017-144 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.6986 | 5.6991 | 0.0005
GEN-2017-144 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.4579 | 7.4608 | 0.0029
GEN-2017-144 | 02 NEBRASKA | 579450 | GEN-2016-075 | 345 | 5.8065 | 5.9168 | 0.1103
GEN-2017-144 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 7.2238 | 7.5245 | 0.3007
GEN-2017-144 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2506 | 12.2547 | 0.0041
GEN-2017-144 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.3029 | 6.305 | 0.0021
GEN-2017-144 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.6857 | 6.6922 | 0.0065
GEN-2017-144 | 02 NEBRASKA | 640050 | AINSWND7 | 115 | 3.8552 | 3.8559 | 0.0007
GEN-2017-144 | 02 NEBRASKA | 640051 | AINSWRT7 | 115 | 3.544 | 3.5445 | 0.0005
GEN-2017-144 | 02 NEBRASKA | 640052 | AINSWRT8 | 69 | 2.0813 | 2.0814 | 0.0001
GEN-2017-144 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 7.2789 | 7.2823 | 0.0034
GEN-2017-144 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.8783 | 9.8863 | 0.008
GEN-2017-144 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.8855 | 14.8922 | 0.0067
GEN-2017-144 | 02 NEBRASKA | 640082 | BEVERLY7 | 115 | 4.9351 | 4.9356 | 0.0005
GEN-2017-144 | 02 NEBRASKA | 640083 | BEVERLY8 | 69 | 4.489 | 4.4892 | 0.0002
GEN-2017-144 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 7.3494 | 7.3529 | 0.0035
GEN-2017-144 | 02 NEBRASKA | 640096 | CALAMS 7 | 115 | 3.5526 | 3.5537 | 0.0011
GEN-2017-144 | 02 NEBRASKA | 640098 | CALAWAY7 | 115 | 3.8776 | 3.8781 | 0.0005
GEN-2017-144 | 02 NEBRASKA | 640099 | CALAWAY8 | 69 | 3.1283 | 3.1285 | 0.0002
GEN-2017-144 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.2986 | 5.3001 | 0.0015
GEN-2017-144 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.4455 | 10.4489 | 0.0034
GEN-2017-144 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.2479 | 12.2515 | 0.0036
GEN-2017-144 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.9968 | 9.9996 | 0.0028
GEN-2017-144 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.3181 | 4.3184 | 0.0003
GEN-2017-144 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 16.307 | 16.3361 | 0.0291
GEN-2017-144 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 19.7689 | 19.7862 | 0.0173
GEN-2017-144 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.2894 | 17.3572 | 0.0678
GEN-2017-144 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.8427 | 23.8884 | 0.0457
GEN-2017-144 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.6104 | 7.6189 | 0.0085
GEN-2017-144 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 8.8162 | 8.8226 | 0.0064
GEN-2017-144 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.8311 | 14.8361 | 0.005
GEN-2017-144 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 9.2605 | 9.2623 | 0.0018
GEN-2017-144 | 02 NEBRASKA | 640267 | MAXWELS7 | 115 | 6.8502 | 6.8523 | 0.0021
GEN-2017-144 | 02 NEBRASKA | 640269 | MCCOOK 7 | 115 | 9.0691 | 9.0703 | 0.0012
GEN-2017-144 | 02 NEBRASKA | 640270 | MCCOOK 8 | 69 | 4.6438 | 4.644 | 0.0002
GEN-2017-144 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.39 | 11.4138 | 0.0238
GEN-2017-144 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.736 | 14.7462 | 0.0102
GEN-2017-144 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7322 | 5.7331 | 0.0009
GEN-2017-144 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.8364 | 23.8497 | 0.0133
GEN-2017-144 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.3483 | 45.3584 | 0.0101
GEN-2017-144 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 13.4805 | 13.4892 | 0.0087
GEN-2017-144 | 02 NEBRASKA | 640287 | N.PLATT7 | 115 | 18.9882 | 18.9973 | 0.0091
GEN-2017-144 | 02 NEBRASKA | 640288 | N.PLATT8 | 69 | 5.1341 | 5.1345 | 0.0004
GEN-2017-144 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.9012 | 7.9038 | 0.0026
GEN-2017-144 | 02 NEBRASKA | 640304 | OGALALANPPD7 | 115 | 14.8511 | 14.8558 | 0.0047
GEN-2017-144 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.3537 | 8.3578 | 0.0041
GEN-2017-144 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.5281 | 6.5302 | 0.0021
GEN-2017-144 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 11.7287 | 11.7308 | 0.0021
GEN-2017-144 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.5821 | 7.5882 | 0.0061
GEN-2017-144 | 02 NEBRASKA | 640331 | RIVERDL7 | 115 | 13.3915 | 13.3997 | 0.0082
GEN-2017-144 | 02 NEBRASKA | 640332 | RIVERDL8 | 69 | 6.7159 | 6.7172 | 0.0013
GEN-2017-144 | 02 NEBRASKA | 640353 | ST.LIB 7 | 115 | 9.9661 | 9.9724 | 0.0063
GEN-2017-144 | 02 NEBRASKA | 640355 | ST.PAUL7 | 115 | 3.9871 | 3.9881 | 0.001
GEN-2017-144 | 02 NEBRASKA | 640359 | STAPLETON 7 | 115 | 4.2517 | 4.2534 | 0.0017
GEN-2017-144 | 02 NEBRASKA | 640360 | STAPLETON 8 | 69 | 3.4655 | 3.4662 | 0.0007
GEN-2017-144 | 02 NEBRASKA | 640365 | STOCKVL7 | 115 | 4.698 | 4.6984 | 0.0004
GEN-2017-144 | 02 NEBRASKA | 640366 | STOCKVL8 | 69 | 3.4147 | 3.4148 | 0.0001
GEN-2017-144 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 11.1773 | 11.1977 | 0.0204
GEN-2017-144 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.4464 | 9.4678 | 0.0214
GEN-2017-144 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.4064 | 8.4095 | 0.0031
GEN-2017-144 | 02 NEBRASKA | 640416 | AURORA_8 | 69 | 4.0862 | 4.0869 | 0.0007
GEN-2017-144 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5288 | 2.5289 | 0.0001
GEN-2017-144 | 02 NEBRASKA | 640500 | CHERRYC3 | 345 | 5.8394 | 5.8706 | 0.0312
GEN-2017-144 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 7.2746 | 7.5799 | 0.3053
GEN-2017-144 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2506 | 12.2547 | 0.0041
GEN-2017-144 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.3225 | 23.3349 | 0.0124
GEN-2017-144 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 19.9762 | 19.9888 | 0.0126
GEN-2017-144 | 02 NEBRASKA | 642071 | SUB-D 7 | 115 | 17.8161 | 17.8343 | 0.0182
GEN-2017-144 | 02 NEBRASKA | 642072 | SUB-E 7 | 115 | 17.3017 | 17.3222 | 0.0205
GEN-2017-144 | 02 NEBRASKA | 648513 | GRPR1 3 | 345 | 5.8065 | 5.9168 | 0.1103
GEN-2017-144 | 02 NEBRASKA | 648520 | GRPR2 3 | 345 | 5.4835 | 5.5809 | 0.0974
GEN-2017-144 | 02 NEBRASKA | 648527 | GRPR_DMY_BUS | 345 | 5.8065 | 5.9168 | 0.1103
GEN-2017-144 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7742 | 17.7796 | 0.0054
GEN-2017-144 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.184 | 21.1898 | 0.0058
GEN-2017-144 | 02 NEBRASKA | 652506 | FTTHOMP3 | 345 | 8.5492 | 8.571 | 0.0218
GEN-2017-144 | 02 NEBRASKA | 652532 | GR PRAIRIE 3 | 345 | 6.2354 | 6.3667 | 0.1313
GEN-2017-144 | 02 NEBRASKA | 652807 | FTTHOM2-LNX3 | 345 | 8.5492 | 8.571 | 0.0218
GEN-2017-144 | 02 NEBRASKA | 652832 | GRPRAR1-LNX3 | 345 | 6.2354 | 6.3667 | 0.1313
GEN-2017-144 | 02 NEBRASKA | 652833 | GRPRAR2-LNX3 | 345 | 6.2354 | 6.3667 | 0.1313
GEN-2017-144 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.8116 | 12.8946 | 0.083
GEN-2017-144 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.6799 | 12.7631 | 0.0832
GEN-2017-144 | 02 NEBRASKA | 659133 | SIDNEY__-MB3 | 345 | 5.9761 | 5.9775 | 0.0014
GEN-2017-144 | 02 NEBRASKA | 659134 | SIDNEY___TS4 | 230 | 6.2742 | 6.2754 | 0.0012
GEN-2017-144 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 5.9761 | 5.9775 | 0.0014
GEN-2017-144 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 6.9841 | 7.2893 | 0.3052
GEN-2017-144 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9682 | 9.9861 | 0.0179
GEN-2017-144 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9205 | 6.9216 | 0.0011
GEN-2017-144 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.7833 | 5.7841 | 0.0008
GEN-2017-181 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.8502 | 12.8518 | 0.0016
GEN-2017-181 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.9594 | 16.9601 | 0.0007
GEN-2017-181 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 8.328 | 8.3298 | 0.0018
GEN-2017-181 | 02 NEBRASKA | 530584 | POSTROCK6 | 230 | 12.0841 | 12.0855 | 0.0014
GEN-2017-181 | 02 NEBRASKA | 530702 | BUCKEYE_230 | 230 | 9.067 | 9.0677 | 0.0007
GEN-2017-181 | 02 NEBRASKA | 531469 | SPERVIL7 | 345 | 12.8017 | 12.8022 | 0.0005
GEN-2017-181 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.7113 | 18.712 | 0.0007
GEN-2017-181 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 8.5046 | 8.5053 | 0.0007
GEN-2017-181 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 20.6776 | 20.68 | 0.0024
GEN-2017-181 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 20.9817 | 20.9827 | 0.001
GEN-2017-181 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 19.1093 | 19.1108 | 0.0015
GEN-2017-181 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 8.1127 | 8.1133 | 0.0006
GEN-2017-181 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 8.1127 | 8.1133 | 0.0006
GEN-2017-181 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 8.1127 | 8.1133 | 0.0006
GEN-2017-181 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 10.1039 | 10.1052 | 0.0013
GEN-2017-181 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 8.0193 | 8.02 | 0.0007
GEN-2017-181 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 10.0458 | 10.0472 | 0.0014
GEN-2017-181 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 6.7602 | 6.7606 | 0.0004
GEN-2017-181 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.4511 | 7.4608 | 0.0097
GEN-2017-181 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 43.8143 | 44.0075 | 0.1932
GEN-2017-181 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.2587 | 19.2944 | 0.0357
GEN-2017-181 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 7.5222 | 7.5245 | 0.0023
GEN-2017-181 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 11.8026 | 12.2547 | 0.4521
GEN-2017-181 | 02 NEBRASKA | 587150 | GEN-2016-021 | 345 | 9.3359 | 9.3372 | 0.0013
GEN-2017-181 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.2982 | 6.305 | 0.0068
GEN-2017-181 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.6876 | 6.6922 | 0.0046
GEN-2017-181 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 31.9279 | 31.9397 | 0.0118
GEN-2017-181 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.679 | 17.688 | 0.009
GEN-2017-181 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.8554 | 16.8633 | 0.0079
GEN-2017-181 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.7693 | 16.7771 | 0.0078
GEN-2017-181 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.8596 | 9.8863 | 0.0267
GEN-2017-181 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.8773 | 14.8922 | 0.0149
GEN-2017-181 | 02 NEBRASKA | 640074 | BEAT. S7 | 115 | 5.4733 | 5.4741 | 0.0008
GEN-2017-181 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 13.7388 | 13.7438 | 0.005
GEN-2017-181 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 16.9108 | 16.9188 | 0.008
GEN-2017-181 | 02 NEBRASKA | 640105 | CARLJCT7 | 115 | 5.7709 | 5.7725 | 0.0016
GEN-2017-181 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 11.1055 | 11.1118 | 0.0063
GEN-2017-181 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.8377 | 20.8461 | 0.0084
GEN-2017-181 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.5517 | 17.5576 | 0.0059
GEN-2017-181 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.664 | 10.6739 | 0.0099
GEN-2017-181 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.705 | 10.7096 | 0.0046
GEN-2017-181 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5605 | 23.5717 | 0.0112
GEN-2017-181 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.4443 | 10.4489 | 0.0046
GEN-2017-181 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.3635 | 20.371 | 0.0075
GEN-2017-181 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.6792 | 27.7084 | 0.0292
GEN-2017-181 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1786 | 18.184 | 0.0054
GEN-2017-181 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6837 | 4.6839 | 0.0002
GEN-2017-181 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.4544 | 8.4605 | 0.0061
GEN-2017-181 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9514 | 5.9523 | 0.0009
GEN-2017-181 | 02 NEBRASKA | 640161 | ELMCRK_7 | 115 | 6.2217 | 6.2229 | 0.0012
GEN-2017-181 | 02 NEBRASKA | 640162 | ELMCRK 8 | 69 | 3.8742 | 3.8745 | 0.0003
GEN-2017-181 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 7.0214 | 7.0255 | 0.0041
GEN-2017-181 | 02 NEBRASKA | 640174 | FRIEND 7 | 115 | 5.7215 | 5.7239 | 0.0024
GEN-2017-181 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.9932 | 9.9996 | 0.0064
GEN-2017-181 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.3177 | 4.3184 | 0.0007
GEN-2017-181 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 16.3309 | 16.3361 | 0.0052
GEN-2017-181 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 19.7827 | 19.7862 | 0.0035
GEN-2017-181 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.333 | 17.3572 | 0.0242
GEN-2017-181 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.8681 | 23.8884 | 0.0203
GEN-2017-181 | 02 NEBRASKA | 640206 | GUIDE R7 | 115 | 4.3802 | 4.3822 | 0.002
GEN-2017-181 | 02 NEBRASKA | 640207 | GUIDE R8 | 69 | 2.2462 | 2.2466 | 0.0004
GEN-2017-181 | 02 NEBRASKA | 640208 | HARBINE7 | 115 | 6.9964 | 6.9974 | 0.001
GEN-2017-181 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.6132 | 7.6189 | 0.0057
GEN-2017-181 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 19.9643 | 19.9888 | 0.0245
GEN-2017-181 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.397 | 4.3987 | 0.0017
GEN-2017-181 | 02 NEBRASKA | 640223 | HILDRTH8 | 69 | 3.5539 | 3.5546 | 0.0007
GEN-2017-181 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 6.3195 | 6.3219 | 0.0024
GEN-2017-181 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.7931 | 13.7966 | 0.0035
GEN-2017-181 | 02 NEBRASKA | 640242 | JOHN.2 7 | 115 | 13.1015 | 13.1042 | 0.0027
GEN-2017-181 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.8057 | 9.8096 | 0.0039
GEN-2017-181 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 12.4548 | 12.4617 | 0.0069
GEN-2017-181 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 8.8214 | 8.8226 | 0.0012
GEN-2017-181 | 02 NEBRASKA | 640261 | LOWELL 7 | 115 | 8.4619 | 8.4656 | 0.0037
GEN-2017-181 | 02 NEBRASKA | 640262 | LOWELL 8 | 69 | 4.2185 | 4.219 | 0.0005
GEN-2017-181 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.3815 | 11.4138 | 0.0323
GEN-2017-181 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.7305 | 14.7462 | 0.0157
GEN-2017-181 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7317 | 5.7331 | 0.0014
GEN-2017-181 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.4694 | 7.4727 | 0.0033
GEN-2017-181 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.555 | 23.8497 | 0.2947
GEN-2017-181 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.1672 | 45.3584 | 0.1912
GEN-2017-181 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.467 | 2.4674 | 0.0004
GEN-2017-181 | 02 NEBRASKA | 640311 | ORLEANS8 | 69 | 2.4695 | 2.4698 | 0.0003
GEN-2017-181 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.2961 | 8.3578 | 0.0617
GEN-2017-181 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.8758 | 16.9188 | 0.043
GEN-2017-181 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.94 | 4.9422 | 0.0022
GEN-2017-181 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7729 | 11.782 | 0.0091
GEN-2017-181 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.5297 | 6.5302 | 0.0005
GEN-2017-181 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.5848 | 7.5882 | 0.0034
GEN-2017-181 | 02 NEBRASKA | 640340 | SEWARD 7 | 115 | 7.7217 | 7.725 | 0.0033
GEN-2017-181 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9425 | 10.9505 | 0.008
GEN-2017-181 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.5223 | 11.5277 | 0.0054
GEN-2017-181 | 02 NEBRASKA | 640361 | STEINER7 | 115 | 4.6081 | 4.6084 | 0.0003
GEN-2017-181 | 02 NEBRASKA | 640362 | STERLNG7 | 115 | 4.7203 | 4.7218 | 0.0015
GEN-2017-181 | 02 NEBRASKA | 640368 | SUPEROR7 | 115 | 3.4943 | 3.4952 | 0.0009
GEN-2017-181 | 02 NEBRASKA | 640372 | SUTTON 7 | 115 | 6.5519 | 6.5544 | 0.0025
GEN-2017-181 | 02 NEBRASKA | 640373 | SUTTON 8 | 69 | 3.9315 | 3.932 | 0.0005
GEN-2017-181 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 11.1833 | 11.1977 | 0.0144
GEN-2017-181 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 9.4253 | 9.4289 | 0.0036
GEN-2017-181 | 02 NEBRASKA | 640411 | YORK 7 | 115 | 7.8675 | 7.8711 | 0.0036
GEN-2017-181 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.405 | 8.4095 | 0.0045
GEN-2017-181 | 02 NEBRASKA | 640415 | CARLJCT8 | 69 | 3.7544 | 3.7548 | 0.0004
GEN-2017-181 | 02 NEBRASKA | 640443 | YORK 8 | 69 | 2.6714 | 2.6716 | 0.0002
GEN-2017-181 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7814 | 4.7816 | 0.0002
GEN-2017-181 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5287 | 2.5289 | 0.0002
GEN-2017-181 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 3.8364 | 3.837 | 0.0006
GEN-2017-181 | 02 NEBRASKA | 640500 | CHERRYC3 | 345 | 5.8698 | 5.8706 | 0.0008
GEN-2017-181 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 7.5776 | 7.5799 | 0.0023
GEN-2017-181 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 11.8026 | 12.2547 | 0.4521
GEN-2017-181 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.7811 | 6.7865 | 0.0054
GEN-2017-181 | 02 NEBRASKA | 640584 | COTTONWD 7 | 115 | 5.4775 | 5.4809 | 0.0034
GEN-2017-181 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 12.1869 | 12.1894 | 0.0025
GEN-2017-181 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.9164 | 9.9179 | 0.0015
GEN-2017-181 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.0605 | 23.3349 | 0.2744
GEN-2017-181 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 43.8143 | 44.0075 | 0.1932
GEN-2017-181 | 02 NEBRASKA | 641085 | E7THST 7 | 115 | 18.8395 | 18.8609 | 0.0214
GEN-2017-181 | 02 NEBRASKA | 641087 | EGYCNTR7 | 115 | 18.6966 | 18.7149 | 0.0183
GEN-2017-181 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 19.9643 | 19.9888 | 0.0245
GEN-2017-181 | 02 NEBRASKA | 641090 | S. 281 7 | 115 | 11.5864 | 11.5937 | 0.0073
GEN-2017-181 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.9362 | 11.9385 | 0.0023
GEN-2017-181 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.5825 | 21.5916 | 0.0091
GEN-2017-181 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.8193 | 28.8501 | 0.0308
GEN-2017-181 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 31.9193 | 31.9469 | 0.0276
GEN-2017-181 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.4568 | 34.4808 | 0.024
GEN-2017-181 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.6501 | 30.6853 | 0.0352
GEN-2017-181 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.0665 | 25.0785 | 0.012
GEN-2017-181 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.8727 | 22.8881 | 0.0154
GEN-2017-181 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.7774 | 44.7914 | 0.014
GEN-2017-181 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.4475 | 32.461 | 0.0135
GEN-2017-181 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.286 | 10.2874 | 0.0014
GEN-2017-181 | 02 NEBRASKA | 647966 | S966 8 | 69 | 0.4927 | 0.4927 | 0
GEN-2017-181 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.6843 | 17.7796 | 0.0953
GEN-2017-181 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.1992 | 21.2967 | 0.0975
GEN-2017-181 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.0709 | 21.1898 | 0.1189
GEN-2017-181 | 02 NEBRASKA | 650207 | NW56&MORTN7 | 115 | 18.3583 | 18.3808 | 0.0225
GEN-2017-181 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.5535 | 21.5856 | 0.0321
GEN-2017-181 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.8242 | 25.8712 | 0.047
GEN-2017-181 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.3174 | 22.3501 | 0.0327
GEN-2017-181 | 02 NEBRASKA | 650218 | 3&VANDORN 7 | 115 | 22.1038 | 22.1352 | 0.0314
GEN-2017-181 | 02 NEBRASKA | 650229 | 27&PLR 7 | 115 | 20.8658 | 20.8955 | 0.0297
GEN-2017-181 | 02 NEBRASKA | 650230 | 2&N 7 | 115 | 26.2283 | 26.272 | 0.0437
GEN-2017-181 | 02 NEBRASKA | 650238 | 20PIONEERS7 | 115 | 27.6734 | 27.7231 | 0.0497
GEN-2017-181 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 28.1259 | 28.1804 | 0.0545
GEN-2017-181 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 23.6139 | 23.6548 | 0.0409
GEN-2017-181 | 02 NEBRASKA | 650247 | 40&BENNET 7 | 115 | 21.6564 | 21.6891 | 0.0327
GEN-2017-181 | 02 NEBRASKA | 650250 | 40&ROKEBY 7 | 115 | 21.493 | 21.5246 | 0.0316
GEN-2017-181 | 02 NEBRASKA | 650258 | 40&GERTIE 7 | 115 | 23.6115 | 23.647 | 0.0355
GEN-2017-181 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.9043 | 29.9566 | 0.0523
GEN-2017-181 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.7859 | 27.8342 | 0.0483
GEN-2017-181 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.4178 | 25.4589 | 0.0411
GEN-2017-181 | 02 NEBRASKA | 650276 | 76&ROKEBY 7 | 115 | 17.9916 | 18.0135 | 0.0219
GEN-2017-181 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.9503 | 21.9769 | 0.0266
GEN-2017-181 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.5508 | 32.6157 | 0.0649
GEN-2017-181 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.9905 | 26.0363 | 0.0458
GEN-2017-181 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.8724 | 12.8946 | 0.0222
GEN-2017-181 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.7415 | 12.7631 | 0.0216
GEN-2017-181 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.1412 | 8.142 | 0.0008
GEN-2017-181 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.2871 | 7.2893 | 0.0022
GEN-2017-181 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.9801 | 8.9813 | 0.0012
GEN-2017-181 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9618 | 9.9861 | 0.0243
GEN-2017-181 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.4396 | 6.9216 | 0.482
GEN-2017-181 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.4475 | 5.7841 | 0.3366
GEN-2017-181 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 8.8069 | 8.8071 | 0.0002
GEN-2017-181 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 17.6211 | 17.6218 | 0.0007
GEN-2017-182 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.8511 | 12.8518 | 0.0007
GEN-2017-182 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.9598 | 16.9601 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 8.3291 | 8.3298 | 0.0007
GEN-2017-182 | 02 NEBRASKA | 530584 | POSTROCK6 | 230 | 12.0849 | 12.0855 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 530702 | BUCKEYE_230 | 230 | 9.0674 | 9.0677 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 531469 | SPERVIL7 | 345 | 12.802 | 12.8022 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.7117 | 18.712 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 8.505 | 8.5053 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 20.6791 | 20.68 | 0.0009
GEN-2017-182 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 20.9823 | 20.9827 | 0.0004
GEN-2017-182 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 19.1102 | 19.1108 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 8.1131 | 8.1133 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 8.1131 | 8.1133 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 8.1131 | 8.1133 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 10.1046 | 10.1052 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 8.0197 | 8.02 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 10.0466 | 10.0472 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 6.7604 | 6.7606 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.4569 | 7.4608 | 0.0039
GEN-2017-182 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 43.9286 | 44.0075 | 0.0789
GEN-2017-182 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.2799 | 19.2944 | 0.0145
GEN-2017-182 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 7.5236 | 7.5245 | 0.0009
GEN-2017-182 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.0664 | 12.2547 | 0.1883
GEN-2017-182 | 02 NEBRASKA | 587150 | GEN-2016-021 | 345 | 9.3367 | 9.3372 | 0.0005
GEN-2017-182 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.3022 | 6.305 | 0.0028
GEN-2017-182 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.6903 | 6.6922 | 0.0019
GEN-2017-182 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 31.9349 | 31.9397 | 0.0048
GEN-2017-182 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.6843 | 17.688 | 0.0037
GEN-2017-182 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.8601 | 16.8633 | 0.0032
GEN-2017-182 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.7739 | 16.7771 | 0.0032
GEN-2017-182 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.8754 | 9.8863 | 0.0109
GEN-2017-182 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.8862 | 14.8922 | 0.006
GEN-2017-182 | 02 NEBRASKA | 640074 | BEAT. S7 | 115 | 5.4738 | 5.4741 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 13.7417 | 13.7438 | 0.0021
GEN-2017-182 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 16.9156 | 16.9188 | 0.0032
GEN-2017-182 | 02 NEBRASKA | 640105 | CARLJCT7 | 115 | 5.7719 | 5.7725 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 11.1093 | 11.1118 | 0.0025
GEN-2017-182 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.8427 | 20.8461 | 0.0034
GEN-2017-182 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.5552 | 17.5576 | 0.0024
GEN-2017-182 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6698 | 10.6739 | 0.0041
GEN-2017-182 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.7077 | 10.7096 | 0.0019
GEN-2017-182 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5672 | 23.5717 | 0.0045
GEN-2017-182 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.447 | 10.4489 | 0.0019
GEN-2017-182 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.3679 | 20.371 | 0.0031
GEN-2017-182 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.6965 | 27.7084 | 0.0119
GEN-2017-182 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1818 | 18.184 | 0.0022
GEN-2017-182 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6838 | 4.6839 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.458 | 8.4605 | 0.0025
GEN-2017-182 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9519 | 5.9523 | 0.0004
GEN-2017-182 | 02 NEBRASKA | 640161 | ELMCRK_7 | 115 | 6.2224 | 6.2229 | 0.0005
GEN-2017-182 | 02 NEBRASKA | 640162 | ELMCRK 8 | 69 | 3.8744 | 3.8745 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 7.0238 | 7.0255 | 0.0017
GEN-2017-182 | 02 NEBRASKA | 640174 | FRIEND 7 | 115 | 5.7229 | 5.7239 | 0.001
GEN-2017-182 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.997 | 9.9996 | 0.0026
GEN-2017-182 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.3181 | 4.3184 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 16.3339 | 16.3361 | 0.0022
GEN-2017-182 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 19.7848 | 19.7862 | 0.0014
GEN-2017-182 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.3474 | 17.3572 | 0.0098
GEN-2017-182 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.8801 | 23.8884 | 0.0083
GEN-2017-182 | 02 NEBRASKA | 640206 | GUIDE R7 | 115 | 4.3814 | 4.3822 | 0.0008
GEN-2017-182 | 02 NEBRASKA | 640207 | GUIDE R8 | 69 | 2.2464 | 2.2466 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 640208 | HARBINE7 | 115 | 6.997 | 6.9974 | 0.0004
GEN-2017-182 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.6166 | 7.6189 | 0.0023
GEN-2017-182 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 19.9788 | 19.9888 | 0.01
GEN-2017-182 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.398 | 4.3987 | 0.0007
GEN-2017-182 | 02 NEBRASKA | 640223 | HILDRTH8 | 69 | 3.5543 | 3.5546 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 6.3209 | 6.3219 | 0.001
GEN-2017-182 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.7952 | 13.7966 | 0.0014
GEN-2017-182 | 02 NEBRASKA | 640242 | JOHN.2 7 | 115 | 13.1031 | 13.1042 | 0.0011
GEN-2017-182 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.808 | 9.8096 | 0.0016
GEN-2017-182 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 12.4588 | 12.4617 | 0.0029
GEN-2017-182 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 8.8221 | 8.8226 | 0.0005
GEN-2017-182 | 02 NEBRASKA | 640261 | LOWELL 7 | 115 | 8.4641 | 8.4656 | 0.0015
GEN-2017-182 | 02 NEBRASKA | 640262 | LOWELL 8 | 69 | 4.2188 | 4.219 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.4007 | 11.4138 | 0.0131
GEN-2017-182 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.7398 | 14.7462 | 0.0064
GEN-2017-182 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7325 | 5.7331 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.4713 | 7.4727 | 0.0014
GEN-2017-182 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.7288 | 23.8497 | 0.1209
GEN-2017-182 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.2803 | 45.3584 | 0.0781
GEN-2017-182 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.4672 | 2.4674 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 640311 | ORLEANS8 | 69 | 2.4697 | 2.4698 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.3326 | 8.3578 | 0.0252
GEN-2017-182 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.9013 | 16.9188 | 0.0175
GEN-2017-182 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9413 | 4.9422 | 0.0009
GEN-2017-182 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7783 | 11.782 | 0.0037
GEN-2017-182 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.53 | 6.5302 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.5868 | 7.5882 | 0.0014
GEN-2017-182 | 02 NEBRASKA | 640340 | SEWARD 7 | 115 | 7.7236 | 7.725 | 0.0014
GEN-2017-182 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9472 | 10.9505 | 0.0033
GEN-2017-182 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.5255 | 11.5277 | 0.0022
GEN-2017-182 | 02 NEBRASKA | 640361 | STEINER7 | 115 | 4.6083 | 4.6084 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640362 | STERLNG7 | 115 | 4.7212 | 4.7218 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 640368 | SUPEROR7 | 115 | 3.4949 | 3.4952 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 640372 | SUTTON 7 | 115 | 6.5534 | 6.5544 | 0.001
GEN-2017-182 | 02 NEBRASKA | 640373 | SUTTON 8 | 69 | 3.9318 | 3.932 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 11.1918 | 11.1977 | 0.0059
GEN-2017-182 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 9.4274 | 9.4289 | 0.0015
GEN-2017-182 | 02 NEBRASKA | 640411 | YORK 7 | 115 | 7.8697 | 7.8711 | 0.0014
GEN-2017-182 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.4077 | 8.4095 | 0.0018
GEN-2017-182 | 02 NEBRASKA | 640415 | CARLJCT8 | 69 | 3.7547 | 3.7548 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640443 | YORK 8 | 69 | 2.6715 | 2.6716 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7815 | 4.7816 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5288 | 2.5289 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 3.8368 | 3.837 | 0.0002
GEN-2017-182 | 02 NEBRASKA | 640500 | CHERRYC3 | 345 | 5.8703 | 5.8706 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 7.579 | 7.5799 | 0.0009
GEN-2017-182 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.0664 | 12.2547 | 0.1883
GEN-2017-182 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.7843 | 6.7865 | 0.0022
GEN-2017-182 | 02 NEBRASKA | 640584 | COTTONWD 7 | 115 | 5.4796 | 5.4809 | 0.0013
GEN-2017-182 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 12.1884 | 12.1894 | 0.001
GEN-2017-182 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.9173 | 9.9179 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.2224 | 23.3349 | 0.1125
GEN-2017-182 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 43.9286 | 44.0075 | 0.0789
GEN-2017-182 | 02 NEBRASKA | 641085 | E7THST 7 | 115 | 18.8522 | 18.8609 | 0.0087
GEN-2017-182 | 02 NEBRASKA | 641087 | EGYCNTR7 | 115 | 18.7074 | 18.7149 | 0.0075
GEN-2017-182 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 19.9788 | 19.9888 | 0.01
GEN-2017-182 | 02 NEBRASKA | 641090 | S. 281 7 | 115 | 11.5907 | 11.5937 | 0.003
GEN-2017-182 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.9376 | 11.9385 | 0.0009
GEN-2017-182 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.5879 | 21.5916 | 0.0037
GEN-2017-182 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.8376 | 28.8501 | 0.0125
GEN-2017-182 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 31.9356 | 31.9469 | 0.0113
GEN-2017-182 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.471 | 34.4808 | 0.0098
GEN-2017-182 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.671 | 30.6853 | 0.0143
GEN-2017-182 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.0736 | 25.0785 | 0.0049
GEN-2017-182 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.8818 | 22.8881 | 0.0063
GEN-2017-182 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.7857 | 44.7914 | 0.0057
GEN-2017-182 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.4555 | 32.461 | 0.0055
GEN-2017-182 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.2868 | 10.2874 | 0.0006
GEN-2017-182 | 02 NEBRASKA | 647966 | S966 8 | 69 | 0.4927 | 0.4927 | 0
GEN-2017-182 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7407 | 17.7796 | 0.0389
GEN-2017-182 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.2569 | 21.2967 | 0.0398
GEN-2017-182 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.1412 | 21.1898 | 0.0486
GEN-2017-182 | 02 NEBRASKA | 650207 | NW56&MORTN7 | 115 | 18.3716 | 18.3808 | 0.0092
GEN-2017-182 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.5725 | 21.5856 | 0.0131
GEN-2017-182 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.852 | 25.8712 | 0.0192
GEN-2017-182 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.3368 | 22.3501 | 0.0133
GEN-2017-182 | 02 NEBRASKA | 650218 | 3&VANDORN 7 | 115 | 22.1224 | 22.1352 | 0.0128
GEN-2017-182 | 02 NEBRASKA | 650229 | 27&PLR 7 | 115 | 20.8834 | 20.8955 | 0.0121
GEN-2017-182 | 02 NEBRASKA | 650230 | 2&N 7 | 115 | 26.2542 | 26.272 | 0.0178
GEN-2017-182 | 02 NEBRASKA | 650238 | 20PIONEERS7 | 115 | 27.7028 | 27.7231 | 0.0203
GEN-2017-182 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 28.1582 | 28.1804 | 0.0222
GEN-2017-182 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 23.6381 | 23.6548 | 0.0167
GEN-2017-182 | 02 NEBRASKA | 650247 | 40&BENNET 7 | 115 | 21.6758 | 21.6891 | 0.0133
GEN-2017-182 | 02 NEBRASKA | 650250 | 40&ROKEBY 7 | 115 | 21.5117 | 21.5246 | 0.0129
GEN-2017-182 | 02 NEBRASKA | 650258 | 40&GERTIE 7 | 115 | 23.6326 | 23.647 | 0.0144
GEN-2017-182 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.9353 | 29.9566 | 0.0213
GEN-2017-182 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.8145 | 27.8342 | 0.0197
GEN-2017-182 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.4422 | 25.4589 | 0.0167
GEN-2017-182 | 02 NEBRASKA | 650276 | 76&ROKEBY 7 | 115 | 18.0046 | 18.0135 | 0.0089
GEN-2017-182 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.9661 | 21.9769 | 0.0108
GEN-2017-182 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.5893 | 32.6157 | 0.0264
GEN-2017-182 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 26.0176 | 26.0363 | 0.0187
GEN-2017-182 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.8855 | 12.8946 | 0.0091
GEN-2017-182 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.7543 | 12.7631 | 0.0088
GEN-2017-182 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.1417 | 8.142 | 0.0003
GEN-2017-182 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.2884 | 7.2893 | 0.0009
GEN-2017-182 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.9808 | 8.9813 | 0.0005
GEN-2017-182 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9762 | 9.9861 | 0.0099
GEN-2017-182 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.7169 | 6.9216 | 0.2047
GEN-2017-182 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.5781 | 5.7841 | 0.206
GEN-2017-182 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 8.807 | 8.8071 | 0.0001
GEN-2017-182 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 17.6215 | 17.6218 | 0.0003
GEN-2017-198 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 10.1051 | 10.1052 | 0.0001
GEN-2017-198 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 8.02 | 8.02 | 0
GEN-2017-198 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 10.0471 | 10.0472 | 0.0001
GEN-2017-198 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 6.7606 | 6.7606 | 0
GEN-2017-198 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 31.9342 | 31.9397 | 0.0055
GEN-2017-198 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.5272 | 39.5345 | 0.0073
GEN-2017-198 | 02 NEBRASKA | 635002 | CBLUFFS8 | 69 | 25.1663 | 25.1678 | 0.0015
GEN-2017-198 | 02 NEBRASKA | 635003 | SUB701 5 | 161 | 21.4703 | 21.4745 | 0.0042
GEN-2017-198 | 02 NEBRASKA | 635004 | SUB701 8 | 69 | 22.33 | 22.3315 | 0.0015
GEN-2017-198 | 02 NEBRASKA | 635005 | SUB702 5 | 161 | 20.8302 | 20.8338 | 0.0036
GEN-2017-198 | 02 NEBRASKA | 635008 | SUB705 8 | 69 | 12.4716 | 12.472 | 0.0004
GEN-2017-198 | 02 NEBRASKA | 635009 | SUB706 8 | 69 | 10.825 | 10.8253 | 0.0003
GEN-2017-198 | 02 NEBRASKA | 635010 | MANAWA 5 | 161 | 21.6573 | 21.6606 | 0.0033
GEN-2017-198 | 02 NEBRASKA | 635011 | INDNCRK5 | 161 | 21.9543 | 21.9576 | 0.0033
GEN-2017-198 | 02 NEBRASKA | 635012 | QUICK 5 | 161 | 11.3812 | 11.3816 | 0.0004
GEN-2017-198 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.0916 | 29.0961 | 0.0045
GEN-2017-198 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.327 | 27.331 | 0.004
GEN-2017-198 | 02 NEBRASKA | 635015 | OVRLND 5 | 161 | 31.3886 | 31.3925 | 0.0039
GEN-2017-198 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.0564 | 29.0609 | 0.0045
GEN-2017-198 | 02 NEBRASKA | 635030 | RIVRBND5 | 161 | 36.03 | 36.0359 | 0.0059
GEN-2017-198 | 02 NEBRASKA | 635031 | BUNGE 5 | 161 | 29.2799 | 29.2835 | 0.0036
GEN-2017-198 | 02 NEBRASKA | 635075 | GLNWOOD8 | 69 | 6.3226 | 6.3226 | 0
GEN-2017-198 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.7078 | 27.7084 | 0.0006
GEN-2017-198 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.5882 | 21.5916 | 0.0034
GEN-2017-198 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.8449 | 28.8501 | 0.0052
GEN-2017-198 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 31.9395 | 31.9469 | 0.0074
GEN-2017-198 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.4717 | 34.4808 | 0.0091
GEN-2017-198 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.6837 | 30.6853 | 0.0016
GEN-2017-198 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.0725 | 25.0785 | 0.006
GEN-2017-198 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.8856 | 22.8881 | 0.0025
GEN-2017-198 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 22.9643 | 22.9682 | 0.0039
GEN-2017-198 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.8297 | 31.8574 | 0.0277
GEN-2017-198 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.7691 | 44.7914 | 0.0223
GEN-2017-198 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 46.7058 | 46.7214 | 0.0156
GEN-2017-198 | 02 NEBRASKA | 646210 | S1210 5 | 161 | 28.0538 | 28.0735 | 0.0197
GEN-2017-198 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.1367 | 36.1559 | 0.0192
GEN-2017-198 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.6567 | 30.6702 | 0.0135
GEN-2017-198 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.309 | 33.3266 | 0.0176
GEN-2017-198 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 28.4939 | 28.5137 | 0.0198
GEN-2017-198 | 02 NEBRASKA | 646222 | S1222 5 | 161 | 27.5602 | 27.5798 | 0.0196
GEN-2017-198 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.5827 | 32.5952 | 0.0125
GEN-2017-198 | 02 NEBRASKA | 646229 | S1229 5 | 161 | 28.7961 | 28.8183 | 0.0222
GEN-2017-198 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.6957 | 26.7019 | 0.0062
GEN-2017-198 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.2342 | 22.24 | 0.0058
GEN-2017-198 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.2076 | 35.222 | 0.0144
GEN-2017-198 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 48.4684 | 48.4794 | 0.011
GEN-2017-198 | 02 NEBRASKA | 646258 | S1258 5 | 161 | 5.9279 | 5.9281 | 0.0002
GEN-2017-198 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 38.3304 | 38.3376 | 0.0072
GEN-2017-198 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 27.4685 | 27.4731 | 0.0046
GEN-2017-198 | 02 NEBRASKA | 646286 | S1286 5 | 161 | 26.6288 | 26.6461 | 0.0173
GEN-2017-198 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 18.9311 | 18.9337 | 0.0026
GEN-2017-198 | 02 NEBRASKA | 646299 | S1299 5 | 161 | 27.6947 | 27.7081 | 0.0134
GEN-2017-198 | 02 NEBRASKA | 646366 | S1366 5 | 161 | 16.3951 | 16.3983 | 0.0032
GEN-2017-198 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.5904 | 32.5972 | 0.0068
GEN-2017-198 | 02 NEBRASKA | 647015 | S6815T1&T2 8 | 69 | 12.0984 | 12.0994 | 0.001
GEN-2017-198 | 02 NEBRASKA | 647016 | 6815TP38 | 69 | 17.5997 | 17.6033 | 0.0036
GEN-2017-198 | 02 NEBRASKA | 647017 | 6815TP98 | 69 | 12.6882 | 12.6893 | 0.0011
GEN-2017-198 | 02 NEBRASKA | 647105 | JCT205 8 | 69 | 22.6198 | 22.7012 | 0.0814
GEN-2017-198 | 02 NEBRASKA | 647107 | SAC623 8 | 69 | 18.2948 | 18.298 | 0.0032
GEN-2017-198 | 02 NEBRASKA | 647108 | SAC629 8 | 69 | 11.9732 | 11.9742 | 0.001
GEN-2017-198 | 02 NEBRASKA | 647109 | SAC SO 8 | 69 | 9.8016 | 9.8025 | 0.0009
GEN-2017-198 | 02 NEBRASKA | 647110 | SAC NO 8 | 69 | 10.075 | 10.0757 | 0.0007
GEN-2017-198 | 02 NEBRASKA | 647815 | S6815T3 8 | 69 | 11.4573 | 11.4588 | 0.0015
GEN-2017-198 | 02 NEBRASKA | 647866 | S6866 8 | 69 | 20.6778 | 20.6812 | 0.0034
GEN-2017-198 | 02 NEBRASKA | 647874 | S6874 8 | 69 | 8.6353 | 8.6359 | 0.0006
GEN-2017-198 | 02 NEBRASKA | 647901 | S901 8 | 69 | 26.905 | 27.0529 | 0.1479
GEN-2017-198 | 02 NEBRASKA | 647904 | S904 8 | 69 | 8.754 | 8.7548 | 0.0008
GEN-2017-198 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 33.0879 | 33.107 | 0.0191
GEN-2017-198 | 02 NEBRASKA | 647907 | S907 8 | 69 | 18.0124 | 18.0166 | 0.0042
GEN-2017-198 | 02 NEBRASKA | 647908 | S908 8 | 69 | 18.6133 | 18.6308 | 0.0175
GEN-2017-198 | 02 NEBRASKA | 647910 | S910 8 | 69 | 26.0027 | 26.0465 | 0.0438
GEN-2017-198 | 02 NEBRASKA | 647911 | S911 8 | 69 | 21.3035 | 21.3107 | 0.0072
GEN-2017-198 | 02 NEBRASKA | 647912 | S912 8 | 69 | 22.8191 | 22.8556 | 0.0365
GEN-2017-198 | 02 NEBRASKA | 647913 | S913 8 | 69 | 16.2183 | 16.2268 | 0.0085
GEN-2017-198 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8154 | 23.8186 | 0.0032
GEN-2017-198 | 02 NEBRASKA | 647917 | S917 8 | 69 | 25.9589 | 25.9628 | 0.0039
GEN-2017-198 | 02 NEBRASKA | 647923 | S923 8 | 69 | 19.2156 | 19.2409 | 0.0253
GEN-2017-198 | 02 NEBRASKA | 647924 | S924 8 | 69 | 24.6065 | 24.628 | 0.0215
GEN-2017-198 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.2819 | 17.2836 | 0.0017
GEN-2017-198 | 02 NEBRASKA | 647938 | S938 8 | 69 | 21.8759 | 21.8803 | 0.0044
GEN-2017-198 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9178 | 20.9201 | 0.0023
GEN-2017-198 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.2137 | 16.2151 | 0.0014
GEN-2017-198 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.3516 | 20.3545 | 0.0029
GEN-2017-198 | 02 NEBRASKA | 647985 | S985 8 | 69 | 8.1581 | 8.1587 | 0.0006
GEN-2017-198 | 02 NEBRASKA | 647995 | S995 8 | 69 | 9.5166 | 9.5175 | 0.0009
GEN-2017-198 | 02 NEBRASKA | 648600 | NC1HS 5 | 161 | 5.8068 | 5.8069 | 0.0001
GEN-2017-198 | 02 NEBRASKA | 648610 | NC2HS 5 | 161 | 5.8159 | 5.816 | 0.0001
GEN-2017-198 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.1891 | 21.1898 | 0.0007
GEN-2017-198 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.142 | 8.142 | 0
GEN-2017-198 | 02 NEBRASKA | 760872 | GEN-2017-198 | 69 | 25.4728 | 25.6201 | 0.1473
GEN-2017-201 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 11.2991 | 11.3023 | 0.0032
GEN-2017-201 | 02 NEBRASKA | 87487 | J748POI | 345 | 12.4868 | 12.4907 | 0.0039
GEN-2017-201 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2527 | 12.2547 | 0.002
GEN-2017-201 | 02 NEBRASKA | 587150 | GEN-2016-021 | 345 | 9.1415 | 9.3372 | 0.1957
GEN-2017-201 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.3161 | 14.318 | 0.0019
GEN-2017-201 | 02 NEBRASKA | 601034 | NOBLES 3 | 345 | 11.6594 | 11.6601 | 0.0007
GEN-2017-201 | 02 NEBRASKA | 603016 | SPLT RK7 | 115 | 38.8091 | 38.813 | 0.0039
GEN-2017-201 | 02 NEBRASKA | 603149 | ANSON4 | 115 | 36.7646 | 36.7682 | 0.0036
GEN-2017-201 | 02 NEBRASKA | 603200 | ANSON 7 | 115 | 35.3419 | 35.345 | 0.0031
GEN-2017-201 | 02 NEBRASKA | 603228 | SPLITRK CAP7 | 115 | 38.2243 | 38.2281 | 0.0038
GEN-2017-201 | 02 NEBRASKA | 603264 | PROSE WIND7 | 115 | 5.0917 | 5.0917 | 0
GEN-2017-201 | 02 NEBRASKA | 603265 | PROSE CAP7 | 115 | 36.8244 | 36.828 | 0.0036
GEN-2017-201 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 31.9365 | 31.9397 | 0.0032
GEN-2017-201 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 26.5167 | 26.5717 | 0.055
GEN-2017-201 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.7085 | 27.7322 | 0.0237
GEN-2017-201 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.9708 | 22.9865 | 0.0157
GEN-2017-201 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.2278 | 26.2489 | 0.0211
GEN-2017-201 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2157 | 10.2171 | 0.0014
GEN-2017-201 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.4043 | 9.4071 | 0.0028
GEN-2017-201 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.0032 | 9.0054 | 0.0022
GEN-2017-201 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.041 | 15.0477 | 0.0067
GEN-2017-201 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.6861 | 17.6951 | 0.009
GEN-2017-201 | 02 NEBRASKA | 635222 | KELLOGG8 | 69 | 18.4387 | 18.4427 | 0.004
GEN-2017-201 | 02 NEBRASKA | 635225 | MORNSD 5 | 161 | 11.2686 | 11.272 | 0.0034
GEN-2017-201 | 02 NEBRASKA | 635226 | LEEDS 5 | 161 | 16.3841 | 16.3916 | 0.0075
GEN-2017-201 | 02 NEBRASKA | 635227 | SBRIDGE T8 | 69 | 8.9238 | 8.9248 | 0.001
GEN-2017-201 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.5438 | 17.553 | 0.0092
GEN-2017-201 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 25.5474 | 25.5674 | 0.02
GEN-2017-201 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.1321 | 15.1387 | 0.0066
GEN-2017-201 | 02 NEBRASKA | 635236 | SALIX 8 | 69 | 13.8186 | 13.8208 | 0.0022
GEN-2017-201 | 02 NEBRASKA | 635237 | SLOAN 8 | 69 | 4.9008 | 4.901 | 0.0002
GEN-2017-201 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.8002 | 9.8037 | 0.0035
GEN-2017-201 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.6975 | 5.698 | 0.0005
GEN-2017-201 | 02 NEBRASKA | 635301 | MONONA 8 | 69 | 4.7232 | 4.7234 | 0.0002
GEN-2017-201 | 02 NEBRASKA | 635302 | MAPLTN 8 | 69 | 3.1825 | 3.1825 | 0
GEN-2017-201 | 02 NEBRASKA | 635303 | SMITHLD8 | 69 | 2.4727 | 2.4727 | 0
GEN-2017-201 | 02 NEBRASKA | 635330 | CRWFRD 5 | 161 | 5.0931 | 5.0934 | 0.0003
GEN-2017-201 | 02 NEBRASKA | 635368 | OBRIEN 3 | 345 | 14.4436 | 14.4455 | 0.0019
GEN-2017-201 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 12.5602 | 12.5638 | 0.0036
GEN-2017-201 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 13.189 | 13.1913 | 0.0023
GEN-2017-201 | 02 NEBRASKA | 636010 | LEHIGH 3 | 345 | 13.6337 | 13.6347 | 0.001
GEN-2017-201 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 12.4033 | 12.4068 | 0.0035
GEN-2017-201 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 8.934 | 8.9361 | 0.0021
GEN-2017-201 | 02 NEBRASKA | 640070 | BANCRFT7 | 115 | 5.292 | 5.2936 | 0.0016
GEN-2017-201 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.77 | 7.7891 | 0.0191
GEN-2017-201 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.1015 | 4.1047 | 0.0032
GEN-2017-201 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6154 | 4.6182 | 0.0028
GEN-2017-201 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.356 | 6.3613 | 0.0053
GEN-2017-201 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.9038 | 3.905 | 0.0012
GEN-2017-201 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 6.386 | 6.3878 | 0.0018
GEN-2017-201 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 4.1939 | 4.1944 | 0.0005
GEN-2017-201 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.552 | 5.5564 | 0.0044
GEN-2017-201 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.817 | 7.8339 | 0.0169
GEN-2017-201 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.8084 | 20.8461 | 0.0377
GEN-2017-201 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.5309 | 17.5576 | 0.0267
GEN-2017-201 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 17.6498 | 17.6762 | 0.0264
GEN-2017-201 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6214 | 10.6739 | 0.0525
GEN-2017-201 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.6878 | 10.7096 | 0.0218
GEN-2017-201 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5206 | 23.5717 | 0.0511
GEN-2017-201 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.43 | 10.4489 | 0.0189
GEN-2017-201 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.2229 | 12.2515 | 0.0286
GEN-2017-201 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.7825 | 18.8136 | 0.0311
GEN-2017-201 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.3346 | 20.371 | 0.0364
GEN-2017-201 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 5.2753 | 5.2786 | 0.0033
GEN-2017-201 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.7399 | 4.7415 | 0.0016
GEN-2017-201 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.3037 | 6.3113 | 0.0076
GEN-2017-201 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9503 | 5.9523 | 0.002
GEN-2017-201 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7156 | 5.7177 | 0.0021
GEN-2017-201 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9405 | 3.9411 | 0.0006
GEN-2017-201 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 5.2545 | 5.2566 | 0.0021
GEN-2017-201 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.3532 | 17.3572 | 0.004
GEN-2017-201 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.5969 | 5.5995 | 0.0026
GEN-2017-201 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.7153 | 3.716 | 0.0007
GEN-2017-201 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.4731 | 13.7966 | 0.3235
GEN-2017-201 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.5504 | 10.6375 | 0.0871
GEN-2017-201 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 19.0309 | 19.1673 | 0.1364
GEN-2017-201 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4857 | 6.4957 | 0.01
GEN-2017-201 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.4118 | 11.4138 | 0.002
GEN-2017-201 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.8392 | 23.8497 | 0.0105
GEN-2017-201 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.3496 | 45.3584 | 0.0088
GEN-2017-201 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 11.3335 | 11.3577 | 0.0242
GEN-2017-201 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 6.3713 | 6.3758 | 0.0045
GEN-2017-201 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.8925 | 13.9613 | 0.0688
GEN-2017-201 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 13.0338 | 13.0928 | 0.059
GEN-2017-201 | 02 NEBRASKA | 640305 | ONEILL 7 | 115 | 4.0923 | 4.0931 | 0.0008
GEN-2017-201 | 02 NEBRASKA | 640306 | ONEILL 8 | 69 | 4.4264 | 4.427 | 0.0006
GEN-2017-201 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7804 | 11.782 | 0.0016
GEN-2017-201 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 6.8772 | 6.8809 | 0.0037
GEN-2017-201 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 6.1118 | 6.1142 | 0.0024
GEN-2017-201 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.8772 | 10.9505 | 0.0733
GEN-2017-201 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.4971 | 11.5277 | 0.0306
GEN-2017-201 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.7929 | 4.7941 | 0.0012
GEN-2017-201 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2559 | 4.2565 | 0.0006
GEN-2017-201 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3707 | 5.3776 | 0.0069
GEN-2017-201 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3271 | 7.3434 | 0.0163
GEN-2017-201 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.2741 | 9.2762 | 0.0021
GEN-2017-201 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.5768 | 8.5789 | 0.0021
GEN-2017-201 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3116 | 9.3232 | 0.0116
GEN-2017-201 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2951 | 11.3041 | 0.009
GEN-2017-201 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1653 | 8.1681 | 0.0028
GEN-2017-201 | 02 NEBRASKA | 640400 | W.POINT7 | 115 | 5.2221 | 5.2246 | 0.0025
GEN-2017-201 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 5.0071 | 5.0077 | 0.0006
GEN-2017-201 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7269 | 7.7311 | 0.0042
GEN-2017-201 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7191 | 4.7201 | 0.001
GEN-2017-201 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 6.8881 | 6.8918 | 0.0037
GEN-2017-201 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9757 | 7.0398 | 0.0641
GEN-2017-201 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 16.526 | 16.5908 | 0.0648
GEN-2017-201 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.499 | 5.5033 | 0.0043
GEN-2017-201 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2527 | 12.2547 | 0.002
GEN-2017-201 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.8686 | 5.8711 | 0.0025
GEN-2017-201 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3381 | 8.3548 | 0.0167
GEN-2017-201 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4488 | 7.4609 | 0.0121
GEN-2017-201 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.8347 | 12.1894 | 0.3547
GEN-2017-201 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.5475 | 9.9179 | 0.3704
GEN-2017-201 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.3251 | 23.3349 | 0.0098
GEN-2017-201 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 15.8113 | 15.869 | 0.0577
GEN-2017-201 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.599 | 11.9385 | 0.3395
GEN-2017-201 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.3251 | 29.3302 | 0.0051
GEN-2017-201 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.5856 | 21.5916 | 0.006
GEN-2017-201 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.8435 | 28.8501 | 0.0066
GEN-2017-201 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 31.9404 | 31.9469 | 0.0065
GEN-2017-201 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.4744 | 34.4808 | 0.0064
GEN-2017-201 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.6818 | 30.6853 | 0.0035
GEN-2017-201 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.0739 | 25.0785 | 0.0046
GEN-2017-201 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.8852 | 22.8881 | 0.0029
GEN-2017-201 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 22.9649 | 22.9682 | 0.0033
GEN-2017-201 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.7874 | 44.7914 | 0.004
GEN-2017-201 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 46.7148 | 46.7214 | 0.0066
GEN-2017-201 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 24.8332 | 24.8373 | 0.0041
GEN-2017-201 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 42.8854 | 42.8907 | 0.0053
GEN-2017-201 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 25.0978 | 25.0998 | 0.002
GEN-2017-201 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.2187 | 35.222 | 0.0033
GEN-2017-201 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 31.8276 | 31.8336 | 0.006
GEN-2017-201 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.4577 | 32.461 | 0.0033
GEN-2017-201 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 48.4728 | 48.4794 | 0.0066
GEN-2017-201 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 35.0457 | 35.0492 | 0.0035
GEN-2017-201 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 18.9322 | 18.9337 | 0.0015
GEN-2017-201 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 29.126 | 29.1311 | 0.0051
GEN-2017-201 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 27.7199 | 27.7245 | 0.0046
GEN-2017-201 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 26.9843 | 26.9887 | 0.0044
GEN-2017-201 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 32.7544 | 32.7578 | 0.0034
GEN-2017-201 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.0722 | 27.073 | 0.0008
GEN-2017-201 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 4.4331 | 4.4341 | 0.001
GEN-2017-201 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7653 | 17.7796 | 0.0143
GEN-2017-201 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.2876 | 21.2967 | 0.0091
GEN-2017-201 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.1821 | 21.1898 | 0.0077
GEN-2017-201 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.5815 | 21.5856 | 0.0041
GEN-2017-201 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.8651 | 25.8712 | 0.0061
GEN-2017-201 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.3463 | 22.3501 | 0.0038
GEN-2017-201 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.6089 | 32.6157 | 0.0068
GEN-2017-201 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 26.032 | 26.0363 | 0.0043
GEN-2017-201 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 11.2881 | 11.2901 | 0.002
GEN-2017-201 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 9.9895 | 9.9923 | 0.0028
GEN-2017-201 | 02 NEBRASKA | 652537 | WHITE 3 | 345 | 19.1735 | 19.1738 | 0.0003
GEN-2017-201 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.758 | 20.7766 | 0.0186
GEN-2017-201 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.6416 | 15.6563 | 0.0147
GEN-2017-201 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.758 | 20.7766 | 0.0186
GEN-2017-201 | 02 NEBRASKA | 652566 | SIOUXCY5 | 161 | 21.5401 | 21.5523 | 0.0122
GEN-2017-201 | 02 NEBRASKA | 652567 | DENISON4 | 230 | 5.1299 | 5.1304 | 0.0005
GEN-2017-201 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.459 | 15.4733 | 0.0143
GEN-2017-201 | 02 NEBRASKA | 655126 | MOS-VERM-ER8 | 69 | 2.0215 | 2.0215 | 0
GEN-2017-201 | 02 NEBRASKA | 655129 | SW806-ER8 | 69 | 0.8789 | 0.8789 | 0
GEN-2017-201 | 02 NEBRASKA | 655130 | SW808-ER8 | 69 | 2.5406 | 2.5406 | 0
GEN-2017-201 | 02 NEBRASKA | 655133 | SW822-ER8 | 69 | 2.1955 | 2.1956 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655136 | SW832-ER8 | 69 | 2.6229 | 2.623 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655137 | SW833-ER8 | 69 | 2.0943 | 2.0943 | 0
GEN-2017-201 | 02 NEBRASKA | 655139 | MOS-USD-ER8 | 69 | 1.9135 | 1.9135 | 0
GEN-2017-201 | 02 NEBRASKA | 655144 | SW869-ER8 | 69 | 1.6812 | 1.6812 | 0
GEN-2017-201 | 02 NEBRASKA | 655145 | SW870-ER8 | 69 | 2.8886 | 2.8887 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655146 | SW873-ER8 | 69 | 2.8873 | 2.8874 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655147 | MOS-JEFF-ER8 | 69 | 2.5412 | 2.5413 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655149 | STR810-ER8 | 69 | 1.968 | 1.9681 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655151 | MOS-BGSP-ER8 | 69 | 1.3648 | 1.3648 | 0
GEN-2017-201 | 02 NEBRASKA | 655152 | SW894-ER8 | 69 | 2.0672 | 2.0673 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655168 | SW8105-ER8 | 69 | 2.4696 | 2.4696 | 0
GEN-2017-201 | 02 NEBRASKA | 655308 | ALCESTER-ER8 | 69 | 1.0264 | 1.0264 | 0
GEN-2017-201 | 02 NEBRASKA | 655311 | AKRON-ER8 | 69 | 1.5312 | 1.5312 | 0
GEN-2017-201 | 02 NEBRASKA | 655313 | RICHLAND-ER8 | 69 | 2.5322 | 2.5323 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655314 | ELKPNTCY-ER8 | 69 | 1.9385 | 1.9385 | 0
GEN-2017-201 | 02 NEBRASKA | 655315 | ELKPOINT-ER8 | 69 | 1.9378 | 1.9378 | 0
GEN-2017-201 | 02 NEBRASKA | 655316 | BURBANK-ER8 | 69 | 1.8804 | 1.8805 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655317 | USD-ER8 | 69 | 1.889 | 1.889 | 0
GEN-2017-201 | 02 NEBRASKA | 655323 | GAYVILLE-ER8 | 69 | 1.4797 | 1.4797 | 0
GEN-2017-201 | 02 NEBRASKA | 655325 | DKTADOME-ER8 | 69 | 1.9526 | 1.9526 | 0
GEN-2017-201 | 02 NEBRASKA | 655326 | BGSPRING-ER8 | 69 | 1.1809 | 1.1809 | 0
GEN-2017-201 | 02 NEBRASKA | 655327 | UNIONCRK-ER8 | 69 | 2.0015 | 2.0015 | 0
GEN-2017-201 | 02 NEBRASKA | 655356 | SPRTMND-ER8 | 69 | 2.9769 | 2.9769 | 0
GEN-2017-201 | 02 NEBRASKA | 655357 | MECKLING-ER8 | 69 | 2.3001 | 2.3001 | 0
GEN-2017-201 | 02 NEBRASKA | 655359 | JEFERSON-ER8 | 69 | 1.688 | 1.688 | 0
GEN-2017-201 | 02 NEBRASKA | 655393 | SWR5123-ER8 | 69 | 0.979 | 0.979 | 0
GEN-2017-201 | 02 NEBRASKA | 655427 | MOS-ALC2-ER8 | 69 | 1.0264 | 1.0264 | 0
GEN-2017-201 | 02 NEBRASKA | 655428 | BIGSPRGS-ER8 | 69 | 1.1809 | 1.1809 | 0
GEN-2017-201 | 02 NEBRASKA | 655484 | RASMUSN-ER4 | 230 | 6.9213 | 6.9229 | 0.0016
GEN-2017-201 | 02 NEBRASKA | 655485 | RASMUSN-ER8 | 69 | 3.3183 | 3.3184 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 655502 | SPRTMND-ER7 | 115 | 6.3904 | 6.3906 | 0.0002
GEN-2017-201 | 02 NEBRASKA | 658100 | VERMLN 7 | 115 | 4.5425 | 4.5426 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 658101 | VERMLNE 7 | 115 | 4.5082 | 4.5083 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 658122 | ROCKRPDMUNI8 | 69 | 2.8459 | 2.8459 | 0
GEN-2017-201 | 02 NEBRASKA | 658124 | LUVERNEMUNW8 | 69 | 1.8256 | 1.8256 | 0
GEN-2017-201 | 02 NEBRASKA | 658126 | LUVERNEMUNE8 | 69 | 1.7284 | 1.7284 | 0
GEN-2017-201 | 02 NEBRASKA | 658128 | LUVERNEMUNS8 | 69 | 1.8313 | 1.8313 | 0
GEN-2017-201 | 02 NEBRASKA | 659121 | SPIRIT_M-BE7 | 115 | 6.3904 | 6.3906 | 0.0002
GEN-2017-201 | 02 NEBRASKA | 659286 | DEERCREK-BE3 | 345 | 18.6289 | 18.6291 | 0.0002
GEN-2017-201 | 02 NEBRASKA | 659311 | PAHOJA__-BE4 | 230 | 7.6427 | 7.6435 | 0.0008
GEN-2017-201 | 02 NEBRASKA | 659708 | LITLRCKT-LO8 | 69 | 1.9726 | 1.9726 | 0
GEN-2017-201 | 02 NEBRASKA | 659709 | LITLRCK -LO8 | 69 | 1.9317 | 1.9317 | 0
GEN-2017-201 | 02 NEBRASKA | 659710 | GEORGETP-LO8 | 69 | 2.3898 | 2.3898 | 0
GEN-2017-201 | 02 NEBRASKA | 659711 | GEORGE -LO8 | 69 | 2.328 | 2.328 | 0
GEN-2017-201 | 02 NEBRASKA | 659712 | RKRMUNTP-LO8 | 69 | 3.3898 | 3.3898 | 0
GEN-2017-201 | 02 NEBRASKA | 659714 | RKRPDTAP-LO8 | 69 | 3.6043 | 3.6044 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 659715 | ROCKRPDS-LO8 | 69 | 3.448 | 3.448 | 0
GEN-2017-201 | 02 NEBRASKA | 659726 | STEEN -LO8 | 69 | 2.3476 | 2.3476 | 0
GEN-2017-201 | 02 NEBRASKA | 659727 | LUVERNE -LO8 | 69 | 1.8646 | 1.8646 | 0
GEN-2017-201 | 02 NEBRASKA | 659735 | CLEVELND-LO4 | 230 | 5.1009 | 5.1013 | 0.0004
GEN-2017-201 | 02 NEBRASKA | 659736 | CLEVELND-LO8 | 69 | 4.4447 | 4.4448 | 0.0001
GEN-2017-201 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5104 | 7.5117 | 0.0013
GEN-2017-201 | 02 NEBRASKA | 659901 | EAGLE___-NI8 | 69 | 14.4066 | 14.408 | 0.0014
GEN-2017-201 | 02 NEBRASKA | 660006 | YANKTON JCT7 | 115 | 9.1365 | 9.1385 | 0.002
GEN-2017-201 | 02 NEBRASKA | 760515 | GEN-2017-222 | 230 | 3.7221 | 3.7223 | 0.0002
GEN-2017-201 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.6094 | 8.9813 | 0.3719
GEN-2017-201 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9846 | 9.9861 | 0.0015
GEN-2017-201 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9211 | 6.9216 | 0.0005
GEN-2017-201 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.7838 | 5.7841 | 0.0003
GEN-2017-201 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.6972 | 8.699 | 0.0018
GEN-2017-201 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.6972 | 8.699 | 0.0018
GEN-2017-210 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.8504 | 12.8518 | 0.0014
GEN-2017-210 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.9595 | 16.9601 | 0.0006
GEN-2017-210 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 8.3281 | 8.3298 | 0.0017
GEN-2017-210 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.3619 | 6.3624 | 0.0005
GEN-2017-210 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.6987 | 5.6991 | 0.0004
GEN-2017-210 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.7114 | 18.712 | 0.0006
GEN-2017-210 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 8.5046 | 8.5053 | 0.0007
GEN-2017-210 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 20.6779 | 20.68 | 0.0021
GEN-2017-210 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 20.9818 | 20.9827 | 0.0009
GEN-2017-210 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 19.1094 | 19.1108 | 0.0014
GEN-2017-210 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 8.1128 | 8.1133 | 0.0005
GEN-2017-210 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 8.1128 | 8.1133 | 0.0005
GEN-2017-210 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 8.1128 | 8.1133 | 0.0005
GEN-2017-210 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 10.104 | 10.1052 | 0.0012
GEN-2017-210 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 8.0193 | 8.02 | 0.0007
GEN-2017-210 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 10.046 | 10.0472 | 0.0012
GEN-2017-210 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 6.7602 | 6.7606 | 0.0004
GEN-2017-210 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.4518 | 7.4608 | 0.009
GEN-2017-210 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 43.8234 | 44.0075 | 0.1841
GEN-2017-210 | 02 NEBRASKA | 579450 | GEN-2016-075 | 345 | 5.9089 | 5.9168 | 0.0079
GEN-2017-210 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.2604 | 19.2944 | 0.034
GEN-2017-210 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 7.503 | 7.5245 | 0.0215
GEN-2017-210 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2023 | 12.2547 | 0.0524
GEN-2017-210 | 02 NEBRASKA | 587150 | GEN-2016-021 | 345 | 9.335 | 9.3372 | 0.0022
GEN-2017-210 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.2987 | 6.305 | 0.0063
GEN-2017-210 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.678 | 6.6922 | 0.0142
GEN-2017-210 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 31.9287 | 31.9397 | 0.011
GEN-2017-210 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.68 | 17.688 | 0.008
GEN-2017-210 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.8563 | 16.8633 | 0.007
GEN-2017-210 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.7702 | 16.7771 | 0.0069
GEN-2017-210 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 7.2631 | 7.2823 | 0.0192
GEN-2017-210 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.8616 | 9.8863 | 0.0247
GEN-2017-210 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.8719 | 14.8922 | 0.0203
GEN-2017-210 | 02 NEBRASKA | 640074 | BEAT. S7 | 115 | 5.4732 | 5.4741 | 0.0009
GEN-2017-210 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 13.7378 | 13.7438 | 0.006
GEN-2017-210 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 16.9098 | 16.9188 | 0.009
GEN-2017-210 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 7.3455 | 7.3529 | 0.0074
GEN-2017-210 | 02 NEBRASKA | 640094 | C.CREEK7 | 115 | 7.4274 | 7.4309 | 0.0035
GEN-2017-210 | 02 NEBRASKA | 640102 | CANADAY4 | 230 | 6.4714 | 6.4764 | 0.005
GEN-2017-210 | 02 NEBRASKA | 640105 | CARLJCT7 | 115 | 5.764 | 5.7725 | 0.0085
GEN-2017-210 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.2949 | 5.3001 | 0.0052
GEN-2017-210 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 11.1053 | 11.1118 | 0.0065
GEN-2017-210 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.827 | 20.8461 | 0.0191
GEN-2017-210 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.5441 | 17.5576 | 0.0135
GEN-2017-210 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.659 | 10.6739 | 0.0149
GEN-2017-210 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.6974 | 10.7096 | 0.0122
GEN-2017-210 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5468 | 23.5717 | 0.0249
GEN-2017-210 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.4345 | 10.4489 | 0.0144
GEN-2017-210 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.2351 | 12.2515 | 0.0164
GEN-2017-210 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.7979 | 18.8136 | 0.0157
GEN-2017-210 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.3526 | 20.371 | 0.0184
GEN-2017-210 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.6827 | 27.7084 | 0.0257
GEN-2017-210 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1792 | 18.184 | 0.0048
GEN-2017-210 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6837 | 4.6839 | 0.0002
GEN-2017-210 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.4496 | 8.4605 | 0.0109
GEN-2017-210 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9508 | 5.9523 | 0.0015
GEN-2017-210 | 02 NEBRASKA | 640159 | DONIPHAN_7 | 115 | 11.5429 | 11.5653 | 0.0224
GEN-2017-210 | 02 NEBRASKA | 640160 | DONIPHAN_8 | 69 | 5.0943 | 5.0969 | 0.0026
GEN-2017-210 | 02 NEBRASKA | 640169 | FAIRBRY7 | 115 | 5.2001 | 5.202 | 0.0019
GEN-2017-210 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 7.0217 | 7.0255 | 0.0038
GEN-2017-210 | 02 NEBRASKA | 640174 | FRIEND 7 | 115 | 5.7144 | 5.7239 | 0.0095
GEN-2017-210 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.9508 | 9.9996 | 0.0488
GEN-2017-210 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.313 | 4.3184 | 0.0054
GEN-2017-210 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 16.3169 | 16.3361 | 0.0192
GEN-2017-210 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 19.7731 | 19.7862 | 0.0131
GEN-2017-210 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.1548 | 17.3572 | 0.2024
GEN-2017-210 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.7378 | 23.8884 | 0.1506
GEN-2017-210 | 02 NEBRASKA | 640208 | HARBINE7 | 115 | 6.9954 | 6.9974 | 0.002
GEN-2017-210 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.5908 | 7.6189 | 0.0281
GEN-2017-210 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 19.9356 | 19.9888 | 0.0532
GEN-2017-210 | 02 NEBRASKA | 640218 | HEBRN N7 | 115 | 6.0673 | 6.0731 | 0.0058
GEN-2017-210 | 02 NEBRASKA | 640220 | HEBRON 7 | 115 | 5.7553 | 5.7605 | 0.0052
GEN-2017-210 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.397 | 4.3987 | 0.0017
GEN-2017-210 | 02 NEBRASKA | 640223 | HILDRTH8 | 69 | 3.5539 | 3.5546 | 0.0007
GEN-2017-210 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 6.3187 | 6.3219 | 0.0032
GEN-2017-210 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.7908 | 13.7966 | 0.0058
GEN-2017-210 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.7989 | 9.8096 | 0.0107
GEN-2017-210 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 12.4456 | 12.4617 | 0.0161
GEN-2017-210 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 8.8183 | 8.8226 | 0.0043
GEN-2017-210 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.8326 | 14.8361 | 0.0035
GEN-2017-210 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 9.261 | 9.2623 | 0.0013
GEN-2017-210 | 02 NEBRASKA | 640256 | LXNGTN 7 | 115 | 7.2914 | 7.2945 | 0.0031
GEN-2017-210 | 02 NEBRASKA | 640257 | LEXNGTN8 | 69 | 3.7785 | 3.779 | 0.0005
GEN-2017-210 | 02 NEBRASKA | 640259 | LOUPCTY7 | 115 | 4.3117 | 4.313 | 0.0013
GEN-2017-210 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.7888 | 11.4138 | 0.625
GEN-2017-210 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.5254 | 14.7462 | 0.2208
GEN-2017-210 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.713 | 5.7331 | 0.0201
GEN-2017-210 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.4671 | 7.4727 | 0.0056
GEN-2017-210 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.5974 | 23.8497 | 0.2523
GEN-2017-210 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.1728 | 45.3584 | 0.1856
GEN-2017-210 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 13.4816 | 13.4892 | 0.0076
GEN-2017-210 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.9019 | 7.9038 | 0.0019
GEN-2017-210 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.4669 | 2.4674 | 0.0005
GEN-2017-210 | 02 NEBRASKA | 640311 | ORLEANS8 | 69 | 2.4695 | 2.4698 | 0.0003
GEN-2017-210 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.3365 | 8.3578 | 0.0213
GEN-2017-210 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.8869 | 16.9188 | 0.0319
GEN-2017-210 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9405 | 4.9422 | 0.0017
GEN-2017-210 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7674 | 11.782 | 0.0146
GEN-2017-210 | 02 NEBRASKA | 640323 | RAVENNA7 | 115 | 6.2124 | 6.2181 | 0.0057
GEN-2017-210 | 02 NEBRASKA | 640324 | RAVENNA8 | 69 | 3.871 | 3.8724 | 0.0014
GEN-2017-210 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.5286 | 6.5302 | 0.0016
GEN-2017-210 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 11.729 | 11.7308 | 0.0018
GEN-2017-210 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.572 | 7.5882 | 0.0162
GEN-2017-210 | 02 NEBRASKA | 640331 | RIVERDL7 | 115 | 13.3774 | 13.3997 | 0.0223
GEN-2017-210 | 02 NEBRASKA | 640332 | RIVERDL8 | 69 | 6.7138 | 6.7172 | 0.0034
GEN-2017-210 | 02 NEBRASKA | 640340 | SEWARD 7 | 115 | 7.7149 | 7.725 | 0.0101
GEN-2017-210 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9373 | 10.9505 | 0.0132
GEN-2017-210 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.5142 | 11.5277 | 0.0135
GEN-2017-210 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.7918 | 4.7941 | 0.0023
GEN-2017-210 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2554 | 4.2565 | 0.0011
GEN-2017-210 | 02 NEBRASKA | 640353 | ST.LIB 7 | 115 | 9.9521 | 9.9724 | 0.0203
GEN-2017-210 | 02 NEBRASKA | 640355 | ST.PAUL7 | 115 | 3.9849 | 3.9881 | 0.0032
GEN-2017-210 | 02 NEBRASKA | 640361 | STEINER7 | 115 | 4.6081 | 4.6084 | 0.0003
GEN-2017-210 | 02 NEBRASKA | 640362 | STERLNG7 | 115 | 4.7203 | 4.7218 | 0.0015
GEN-2017-210 | 02 NEBRASKA | 640372 | SUTTON 7 | 115 | 6.5413 | 6.5544 | 0.0131
GEN-2017-210 | 02 NEBRASKA | 640373 | SUTTON 8 | 69 | 3.9292 | 3.932 | 0.0028
GEN-2017-210 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 11.1532 | 11.1977 | 0.0445
GEN-2017-210 | 02 NEBRASKA | 640375 | TAMORA 7 | 115 | 6.1307 | 6.1404 | 0.0097
GEN-2017-210 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.4642 | 9.4678 | 0.0036
GEN-2017-210 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 9.419 | 9.4289 | 0.0099
GEN-2017-210 | 02 NEBRASKA | 640411 | YORK 7 | 115 | 7.837 | 7.8711 | 0.0341
GEN-2017-210 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.3585 | 8.4095 | 0.051
GEN-2017-210 | 02 NEBRASKA | 640415 | CARLJCT8 | 69 | 3.7527 | 3.7548 | 0.0021
GEN-2017-210 | 02 NEBRASKA | 640416 | AURORA_8 | 69 | 4.0833 | 4.0869 | 0.0036
GEN-2017-210 | 02 NEBRASKA | 640443 | YORK 8 | 69 | 2.6693 | 2.6716 | 0.0023
GEN-2017-210 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7814 | 4.7816 | 0.0002
GEN-2017-210 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5262 | 2.5289 | 0.0027
GEN-2017-210 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 3.8363 | 3.837 | 0.0007
GEN-2017-210 | 02 NEBRASKA | 640468 | TAMORA 8 | 69 | 4.1313 | 4.1339 | 0.0026
GEN-2017-210 | 02 NEBRASKA | 640500 | CHERRYC3 | 345 | 5.8659 | 5.8706 | 0.0047
GEN-2017-210 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 7.5581 | 7.5799 | 0.0218
GEN-2017-210 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2023 | 12.2547 | 0.0524
GEN-2017-210 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.8697 | 5.8711 | 0.0014
GEN-2017-210 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.7817 | 6.7865 | 0.0048
GEN-2017-210 | 02 NEBRASKA | 640584 | COTTONWD 7 | 115 | 5.4779 | 5.4809 | 0.003
GEN-2017-210 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 12.1853 | 12.1894 | 0.0041
GEN-2017-210 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.9154 | 9.9179 | 0.0025
GEN-2017-210 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.0996 | 23.3349 | 0.2353
GEN-2017-210 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 43.8234 | 44.0075 | 0.1841
GEN-2017-210 | 02 NEBRASKA | 641085 | E7THST 7 | 115 | 18.8134 | 18.8609 | 0.0475
GEN-2017-210 | 02 NEBRASKA | 641087 | EGYCNTR7 | 115 | 18.6722 | 18.7149 | 0.0427
GEN-2017-210 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 19.9356 | 19.9888 | 0.0532
GEN-2017-210 | 02 NEBRASKA | 641090 | S. 281 7 | 115 | 11.5765 | 11.5937 | 0.0172
GEN-2017-210 | 02 NEBRASKA | 642066 | SUB-H G | 115 | 15.8743 | 15.9286 | 0.0543
GEN-2017-210 | 02 NEBRASKA | 642070 | SUB-C 7 | 115 | 12.6685 | 12.7031 | 0.0346
GEN-2017-210 | 02 NEBRASKA | 642071 | SUB-D 7 | 115 | 17.7735 | 17.8343 | 0.0608
GEN-2017-210 | 02 NEBRASKA | 642072 | SUB-E 7 | 115 | 17.2545 | 17.3222 | 0.0677
GEN-2017-210 | 02 NEBRASKA | 642073 | SUB-F 7 | 115 | 12.8941 | 12.9286 | 0.0345
GEN-2017-210 | 02 NEBRASKA | 642076 | SUB-J 7 | 115 | 16.7387 | 16.7928 | 0.0541
GEN-2017-210 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.9346 | 11.9385 | 0.0039
GEN-2017-210 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.5828 | 21.5916 | 0.0088
GEN-2017-210 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.8215 | 28.8501 | 0.0286
GEN-2017-210 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 31.9212 | 31.9469 | 0.0257
GEN-2017-210 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.4584 | 34.4808 | 0.0224
GEN-2017-210 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.6538 | 30.6853 | 0.0315
GEN-2017-210 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.0671 | 25.0785 | 0.0114
GEN-2017-210 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.8739 | 22.8881 | 0.0142
GEN-2017-210 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.7782 | 44.7914 | 0.0132
GEN-2017-210 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.4483 | 32.461 | 0.0127
GEN-2017-210 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.286 | 10.2874 | 0.0014
GEN-2017-210 | 02 NEBRASKA | 647966 | S966 8 | 69 | 0.4927 | 0.4927 | 0
GEN-2017-210 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 4.4335 | 4.4341 | 0.0006
GEN-2017-210 | 02 NEBRASKA | 648513 | GRPR1 3 | 345 | 5.9089 | 5.9168 | 0.0079
GEN-2017-210 | 02 NEBRASKA | 648520 | GRPR2 3 | 345 | 5.574 | 5.5809 | 0.0069
GEN-2017-210 | 02 NEBRASKA | 648527 | GRPR_DMY_BUS | 345 | 5.9089 | 5.9168 | 0.0079
GEN-2017-210 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.6904 | 17.7796 | 0.0892
GEN-2017-210 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.2078 | 21.2967 | 0.0889
GEN-2017-210 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.0845 | 21.1898 | 0.1053
GEN-2017-210 | 02 NEBRASKA | 650207 | NW56&MORTN7 | 115 | 18.3557 | 18.3808 | 0.0251
GEN-2017-210 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.5494 | 21.5856 | 0.0362
GEN-2017-210 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.8177 | 25.8712 | 0.0535
GEN-2017-210 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.3146 | 22.3501 | 0.0355
GEN-2017-210 | 02 NEBRASKA | 650218 | 3&VANDORN 7 | 115 | 22.1022 | 22.1352 | 0.033
GEN-2017-210 | 02 NEBRASKA | 650229 | 27&PLR 7 | 115 | 20.8648 | 20.8955 | 0.0307
GEN-2017-210 | 02 NEBRASKA | 650230 | 2&N 7 | 115 | 26.2256 | 26.272 | 0.0464
GEN-2017-210 | 02 NEBRASKA | 650238 | 20PIONEERS7 | 115 | 27.6713 | 27.7231 | 0.0518
GEN-2017-210 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 28.124 | 28.1804 | 0.0564
GEN-2017-210 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 23.6132 | 23.6548 | 0.0416
GEN-2017-210 | 02 NEBRASKA | 650247 | 40&BENNET 7 | 115 | 21.6557 | 21.6891 | 0.0334
GEN-2017-210 | 02 NEBRASKA | 650250 | 40&ROKEBY 7 | 115 | 21.4921 | 21.5246 | 0.0325
GEN-2017-210 | 02 NEBRASKA | 650258 | 40&GERTIE 7 | 115 | 23.6102 | 23.647 | 0.0368
GEN-2017-210 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.9033 | 29.9566 | 0.0533
GEN-2017-210 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.7846 | 27.8342 | 0.0496
GEN-2017-210 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.4169 | 25.4589 | 0.042
GEN-2017-210 | 02 NEBRASKA | 650276 | 76&ROKEBY 7 | 115 | 17.9911 | 18.0135 | 0.0224
GEN-2017-210 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.9502 | 21.9769 | 0.0267
GEN-2017-210 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.5517 | 32.6157 | 0.064
GEN-2017-210 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.9885 | 26.0363 | 0.0478
GEN-2017-210 | 02 NEBRASKA | 652532 | GR PRAIRIE 3 | 345 | 6.3574 | 6.3667 | 0.0093
GEN-2017-210 | 02 NEBRASKA | 652832 | GRPRAR1-LNX3 | 345 | 6.3574 | 6.3667 | 0.0093
GEN-2017-210 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.6606 | 12.8946 | 0.234
GEN-2017-210 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.5349 | 12.7631 | 0.2282
GEN-2017-210 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 5.9766 | 5.9775 | 0.0009
GEN-2017-210 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.1413 | 8.142 | 0.0007
GEN-2017-210 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.2691 | 7.2893 | 0.0202
GEN-2017-210 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.9792 | 8.9813 | 0.0021
GEN-2017-210 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.3555 | 9.9861 | 0.6306
GEN-2017-210 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9065 | 6.9216 | 0.0151
GEN-2017-210 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.7737 | 5.7841 | 0.0104
GEN-2017-210 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 8.8069 | 8.8071 | 0.0002
GEN-2017-210 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 17.6212 | 17.6218 | 0.0006
GEN-2017-234 | 02 NEBRASKA | 640054 | ALBION 7 | 115 | 5.7227 | 5.8887 | 0.166
GEN-2017-234 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 7.2797 | 7.2823 | 0.0026
GEN-2017-234 | 02 NEBRASKA | 640089 | BROKENB7 | 115 | 5.1432 | 5.2375 | 0.0943
GEN-2017-234 | 02 NEBRASKA | 640090 | BROKENBG | 69 | 5.0677 | 5.1212 | 0.0535
GEN-2017-234 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 7.3421 | 7.3529 | 0.0108
GEN-2017-234 | 02 NEBRASKA | 640094 | C.CREEK7 | 115 | 7.4129 | 7.4309 | 0.018
GEN-2017-234 | 02 NEBRASKA | 640098 | CALAWAY7 | 115 | 3.8484 | 3.8781 | 0.0297
GEN-2017-234 | 02 NEBRASKA | 640099 | CALAWAY8 | 69 | 3.1171 | 3.1285 | 0.0114
GEN-2017-234 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.2982 | 5.3001 | 0.0019
GEN-2017-234 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 17.6586 | 17.6762 | 0.0176
GEN-2017-234 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5457 | 23.5717 | 0.026
GEN-2017-234 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.7864 | 18.8136 | 0.0272
GEN-2017-234 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.338 | 20.371 | 0.033
GEN-2017-234 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.3094 | 6.3113 | 0.0019
GEN-2017-234 | 02 NEBRASKA | 640176 | FULERTN7 | 115 | 2.7382 | 2.7756 | 0.0374
GEN-2017-234 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 5.208 | 5.2566 | 0.0486
GEN-2017-234 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.3359 | 17.3572 | 0.0213
GEN-2017-234 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.8486 | 23.8884 | 0.0398
GEN-2017-234 | 02 NEBRASKA | 640259 | LOUPCTY7 | 115 | 4.1576 | 4.313 | 0.1554
GEN-2017-234 | 02 NEBRASKA | 640267 | MAXWELS7 | 115 | 6.8417 | 6.8523 | 0.0106
GEN-2017-234 | 02 NEBRASKA | 640284 | N.LOUP 7 | 115 | 3.878 | 4.2394 | 0.3614
GEN-2017-234 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 11.3314 | 11.3577 | 0.0263
GEN-2017-234 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 6.3708 | 6.3758 | 0.005
GEN-2017-234 | 02 NEBRASKA | 640308 | ORD 7 | 115 | 3.216 | 3.3924 | 0.1764
GEN-2017-234 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 6.7992 | 6.8809 | 0.0817
GEN-2017-234 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 6.1124 | 6.1142 | 0.0018
GEN-2017-234 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.7924 | 4.7941 | 0.0017
GEN-2017-234 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2556 | 4.2565 | 0.0009
GEN-2017-234 | 02 NEBRASKA | 640347 | SPALDNG7 | 115 | 3.6827 | 4.016 | 0.3333
GEN-2017-234 | 02 NEBRASKA | 640353 | ST.LIB 7 | 115 | 9.935 | 9.9724 | 0.0374
GEN-2017-234 | 02 NEBRASKA | 640355 | ST.PAUL7 | 115 | 3.9822 | 3.9881 | 0.0059
GEN-2017-234 | 02 NEBRASKA | 640416 | AURORA_8 | 69 | 4.0864 | 4.0869 | 0.0005
GEN-2017-234 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 6.8103 | 6.8918 | 0.0815
GEN-2017-234 | 02 NEBRASKA | 640445 | BROKENBOW.W7 | 115 | 4.2897 | 4.3713 | 0.0816
GEN-2017-234 | 02 NEBRASKA | 640455 | MUDDY CREEK7 | 115 | 4.451 | 4.5411 | 0.0901
GEN-2017-234 | 02 NEBRASKA | 640475 | ORD 8 | 69 | 2.5528 | 2.6162 | 0.0634
GEN-2017-234 | 02 NEBRASKA | 642069 | SUB-B 7 | 115 | 12.6381 | 12.6615 | 0.0234
GEN-2017-234 | 02 NEBRASKA | 642070 | SUB-C 7 | 115 | 12.6824 | 12.7031 | 0.0207
GEN-2017-234 | 02 NEBRASKA | 642071 | SUB-D 7 | 115 | 17.81 | 17.8343 | 0.0243
GEN-2017-234 | 02 NEBRASKA | 642072 | SUB-E 7 | 115 | 17.2963 | 17.3222 | 0.0259
GEN-2017-234 | 02 NEBRASKA | 642073 | SUB-F 7 | 115 | 12.901 | 12.9286 | 0.0276
GEN-2017-234 | 02 NEBRASKA | 761691 | GEN-2017-234 | 115 | 3.4898 | 4.0369 | 0.5471
GEN-2017-234 | 02 NEBRASKA | 761695 | G17-234-TAP | 115 | 3.5989 | 4.1431 | 0.5442
GEN-2017-108 | 03 CENTRAL | 99911 | GI91POI | 69 | 1.9449 | 1.9458 | 0.0009
GEN-2017-108 | 03 CENTRAL | 300034 | 5EDMONS | 161 | 6.5748 | 6.6035 | 0.0287
GEN-2017-108 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 13.1194 | 13.6745 | 0.5551
GEN-2017-108 | 03 CENTRAL | 300082 | 5GEORGE | 161 | 8.1805 | 8.2119 | 0.0314
GEN-2017-108 | 03 CENTRAL | 300108 | 5OSCEOLTP | 161 | 6.5846 | 6.6387 | 0.0541
GEN-2017-108 | 03 CENTRAL | 300110 | 5PITTSV | 161 | 8.7672 | 8.7879 | 0.0207
GEN-2017-108 | 03 CENTRAL | 300117 | 5SEDALA | 161 | 8.7726 | 8.8235 | 0.0509
GEN-2017-108 | 03 CENTRAL | 300124 | 5HOLDENB2 | 161 | 7.7589 | 7.8006 | 0.0417
GEN-2017-108 | 03 CENTRAL | 300320 | 5LEVASY | 161 | 10.5286 | 10.5486 | 0.02
GEN-2017-108 | 03 CENTRAL | 300323 | 2CENTRV | 69 | 4.4728 | 4.4789 | 0.0061
GEN-2017-108 | 03 CENTRAL | 300325 | 2RT Z | 69 | 4.1703 | 4.1738 | 0.0035
GEN-2017-108 | 03 CENTRAL | 300327 | 2ELM | 69 | 4.4465 | 4.4511 | 0.0046
GEN-2017-108 | 03 CENTRAL | 300328 | 2MAGNOL | 69 | 2.2745 | 2.2761 | 0.0016
GEN-2017-108 | 03 CENTRAL | 300331 | 2PITTSV | 69 | 4.4947 | 4.4982 | 0.0035
GEN-2017-108 | 03 CENTRAL | 300334 | 2ROSEHL | 69 | 3.6103 | 3.615 | 0.0047
GEN-2017-108 | 03 CENTRAL | 300336 | 2HOLDEN | 69 | 6.5518 | 6.5637 | 0.0119
GEN-2017-108 | 03 CENTRAL | 300528 | 2DRESDN | 69 | 5.8012 | 5.8086 | 0.0074
GEN-2017-108 | 03 CENTRAL | 300530 | 2GEOGT2 | 69 | 7.7365 | 7.7496 | 0.0131
GEN-2017-108 | 03 CENTRAL | 300534 | 2LINCLN | 69 | 4.8815 | 4.8909 | 0.0094
GEN-2017-108 | 03 CENTRAL | 300541 | 2SEDALI | 69 | 9.5801 | 9.6034 | 0.0233
GEN-2017-108 | 03 CENTRAL | 300555 | 5GRAVOIB1 | 161 | 7.724 | 7.7368 | 0.0128
GEN-2017-108 | 03 CENTRAL | 300557 | 2IVYBND | 69 | 2.7765 | 2.778 | 0.0015
GEN-2017-108 | 03 CENTRAL | 300558 | 2MTHULD | 69 | 2.9545 | 2.9569 | 0.0024
GEN-2017-108 | 03 CENTRAL | 300562 | 2STOVER | 69 | 1.9532 | 1.9543 | 0.0011
GEN-2017-108 | 03 CENTRAL | 300687 | 2APPLTN | 69 | 2.9747 | 2.9788 | 0.0041
GEN-2017-108 | 03 CENTRAL | 300688 | 2AUSTIN | 69 | 4.3566 | 4.3628 | 0.0062
GEN-2017-108 | 03 CENTRAL | 300689 | 2BUTLER | 69 | 6.0286 | 6.04 | 0.0114
GEN-2017-108 | 03 CENTRAL | 300690 | 2BUTLERE | 69 | 4.8269 | 4.8351 | 0.0082
GEN-2017-108 | 03 CENTRAL | 300692 | 2CLINTN | 69 | 13.7104 | 13.8925 | 0.1821
GEN-2017-108 | 03 CENTRAL | 300696 | 2CREIGH | 69 | 4.1443 | 4.1512 | 0.0069
GEN-2017-108 | 03 CENTRAL | 300701 | 2GAINES | 69 | 4.652 | 4.669 | 0.017
GEN-2017-108 | 03 CENTRAL | 300702 | 2LADUE | 69 | 4.0678 | 4.0798 | 0.012
GEN-2017-108 | 03 CENTRAL | 300703 | 2LEETON | 69 | 4.0163 | 4.0284 | 0.0121
GEN-2017-108 | 03 CENTRAL | 300706 | 2PIPER | 69 | 3.7409 | 3.7502 | 0.0093
GEN-2017-108 | 03 CENTRAL | 300789 | 2TRUMAN | 69 | 1.9243 | 1.9267 | 0.0024
GEN-2017-108 | 03 CENTRAL | 300804 | 2DAMSCUS | 69 | 4.5881 | 4.599 | 0.0109
GEN-2017-108 | 03 CENTRAL | 300810 | 2MTZION | 69 | 3.9813 | 3.9914 | 0.0101
GEN-2017-108 | 03 CENTRAL | 300811 | 2OSCEOL | 69 | 6.2057 | 6.2231 | 0.0174
GEN-2017-108 | 03 CENTRAL | 300816 | 5COLLINS | 161 | 6.7027 | 6.7359 | 0.0332
GEN-2017-108 | 03 CENTRAL | 301040 | 5OSCEOL | 161 | 6.569 | 6.6228 | 0.0538
GEN-2017-108 | 03 CENTRAL | 301342 | 5BUTLER | 161 | 6.8872 | 6.916 | 0.0288
GEN-2017-108 | 03 CENTRAL | 301370 | 5TURKEYCRK | 161 | 5.3617 | 5.3845 | 0.0228
GEN-2017-108 | 03 CENTRAL | 301401 | 2TURKEYCRK | 69 | 6.652 | 6.6652 | 0.0132
GEN-2017-108 | 03 CENTRAL | 301402 | 5LOSTVALY | 161 | 7.2634 | 7.3064 | 0.043
GEN-2017-108 | 03 CENTRAL | 301477 | 5OSCEOKCTP | 161 | 6.5831 | 6.6373 | 0.0542
GEN-2017-108 | 03 CENTRAL | 301515 | 5SHARSNV | 161 | 15.4681 | 15.596 | 0.1279
GEN-2017-108 | 03 CENTRAL | 301522 | 5OSCEOKC | 161 | 6.5759 | 6.63 | 0.0541
GEN-2017-108 | 03 CENTRAL | 301561 | 5HOLDENB1 | 161 | 7.7552 | 7.7967 | 0.0415
GEN-2017-108 | 03 CENTRAL | 301626 | 2CLINTNLD | 69 | 13.5319 | 13.7094 | 0.1775
GEN-2017-108 | 03 CENTRAL | 503507 | 2BUTLEREGEN | 69 | 4.8243 | 4.8325 | 0.0082
GEN-2017-108 | 03 CENTRAL | 505498 | STOCKTN5 | 161 | 9.9374 | 9.9649 | 0.0275
GEN-2017-108 | 03 CENTRAL | 505502 | TRUMAN 5 | 161 | 7.4646 | 7.5144 | 0.0498
GEN-2017-108 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6464 | 19.6479 | 0.0015
GEN-2017-108 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.7766 | 17.7815 | 0.0049
GEN-2017-108 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 22.6239 | 22.6421 | 0.0182
GEN-2017-108 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.9807 | 15.9817 | 0.001
GEN-2017-108 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.3075 | 18.3104 | 0.0029
GEN-2017-108 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.7097 | 18.7116 | 0.0019
GEN-2017-108 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5568 | 16.5586 | 0.0018
GEN-2017-108 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7992 | 13.8005 | 0.0013
GEN-2017-108 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.5552 | 22.5589 | 0.0037
GEN-2017-108 | 03 CENTRAL | 532914 | SPRGHL 5 | 161 | 11.1648 | 11.1769 | 0.0121
GEN-2017-108 | 03 CENTRAL | 533262 | BONITA 3 | 115 | 10.1672 | 10.1708 | 0.0036
GEN-2017-108 | 03 CENTRAL | 533267 | SPRINGH3 | 115 | 10.076 | 10.0803 | 0.0043
GEN-2017-108 | 03 CENTRAL | 541138 | CLNTPLT_CAP2 | 69 | 8.3897 | 8.4599 | 0.0702
GEN-2017-108 | 03 CENTRAL | 541146 | SEDLIAW_CAP5 | 161 | 9.0461 | 9.0885 | 0.0424
GEN-2017-108 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.9023 | 20.9599 | 0.0576
GEN-2017-108 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.084 | 19.1273 | 0.0433
GEN-2017-108 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.972 | 22.0014 | 0.0294
GEN-2017-108 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 16.4964 | 16.7169 | 0.2205
GEN-2017-108 | 03 CENTRAL | 541209 | SEDALIA5 | 161 | 9.5449 | 9.5922 | 0.0473
GEN-2017-108 | 03 CENTRAL | 541210 | MARTCTY5 | 161 | 28.2742 | 28.3481 | 0.0739
GEN-2017-108 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 7.5616 | 7.6608 | 0.0992
GEN-2017-108 | 03 CENTRAL | 541223 | GRDVWE 5 | 161 | 20.5143 | 20.5516 | 0.0373
GEN-2017-108 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 34.8457 | 34.9521 | 0.1064
GEN-2017-108 | 03 CENTRAL | 541239 | HSNVL 5 | 161 | 15.6115 | 15.7418 | 0.1303
GEN-2017-108 | 03 CENTRAL | 541240 | ADRIAN 5 | 161 | 8.4751 | 8.525 | 0.0499
GEN-2017-108 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.6296 | 7.6519 | 0.0223
GEN-2017-108 | 03 CENTRAL | 541242 | CLINTON5 | 161 | 13.0714 | 13.6224 | 0.551
GEN-2017-108 | 03 CENTRAL | 541271 | SEDN 2 | 69 | 7.3895 | 7.4018 | 0.0123
GEN-2017-108 | 03 CENTRAL | 541272 | SEDS 2 | 69 | 6.5847 | 6.5946 | 0.0099
GEN-2017-108 | 03 CENTRAL | 541287 | MARTCTY2 | 69 | 7.3498 | 7.3521 | 0.0023
GEN-2017-108 | 03 CENTRAL | 541291 | FREEMAN2 | 69 | 4.5286 | 4.5314 | 0.0028
GEN-2017-108 | 03 CENTRAL | 541292 | ANCONDA2 | 69 | 6.4272 | 6.4335 | 0.0063
GEN-2017-108 | 03 CENTRAL | 541295 | HSNVL 2 | 69 | 8.5038 | 8.5151 | 0.0113
GEN-2017-108 | 03 CENTRAL | 541300 | POSTOAK2 | 69 | 4.375 | 4.3855 | 0.0105
GEN-2017-108 | 03 CENTRAL | 541301 | CLNTPLT2 | 69 | 8.5677 | 8.6409 | 0.0732
GEN-2017-108 | 03 CENTRAL | 541302 | CLNTGRN2 | 69 | 8.3037 | 8.3741 | 0.0704
GEN-2017-108 | 03 CENTRAL | 541303 | CLNTN N2 | 69 | 8.0936 | 8.1628 | 0.0692
GEN-2017-108 | 03 CENTRAL | 541304 | URICHTP2 | 69 | 3.2157 | 3.2234 | 0.0077
GEN-2017-108 | 03 CENTRAL | 541305 | URICH 2 | 69 | 2.3071 | 2.311 | 0.0039
GEN-2017-108 | 03 CENTRAL | 541314 | NWARSAW5 | 161 | 7.2481 | 7.2909 | 0.0428
GEN-2017-108 | 03 CENTRAL | 541315 | NWARSAW2 | 69 | 3.5317 | 3.5356 | 0.0039
GEN-2017-108 | 03 CENTRAL | 541320 | CLNTN S2 | 69 | 8.3574 | 8.4289 | 0.0715
GEN-2017-108 | 03 CENTRAL | 541337 | WAFBE_SW5 | 161 | 6.6548 | 6.6718 | 0.017
GEN-2017-108 | 03 CENTRAL | 541338 | WAFBE5 | 161 | 6.0616 | 6.0758 | 0.0142
GEN-2017-108 | 03 CENTRAL | 541340 | BELTONS5 | 161 | 19.6215 | 19.6777 | 0.0562
GEN-2017-108 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 21.0721 | 21.184 | 0.1119
GEN-2017-108 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 23.2164 | 23.3053 | 0.0889
GEN-2017-108 | 03 CENTRAL | 541343 | S.HARP 2 | 69 | 4.5798 | 4.5826 | 0.0028
GEN-2017-108 | 03 CENTRAL | 541344 | PECULRS5 | 161 | 21.6966 | 21.789 | 0.0924
GEN-2017-108 | 03 CENTRAL | 541382 | HONEYWL5 | 161 | 22.8455 | 22.8984 | 0.0529
GEN-2017-108 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 7.1611 | 7.1808 | 0.0197
GEN-2017-108 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.536 | 19.5592 | 0.0232
GEN-2017-108 | 03 CENTRAL | 541540 | FREEMAN_SP2 | 69 | 4.2215 | 4.2239 | 0.0024
GEN-2017-108 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2017-108 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 35.4613 | 35.493 | 0.0317
GEN-2017-108 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 30.7952 | 30.8392 | 0.044
GEN-2017-108 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.639 | 28.678 | 0.039
GEN-2017-108 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.3567 | 30.3737 | 0.017
GEN-2017-108 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.9397 | 26.0141 | 0.0744
GEN-2017-108 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.7871 | 40.9926 | 0.2055
GEN-2017-108 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.4375 | 24.4621 | 0.0246
GEN-2017-108 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 44.6165 | 44.6667 | 0.0502
GEN-2017-108 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5399 | 27.5599 | 0.02
GEN-2017-108 | 03 CENTRAL | 542992 | BENDIX 5 | 161 | 30.3632 | 30.4037 | 0.0405
GEN-2017-108 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 37.4756 | 37.5409 | 0.0653
GEN-2017-108 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 20.0442 | 20.0703 | 0.0261
GEN-2017-108 | 03 CENTRAL | 542996 | MIDTOWN5 | 161 | 35.895 | 35.9339 | 0.0389
GEN-2017-108 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 35.7643 | 35.8009 | 0.0366
GEN-2017-108 | 03 CENTRAL | 542998 | LVISTA 5 | 161 | 24.4685 | 24.4943 | 0.0258
GEN-2017-108 | 03 CENTRAL | 543001 | FOREST 5 | 161 | 32.1159 | 32.1522 | 0.0363
GEN-2017-108 | 03 CENTRAL | 543002 | MARTCIT5 | 161 | 25.2629 | 25.325 | 0.0621
GEN-2017-108 | 03 CENTRAL | 543007 | SWOPE S5 | 161 | 22.2495 | 22.2668 | 0.0173
GEN-2017-108 | 03 CENTRAL | 543008 | BUNKRDG5 | 161 | 24.5207 | 24.5473 | 0.0266
GEN-2017-108 | 03 CENTRAL | 543010 | WINJT S5 | 161 | 23.8303 | 23.8501 | 0.0198
GEN-2017-108 | 03 CENTRAL | 543035 | TOMHAWK5 | 161 | 25.8338 | 25.8607 | 0.0269
GEN-2017-108 | 03 CENTRAL | 543036 | OLATHE 5 | 161 | 27.5529 | 27.5824 | 0.0295
GEN-2017-108 | 03 CENTRAL | 543043 | MURLEN 5 | 161 | 18.5746 | 18.5862 | 0.0116
GEN-2017-108 | 03 CENTRAL | 543045 | SWITZER5 | 161 | 19.9275 | 19.9418 | 0.0143
GEN-2017-108 | 03 CENTRAL | 543046 | OXFORD 5 | 161 | 21.3364 | 21.3643 | 0.0279
GEN-2017-108 | 03 CENTRAL | 543048 | COLLEGE5 | 161 | 30.8582 | 30.8867 | 0.0285
GEN-2017-108 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 31.2925 | 31.3159 | 0.0234
GEN-2017-108 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2324 | 23.2809 | 0.0485
GEN-2017-108 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.0926 | 25.1614 | 0.0688
GEN-2017-108 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8816 | 10.8838 | 0.0022
GEN-2017-108 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 20.9979 | 21.0447 | 0.0468
GEN-2017-108 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3251 | 9.3343 | 0.0092
GEN-2017-108 | 03 CENTRAL | 543067 | CENTENL5 | 161 | 10.8273 | 10.8329 | 0.0056
GEN-2017-108 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.4935 | 14.5118 | 0.0183
GEN-2017-108 | 03 CENTRAL | 543069 | PAOLA 5 | 161 | 10.9255 | 10.9303 | 0.0048
GEN-2017-108 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.2071 | 10.2093 | 0.0022
GEN-2017-108 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.4263 | 29.442 | 0.0157
GEN-2017-108 | 03 CENTRAL | 543112 | OSAWAT 5 | 161 | 10.8329 | 10.8375 | 0.0046
GEN-2017-108 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8431 | 13.8632 | 0.0201
GEN-2017-108 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.3461 | 22.3562 | 0.0101
GEN-2017-108 | 03 CENTRAL | 543135 | OSAWTM_CAP5 | 161 | 10.1937 | 10.1978 | 0.0041
GEN-2017-108 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8175 | 26.8364 | 0.0189
GEN-2017-108 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8175 | 26.8364 | 0.0189
GEN-2017-108 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8156 | 2.8156 | 0
GEN-2017-108 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2017-108 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2017-108 | 03 CENTRAL | 760914 | GEN-2017-209 | 345 | 19.2002 | 19.209 | 0.0088
GEN-2017-108 | 03 CENTRAL | 760921 | G17-209-TAP | 345 | 19.702 | 19.7113 | 0.0093
GEN-2017-108 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 6.0082 | 7.3625 | 1.3543
GEN-2017-108 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 10.9118 | 12.1404 | 1.2286
GEN-2017-108 | 03 CENTRAL | 761901 | GEN-2017-125 | 345 | 5.3329 | 5.3333 | 0.0004
GEN-2017-108 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.5608 | 28.5995 | 0.0387
GEN-2017-115 | 03 CENTRAL | 85831 | J583 | 345 | 6.1897 | 6.19 | 0.0003
GEN-2017-115 | 03 CENTRAL | 300039 | 7FAIRPT | 345 | 12.9008 | 12.9083 | 0.0075
GEN-2017-115 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 18.2127 | 18.213 | 0.0003
GEN-2017-115 | 03 CENTRAL | 300076 | 5FAIRPTB2 | 161 | 16.8648 | 16.8683 | 0.0035
GEN-2017-115 | 03 CENTRAL | 301347 | 5WINSLOW | 161 | 8.9337 | 8.9346 | 0.0009
GEN-2017-115 | 03 CENTRAL | 301559 | 5FAIRPTXF3 | 161 | 16.8831 | 16.8866 | 0.0035
GEN-2017-115 | 03 CENTRAL | 345088 | 7MCCREDIE | 345 | 14.2494 | 14.2495 | 0.0001
GEN-2017-115 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 16.4548 | 16.4553 | 0.0005
GEN-2017-115 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.4857 | 22.486 | 0.0003
GEN-2017-115 | 03 CENTRAL | 541147 | ST JOE_CAP5 | 161 | 18.7391 | 18.7432 | 0.0041
GEN-2017-115 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 11.5923 | 11.7132 | 0.1209
GEN-2017-115 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.9576 | 20.9599 | 0.0023
GEN-2017-115 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 20.7654 | 20.7783 | 0.0129
GEN-2017-115 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.124 | 19.1273 | 0.0033
GEN-2017-115 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.988 | 22.0014 | 0.0134
GEN-2017-115 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.5366 | 27.5409 | 0.0043
GEN-2017-115 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 34.9501 | 34.9521 | 0.002
GEN-2017-115 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 29.1084 | 29.1127 | 0.0043
GEN-2017-115 | 03 CENTRAL | 541253 | ST JOE 5 | 161 | 21.0167 | 21.0218 | 0.0051
GEN-2017-115 | 03 CENTRAL | 541257 | COOK 5 | 161 | 14.6553 | 14.6577 | 0.0024
GEN-2017-115 | 03 CENTRAL | 541258 | WOODBIN5 | 161 | 17.657 | 17.6606 | 0.0036
GEN-2017-115 | 03 CENTRAL | 541394 | AVENUECTY 5 | 161 | 6.4027 | 6.4031 | 0.0004
GEN-2017-115 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 19.167 | 19.1752 | 0.0082
GEN-2017-115 | 03 CENTRAL | 541401 | EASTOWN5 | 161 | 18.0547 | 18.0582 | 0.0035
GEN-2017-115 | 03 CENTRAL | 541411 | MC REAC1 | 345 | 10.8803 | 10.9865 | 0.1062
GEN-2017-115 | 03 CENTRAL | 541412 | MC REAC2 | 345 | 10.8803 | 10.9865 | 0.1062
GEN-2017-115 | 03 CENTRAL | 541413 | MC REAC3 | 345 | 10.8803 | 10.9865 | 0.1062
GEN-2017-115 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.5487 | 19.5592 | 0.0105
GEN-2017-115 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 9.2961 | 9.3311 | 0.035
GEN-2017-115 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 8.1492 | 8.1756 | 0.0264
GEN-2017-115 | 03 CENTRAL | 541510 | HOLT 7 | 345 | 17.8591 | 18.2602 | 0.4011
GEN-2017-115 | 03 CENTRAL | 541511 | ROCKCK7 | 345 | 11.4143 | 11.5519 | 0.1376
GEN-2017-115 | 03 CENTRAL | 541517 | HOLT_REACT7 | 345 | 17.6795 | 18.0725 | 0.393
GEN-2017-115 | 03 CENTRAL | 541543 | OUTLAW | 345 | 8.756 | 8.8293 | 0.0733
GEN-2017-115 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.723 | 23.7308 | 0.0078
GEN-2017-115 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.2333 | 23.2402 | 0.0069
GEN-2017-115 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 31.5503 | 31.5568 | 0.0065
GEN-2017-115 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 60.1099 | 60.12 | 0.0101
GEN-2017-115 | 03 CENTRAL | 560746 | G13-002-TAP | 115 | 42.7013 | 42.7141 | 0.0128
GEN-2017-115 | 03 CENTRAL | 583700 | GEN-2013-019 | 115 | 18.462 | 18.4644 | 0.0024
GEN-2017-115 | 03 CENTRAL | 585241 | GEN-2015-088 | 345 | 11.2735 | 11.2763 | 0.0028
GEN-2017-115 | 03 CENTRAL | 635000 | CBLUFFS3 | 345 | 31.8405 | 31.8547 | 0.0142
GEN-2017-115 | 03 CENTRAL | 635001 | CBLUFFS5 | 161 | 39.4565 | 39.4659 | 0.0094
GEN-2017-115 | 03 CENTRAL | 635002 | CBLUFFS8 | 69 | 25.1538 | 25.1553 | 0.0015
GEN-2017-115 | 03 CENTRAL | 635011 | INDNCRK5 | 161 | 21.931 | 21.9338 | 0.0028
GEN-2017-115 | 03 CENTRAL | 635013 | PNYCRK 3 | 345 | 29.0164 | 29.0284 | 0.012
GEN-2017-115 | 03 CENTRAL | 635014 | OVRLND 3 | 345 | 27.2608 | 27.271 | 0.0102
GEN-2017-115 | 03 CENTRAL | 635015 | OVRLND 5 | 161 | 31.3459 | 31.3518 | 0.0059
GEN-2017-115 | 03 CENTRAL | 635016 | STHLND 3 | 345 | 28.9813 | 28.9933 | 0.012
GEN-2017-115 | 03 CENTRAL | 635017 | ATCHSN 3 | 345 | 22.6006 | 22.8172 | 0.2166
GEN-2017-115 | 03 CENTRAL | 635018 | WESTBORO 3 | 345 | 20.9664 | 21.1428 | 0.1764
GEN-2017-115 | 03 CENTRAL | 635030 | RIVRBND5 | 161 | 35.9717 | 35.9795 | 0.0078
GEN-2017-115 | 03 CENTRAL | 635100 | RLHILLS3 | 345 | 13.5775 | 13.5824 | 0.0049
GEN-2017-115 | 03 CENTRAL | 635200 | RAUN 3 | 345 | 25.8174 | 25.8185 | 0.0011
GEN-2017-115 | 03 CENTRAL | 635570 | ORIENT 3 | 345 | 18.754 | 18.7662 | 0.0122
GEN-2017-115 | 03 CENTRAL | 635589 | ECLIPSE3 | 345 | 9.3881 | 9.3888 | 0.0007
GEN-2017-115 | 03 CENTRAL | 635590 | FALLOW 3 | 345 | 11.4537 | 11.4548 | 0.0011
GEN-2017-115 | 03 CENTRAL | 637084 | J476 SHENHLL | 345 | 20.8295 | 21.0035 | 0.174
GEN-2017-115 | 03 CENTRAL | 640088 | BPS SUB7 | 115 | 16.8703 | 16.871 | 0.0007
GEN-2017-115 | 03 CENTRAL | 640111 | CLATONA7 | 115 | 11.0723 | 11.0728 | 0.0005
GEN-2017-115 | 03 CENTRAL | 640125 | COLMB.E3 | 345 | 10.1239 | 10.1248 | 0.0009
GEN-2017-115 | 03 CENTRAL | 640139 | COOPER 3 | 345 | 29.5777 | 29.7225 | 0.1448
GEN-2017-115 | 03 CENTRAL | 640140 | COOPER 5 | 161 | 18.4519 | 18.473 | 0.0211
GEN-2017-115 | 03 CENTRAL | 640141 | COOPER_ESST8 | 69 | 4.6914 | 4.692 | 0.0006
GEN-2017-115 | 03 CENTRAL | 640143 | COOPER_602 8 | 69 | 2.0097 | 2.0097 | 0
GEN-2017-115 | 03 CENTRAL | 640153 | CRETE__7 | 115 | 8.4218 | 8.4222 | 0.0004
GEN-2017-115 | 03 CENTRAL | 640171 | FIRTH 7 | 115 | 6.9987 | 6.999 | 0.0003
GEN-2017-115 | 03 CENTRAL | 640234 | HUMBOLT5 | 161 | 7.9856 | 7.9869 | 0.0013
GEN-2017-115 | 03 CENTRAL | 640271 | MCCOOL 3 | 345 | 11.0485 | 11.05 | 0.0015
GEN-2017-115 | 03 CENTRAL | 640272 | MCCOOL 7 | 115 | 14.5845 | 14.5853 | 0.0008
GEN-2017-115 | 03 CENTRAL | 640273 | MCCOOL 8 | 69 | 5.7184 | 5.7184 | 0
GEN-2017-115 | 03 CENTRAL | 640277 | MOORE 3 | 345 | 22.8655 | 22.8814 | 0.0159
GEN-2017-115 | 03 CENTRAL | 640278 | SHELDON7 | 115 | 44.1412 | 44.154 | 0.0128
GEN-2017-115 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 8.0342 | 8.0347 | 0.0005
GEN-2017-115 | 03 CENTRAL | 640446 | COOPER 8 | 69 | 4.7894 | 4.79 | 0.0006
GEN-2017-115 | 03 CENTRAL | 640525 | TOBIAS 3 | 345 | 11.2735 | 11.2763 | 0.0028
GEN-2017-115 | 03 CENTRAL | 640590 | MONOLITH 3 | 345 | 22.4118 | 22.4274 | 0.0156
GEN-2017-115 | 03 CENTRAL | 640591 | MONOLITH 7 | 115 | 42.7013 | 42.7141 | 0.0128
GEN-2017-115 | 03 CENTRAL | 645100 | FC1A 5 | 161 | 29.2169 | 29.2223 | 0.0054
GEN-2017-115 | 03 CENTRAL | 645451 | S3451 3 | 345 | 21.4637 | 21.4705 | 0.0068
GEN-2017-115 | 03 CENTRAL | 645454 | S3454 3 | 345 | 28.6383 | 28.6568 | 0.0185
GEN-2017-115 | 03 CENTRAL | 645455 | S3455 3 | 345 | 31.7411 | 31.7629 | 0.0218
GEN-2017-115 | 03 CENTRAL | 645456 | S3456 3 | 345 | 34.2823 | 34.3064 | 0.0241
GEN-2017-115 | 03 CENTRAL | 645458 | S3458 3 | 345 | 30.6022 | 30.7028 | 0.1006
GEN-2017-115 | 03 CENTRAL | 645459 | S3459 3 | 345 | 24.9562 | 24.9669 | 0.0107
GEN-2017-115 | 03 CENTRAL | 645740 | S3740 3 | 345 | 22.7863 | 22.8026 | 0.0163
GEN-2017-115 | 03 CENTRAL | 645761 | S3761 3 | 345 | 22.8631 | 22.8741 | 0.011
GEN-2017-115 | 03 CENTRAL | 646201 | S1201 5 | 161 | 31.7722 | 31.778 | 0.0058
GEN-2017-115 | 03 CENTRAL | 646206 | S1206 5 | 161 | 44.6529 | 44.6662 | 0.0133
GEN-2017-115 | 03 CENTRAL | 646209 | S1209 5 | 161 | 46.5366 | 46.5516 | 0.015
GEN-2017-115 | 03 CENTRAL | 646216 | S1216 5 | 161 | 30.598 | 30.6042 | 0.0062
GEN-2017-115 | 03 CENTRAL | 646217 | S1217 5 | 161 | 33.2377 | 33.2448 | 0.0071
GEN-2017-115 | 03 CENTRAL | 646220 | S1220 5 | 161 | 28.448 | 28.4526 | 0.0046
GEN-2017-115 | 03 CENTRAL | 646221 | S1221 5 | 161 | 35.2415 | 35.2508 | 0.0093
GEN-2017-115 | 03 CENTRAL | 646229 | S1229 5 | 161 | 28.7482 | 28.753 | 0.0048
GEN-2017-115 | 03 CENTRAL | 646231 | S1231 5 | 161 | 42.7352 | 42.7482 | 0.013
GEN-2017-115 | 03 CENTRAL | 646232 | S1232 5 | 161 | 26.6498 | 26.6548 | 0.005
GEN-2017-115 | 03 CENTRAL | 646233 | S1233 5 | 161 | 29.2387 | 29.2455 | 0.0068
GEN-2017-115 | 03 CENTRAL | 646244 | S1244 5 | 161 | 22.2062 | 22.2097 | 0.0035
GEN-2017-115 | 03 CENTRAL | 646249 | S1249 5 | 161 | 25.0389 | 25.044 | 0.0051
GEN-2017-115 | 03 CENTRAL | 646250 | S1250 5 | 161 | 35.126 | 35.1331 | 0.0071
GEN-2017-115 | 03 CENTRAL | 646251 | S1251 5 | 161 | 31.7001 | 31.7065 | 0.0064
GEN-2017-115 | 03 CENTRAL | 646254 | S1254 5 | 161 | 32.3577 | 32.3665 | 0.0088
GEN-2017-115 | 03 CENTRAL | 646255 | S1255 5 | 161 | 48.2742 | 48.2938 | 0.0196
GEN-2017-115 | 03 CENTRAL | 646259 | S1259 5 | 161 | 38.2155 | 38.227 | 0.0115
GEN-2017-115 | 03 CENTRAL | 646263 | S1263 5 | 161 | 8.1059 | 8.1077 | 0.0018
GEN-2017-115 | 03 CENTRAL | 646278 | S1278 5 | 161 | 27.4133 | 27.419 | 0.0057
GEN-2017-115 | 03 CENTRAL | 646280 | S1280 5 | 161 | 10.3188 | 10.3221 | 0.0033
GEN-2017-115 | 03 CENTRAL | 646281 | S1281 5 | 161 | 34.9389 | 34.9483 | 0.0094
GEN-2017-115 | 03 CENTRAL | 646286 | S1286 5 | 161 | 26.5887 | 26.5927 | 0.004
GEN-2017-115 | 03 CENTRAL | 646347 | S1347 5 | 161 | 32.6665 | 32.6734 | 0.0069
GEN-2017-115 | 03 CENTRAL | 646361 | S1361 5 | 161 | 40.1501 | 40.1629 | 0.0128
GEN-2017-115 | 03 CENTRAL | 646366 | S1366 5 | 161 | 16.3804 | 16.3825 | 0.0021
GEN-2017-115 | 03 CENTRAL | 647006 | S906 N 8 | 69 | 32.5661 | 32.5687 | 0.0026
GEN-2017-115 | 03 CENTRAL | 647015 | S6815T1&T2 8 | 69 | 12.0951 | 12.0954 | 0.0003
GEN-2017-115 | 03 CENTRAL | 647016 | 6815TP38 | 69 | 17.5928 | 17.5937 | 0.0009
GEN-2017-115 | 03 CENTRAL | 647017 | 6815TP98 | 69 | 12.6845 | 12.6849 | 0.0004
GEN-2017-115 | 03 CENTRAL | 647815 | S6815T3 8 | 69 | 11.4544 | 11.4548 | 0.0004
GEN-2017-115 | 03 CENTRAL | 647874 | S6874 8 | 69 | 8.6336 | 8.6338 | 0.0002
GEN-2017-115 | 03 CENTRAL | 647901 | S901 8 | 69 | 26.8924 | 26.8936 | 0.0012
GEN-2017-115 | 03 CENTRAL | 647904 | S904 8 | 69 | 8.7518 | 8.7521 | 0.0003
GEN-2017-115 | 03 CENTRAL | 647906 | S906 S 8 | 69 | 33.0642 | 33.0669 | 0.0027
GEN-2017-115 | 03 CENTRAL | 647909 | S909 8 | 69 | 27.0478 | 27.0497 | 0.0019
GEN-2017-115 | 03 CENTRAL | 647916 | S916 8 | 69 | 23.8 | 23.8015 | 0.0015
GEN-2017-115 | 03 CENTRAL | 647924 | S924 8 | 69 | 24.5938 | 24.5952 | 0.0014
GEN-2017-115 | 03 CENTRAL | 647928 | S928 8 | 69 | 17.2745 | 17.2753 | 0.0008
GEN-2017-115 | 03 CENTRAL | 647938 | S938 8 | 69 | 21.8652 | 21.8664 | 0.0012
GEN-2017-115 | 03 CENTRAL | 647995 | S995 8 | 69 | 9.5146 | 9.5148 | 0.0002
GEN-2017-115 | 03 CENTRAL | 650114 | NW68HOLDRG3 | 345 | 17.321 | 17.3287 | 0.0077
GEN-2017-115 | 03 CENTRAL | 650185 | WAGENER 3 | 345 | 20.8682 | 20.8814 | 0.0132
GEN-2017-115 | 03 CENTRAL | 650189 | 103&ROKEBY3 | 345 | 20.7161 | 20.7319 | 0.0158
GEN-2017-115 | 03 CENTRAL | 650214 | NW68HOLDRG7 | 115 | 25.6175 | 25.6218 | 0.0043
GEN-2017-115 | 03 CENTRAL | 650242 | FOLSM&PHIL7 | 115 | 27.8805 | 27.8854 | 0.0049
GEN-2017-115 | 03 CENTRAL | 650246 | SW7&BENNET7 | 115 | 23.4242 | 23.4277 | 0.0035
GEN-2017-115 | 03 CENTRAL | 650267 | 84LEIGHTON7 | 115 | 29.6849 | 29.6907 | 0.0058
GEN-2017-115 | 03 CENTRAL | 650271 | 81&OCHENEY7 | 115 | 25.2418 | 25.246 | 0.0042
GEN-2017-115 | 03 CENTRAL | 650279 | 120&ALVO 7 | 115 | 21.8407 | 21.8439 | 0.0032
GEN-2017-115 | 03 CENTRAL | 650285 | WAGENER 7 | 115 | 32.2936 | 32.3012 | 0.0076
GEN-2017-115 | 03 CENTRAL | 653571 | GR ISLD3 | 345 | 12.3512 | 12.3521 | 0.0009
GEN-2017-115 | 03 CENTRAL | 760746 | GEN-2017-115 | 345 | 12.1521 | 12.5586 | 0.4065
GEN-2017-115 | 03 CENTRAL | 760872 | GEN-2017-198 | 69 | 25.4616 | 25.4628 | 0.0012
GEN-2017-115 | 03 CENTRAL | 761208 | GEN-2017-210 | 345 | 9.6769 | 9.6781 | 0.0012
GEN-2017-115 | 03 CENTRAL | 761292 | GEN-2017-181 | 345 | 6.6267 | 6.6276 | 0.0009
GEN-2017-115 | 03 CENTRAL | 761313 | GEN-2017-182 | 345 | 5.5792 | 5.5798 | 0.0006
GEN-2017-115 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.8093 | 8.8104 | 0.0011
GEN-2017-115 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.6324 | 17.6377 | 0.0053
GEN-2017-115 | 03 CENTRAL | 992001 | VSC2_1 | 276 | 5.7605 | 5.7605 | 0
GEN-2017-115 | 03 CENTRAL | 992002 | VSC2_2 | 276 | 5.7605 | 5.7605 | 0
GEN-2017-115 | 03 CENTRAL | 992003 | VSC2_3 | 345 | 7.1233 | 7.1234 | 0.0001
GEN-2017-115 | 03 CENTRAL | 992005 | VSC2_5 | 276 | 5.7605 | 5.7605 | 0
GEN-2017-115 | 03 CENTRAL | 992006 | VSC2_6 | 276 | 5.7605 | 5.7605 | 0
GEN-2017-119 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 7.0643 | 7.0716 | 0.0073
GEN-2017-119 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 6.169 | 6.1744 | 0.0054
GEN-2017-119 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 6.5353 | 6.5413 | 0.006
GEN-2017-119 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 11.9625 | 11.9665 | 0.004
GEN-2017-119 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 16.5276 | 16.5377 | 0.0101
GEN-2017-119 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.7967 | 24.8418 | 0.0451
GEN-2017-119 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.547 | 10.6006 | 0.0536
GEN-2017-119 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.6546 | 13.6661 | 0.0115
GEN-2017-119 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6512 | 11.6973 | 0.0461
GEN-2017-119 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.4498 | 11.6284 | 0.1786
GEN-2017-119 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 25.0636 | 25.0892 | 0.0256
GEN-2017-119 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.915 | 13.9216 | 0.0066
GEN-2017-119 | 03 CENTRAL | 532852 | JEC 6 | 230 | 25.9435 | 25.9872 | 0.0437
GEN-2017-119 | 03 CENTRAL | 532861 | EMANHAT6 | 230 | 10.5469 | 10.5859 | 0.039
GEN-2017-119 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.5047 | 14.5206 | 0.0159
GEN-2017-119 | 03 CENTRAL | 532865 | NMANHT6 | 230 | 9.6251 | 9.6663 | 0.0412
GEN-2017-119 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0346 | 9.0493 | 0.0147
GEN-2017-119 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 8.1754 | 8.1931 | 0.0177
GEN-2017-119 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.7602 | 13.8406 | 0.0804
GEN-2017-119 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.4636 | 8.4778 | 0.0142
GEN-2017-119 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 5.0411 | 5.0452 | 0.0041
GEN-2017-119 | 03 CENTRAL | 533320 | CLAYCSS3 | 115 | 2.4362 | 2.437 | 0.0008
GEN-2017-119 | 03 CENTRAL | 533323 | CLAYCTR3 | 115 | 3.1047 | 3.1059 | 0.0012
GEN-2017-119 | 03 CENTRAL | 533324 | TCRILEY 3 | 115 | 2.1373 | 2.1379 | 0.0006
GEN-2017-119 | 03 CENTRAL | 533325 | CLAYGEN3 | 115 | 2.3634 | 2.3641 | 0.0007
GEN-2017-119 | 03 CENTRAL | 533326 | EMANHAT3 | 115 | 14.0945 | 14.1275 | 0.033
GEN-2017-119 | 03 CENTRAL | 533327 | LEVEE 3 | 115 | 13.4234 | 13.4536 | 0.0302
GEN-2017-119 | 03 CENTRAL | 533328 | FT JCT 3 | 115 | 15.9369 | 15.9699 | 0.033
GEN-2017-119 | 03 CENTRAL | 533333 | KSU W 3 | 115 | 12.3911 | 12.4179 | 0.0268
GEN-2017-119 | 03 CENTRAL | 533335 | MCDOWEL3 | 115 | 19.3676 | 19.4097 | 0.0421
GEN-2017-119 | 03 CENTRAL | 533336 | GEARY 3 | 115 | 19.9801 | 20.0348 | 0.0547
GEN-2017-119 | 03 CENTRAL | 533343 | PEIL 3 | 115 | 10.9339 | 10.9537 | 0.0198
GEN-2017-119 | 03 CENTRAL | 533345 | WILDCAT3 | 115 | 10.3919 | 10.4091 | 0.0172
GEN-2017-119 | 03 CENTRAL | 533346 | KSU E 3 | 115 | 12.3905 | 12.4173 | 0.0268
GEN-2017-119 | 03 CENTRAL | 533347 | NMANHT3 | 115 | 13.3862 | 13.4184 | 0.0322
GEN-2017-119 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8993 | 3.9008 | 0.0015
GEN-2017-119 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4738 | 3.475 | 0.0012
GEN-2017-119 | 03 CENTRAL | 533362 | CHAPMAN3 | 115 | 11.828 | 11.8465 | 0.0185
GEN-2017-119 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 12.3674 | 12.3945 | 0.0271
GEN-2017-119 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.788 | 12.8182 | 0.0302
GEN-2017-119 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 10.6565 | 10.6779 | 0.0214
GEN-2017-119 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 18.1165 | 18.1803 | 0.0638
GEN-2017-119 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.3138 | 23.3667 | 0.0529
GEN-2017-119 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.7756 | 11.7933 | 0.0177
GEN-2017-119 | 03 CENTRAL | 539634 | MRWYP26 | 230 | 6.4337 | 6.5756 | 0.1419
GEN-2017-119 | 03 CENTRAL | 539637 | MRWYP16 | 230 | 7.6293 | 7.8371 | 0.2078
GEN-2017-119 | 03 CENTRAL | 539639 | ELMCREK6 | 230 | 8.6253 | 8.905 | 0.2797
GEN-2017-119 | 03 CENTRAL | 539647 | IONIA 3 | 115 | 3.0783 | 3.0837 | 0.0054
GEN-2017-119 | 03 CENTRAL | 539656 | CLIFTON3 | 115 | 4.9997 | 5.0077 | 0.008
GEN-2017-119 | 03 CENTRAL | 539657 | CONCORD3 | 115 | 7.8561 | 7.9212 | 0.0651
GEN-2017-119 | 03 CENTRAL | 539658 | CONCRD6 | 230 | 6.0834 | 6.2035 | 0.1201
GEN-2017-119 | 03 CENTRAL | 539663 | GLENELD3 | 115 | 2.9241 | 2.9296 | 0.0055
GEN-2017-119 | 03 CENTRAL | 539665 | GRNLEAF3 | 115 | 4.1837 | 4.1872 | 0.0035
GEN-2017-119 | 03 CENTRAL | 539669 | JEWELL 3 | 115 | 3.2667 | 3.2744 | 0.0077
GEN-2017-119 | 03 CENTRAL | 539805 | ELMCREEK7 | 345 | 6.143 | 6.4654 | 0.3224
GEN-2017-119 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8226 | 6.8493 | 0.0267
GEN-2017-119 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.261 | 10.3256 | 0.0646
GEN-2017-119 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.4356 | 8.577 | 0.1414
GEN-2017-119 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.7761 | 9.9682 | 0.1921
GEN-2017-119 | 03 CENTRAL | 760578 | GEN-2017-119 | 345 | 5.8666 | 6.188 | 0.3214
GEN-2017-120 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 7.0525 | 7.0716 | 0.0191
GEN-2017-120 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 6.1604 | 6.1744 | 0.014
GEN-2017-120 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 6.5254 | 6.5413 | 0.0159
GEN-2017-120 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 11.9599 | 11.9665 | 0.0066
GEN-2017-120 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.4964 | 10.6006 | 0.1042
GEN-2017-120 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.5161 | 11.6284 | 0.1123
GEN-2017-120 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.4758 | 14.5206 | 0.0448
GEN-2017-120 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0204 | 9.0493 | 0.0289
GEN-2017-120 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 8.1477 | 8.1931 | 0.0454
GEN-2017-120 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.6157 | 13.8406 | 0.2249
GEN-2017-120 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.438 | 8.4778 | 0.0398
GEN-2017-120 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 5.0337 | 5.0452 | 0.0115
GEN-2017-120 | 03 CENTRAL | 533320 | CLAYCSS3 | 115 | 2.4175 | 2.437 | 0.0195
GEN-2017-120 | 03 CENTRAL | 533323 | CLAYCTR3 | 115 | 3.0746 | 3.1059 | 0.0313
GEN-2017-120 | 03 CENTRAL | 533324 | TCRILEY 3 | 115 | 2.1228 | 2.1379 | 0.0151
GEN-2017-120 | 03 CENTRAL | 533325 | CLAYGEN3 | 115 | 2.3458 | 2.3641 | 0.0183
GEN-2017-120 | 03 CENTRAL | 533328 | FT JCT 3 | 115 | 15.6556 | 15.9699 | 0.3143
GEN-2017-120 | 03 CENTRAL | 533329 | NCFOUND3 | 115 | 12.0327 | 12.258 | 0.2253
GEN-2017-120 | 03 CENTRAL | 533335 | MCDOWEL3 | 115 | 19.2143 | 19.4097 | 0.1954
GEN-2017-120 | 03 CENTRAL | 533336 | GEARY 3 | 115 | 19.6804 | 20.0348 | 0.3544
GEN-2017-120 | 03 CENTRAL | 533342 | WJCCTY 3 | 115 | 14.0713 | 14.3762 | 0.3049
GEN-2017-120 | 03 CENTRAL | 533344 | WJCCTYW3 | 115 | 13.9767 | 14.2813 | 0.3046
GEN-2017-120 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8966 | 3.9008 | 0.0042
GEN-2017-120 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4717 | 3.475 | 0.0033
GEN-2017-120 | 03 CENTRAL | 533361 | AEC 3 | 115 | 7.8551 | 8.7575 | 0.9024
GEN-2017-120 | 03 CENTRAL | 533362 | CHAPMAN3 | 115 | 11.3954 | 11.8465 | 0.4511
GEN-2017-120 | 03 CENTRAL | 533364 | CRAWFRD3 | 115 | 9.7291 | 9.9515 | 0.2224
GEN-2017-120 | 03 CENTRAL | 533365 | EABILEN3 | 115 | 8.0819 | 8.8325 | 0.7506
GEN-2017-120 | 03 CENTRAL | 533367 | BERG 3 | 115 | 11.4291 | 11.6387 | 0.2096
GEN-2017-120 | 03 CENTRAL | 533370 | NORTHST3 | 115 | 10.1374 | 10.4526 | 0.3152
GEN-2017-120 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 11.8836 | 12.3945 | 0.5109
GEN-2017-120 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.5604 | 12.8182 | 0.2578
GEN-2017-120 | 03 CENTRAL | 533376 | SALINA 3 | 115 | 9.744 | 10.0094 | 0.2654
GEN-2017-120 | 03 CENTRAL | 533377 | SCHILNG3 | 115 | 10.6036 | 10.8231 | 0.2195
GEN-2017-120 | 03 CENTRAL | 533378 | SMOKYHLLS3 | 115 | 10.9583 | 11.1487 | 0.1904
GEN-2017-120 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 10.5068 | 10.6779 | 0.1711
GEN-2017-120 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 17.7352 | 18.1803 | 0.4451
GEN-2017-120 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.2602 | 7.308 | 0.0478
GEN-2017-120 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.7429 | 11.7933 | 0.0504
GEN-2017-120 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.4074 | 11.4575 | 0.0501
GEN-2017-120 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8295 | 6.8493 | 0.0198
GEN-2017-120 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.2775 | 10.3256 | 0.0481
GEN-2017-120 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.5205 | 8.577 | 0.0565
GEN-2017-120 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.8914 | 9.9682 | 0.0768
GEN-2017-120 | 03 CENTRAL | 760000 | GEN-2017-120 | 115 | 7.806 | 8.9954 | 1.1894
GEN-2017-120 | 03 CENTRAL | 760007 | G17-120-TAP | 115 | 7.806 | 8.9954 | 1.1894
GEN-2017-121 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 17.675 | 17.6864 | 0.0114
GEN-2017-121 | 03 CENTRAL | 514759 | NEWKIRK4 | 138 | 9.0676 | 9.1225 | 0.0549
GEN-2017-121 | 03 CENTRAL | 514804 | MIDLTNT4 | 138 | 8.1859 | 8.2578 | 0.0719
GEN-2017-121 | 03 CENTRAL | 515381 | PECKHMT4 | 138 | 8.7132 | 8.7722 | 0.059
GEN-2017-121 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.5572 | 12.5699 | 0.0127
GEN-2017-121 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.5392 | 12.5518 | 0.0126
GEN-2017-121 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.4267 | 12.4487 | 0.022
GEN-2017-121 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.4194 | 14.4353 | 0.0159
GEN-2017-121 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.6313 | 6.6347 | 0.0034
GEN-2017-121 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.447 | 11.4591 | 0.0121
GEN-2017-121 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.0054 | 11.0224 | 0.017
GEN-2017-121 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 5.9048 | 5.906 | 0.0012
GEN-2017-121 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.769 | 10.7771 | 0.0081
GEN-2017-121 | 03 CENTRAL | 520450 | NWBRAMN4 | 138 | 5.6724 | 5.6974 | 0.025
GEN-2017-121 | 03 CENTRAL | 521198 | CHILOCCO4 | 138 | 6.3518 | 6.3952 | 0.0434
GEN-2017-121 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.6005 | 7.6058 | 0.0053
GEN-2017-121 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.2236 | 5.2261 | 0.0025
GEN-2017-121 | 03 CENTRAL | 529290 | OMNUKRK4 | 138 | 8.9732 | 9.0269 | 0.0537
GEN-2017-121 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6403 | 19.6479 | 0.0076
GEN-2017-121 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6891 | 11.6973 | 0.0082
GEN-2017-121 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.9767 | 15.9817 | 0.005
GEN-2017-121 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 21.4289 | 21.4794 | 0.0505
GEN-2017-121 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2734 | 7.2777 | 0.0043
GEN-2017-121 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0696 | 6.0724 | 0.0028
GEN-2017-121 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0418 | 5.0437 | 0.0019
GEN-2017-121 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.1338 | 7.1376 | 0.0038
GEN-2017-121 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.3364 | 19.4083 | 0.0719
GEN-2017-121 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9377 | 6.9479 | 0.0102
GEN-2017-121 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8956 | 18.9731 | 0.0775
GEN-2017-121 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6148 | 5.6211 | 0.0063
GEN-2017-121 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 25.0078 | 25.0892 | 0.0814
GEN-2017-121 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.702 | 18.7116 | 0.0096
GEN-2017-121 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1648 | 14.2196 | 0.0548
GEN-2017-121 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.5078 | 10.516 | 0.0082
GEN-2017-121 | 03 CENTRAL | 532981 | CRESWLN4 | 138 | 8.3836 | 8.5284 | 0.1448
GEN-2017-121 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.0625 | 10.6084 | 0.5459
GEN-2017-121 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.2481 | 12.01 | 0.7619
GEN-2017-121 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 5.8512 | 6.019 | 0.1678
GEN-2017-121 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.4028 | 28.5075 | 0.1047
GEN-2017-121 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.3871 | 22.5244 | 0.1373
GEN-2017-121 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 17.5333 | 17.6435 | 0.1102
GEN-2017-121 | 03 CENTRAL | 533032 | BU11PON4 | 138 | 15.3452 | 15.4288 | 0.0836
GEN-2017-121 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5204 | 14.5731 | 0.0527
GEN-2017-121 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.8809 | 25.1902 | 0.3093
GEN-2017-121 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.828 | 31.9281 | 0.1001
GEN-2017-121 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.7547 | 31.8544 | 0.0997
GEN-2017-121 | 03 CENTRAL | 533042 | FARBER 4 | 138 | 16.6123 | 16.9294 | 0.3171
GEN-2017-121 | 03 CENTRAL | 533044 | GILL E 4 | 138 | 22.0635 | 22.1871 | 0.1236
GEN-2017-121 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 22.1266 | 22.251 | 0.1244
GEN-2017-121 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 22.1237 | 22.2483 | 0.1246
GEN-2017-121 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.121 | 22.2454 | 0.1244
GEN-2017-121 | 03 CENTRAL | 533051 | INTERST4 | 138 | 15.9754 | 16.0265 | 0.0511
GEN-2017-121 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.0801 | 21.1331 | 0.053
GEN-2017-121 | 03 CENTRAL | 533058 | 47TH ST4 | 138 | 17.4606 | 17.5974 | 0.1368
GEN-2017-121 | 03 CENTRAL | 533059 | ELPASOE4 | 138 | 24.8372 | 25.1472 | 0.31
GEN-2017-121 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.2731 | 31.4772 | 0.2041
GEN-2017-121 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.206 | 11.8943 | 0.6883
GEN-2017-121 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.5719 | 19.6083 | 0.0364
GEN-2017-121 | 03 CENTRAL | 533066 | 64TH 4 | 138 | 14.7382 | 14.8212 | 0.083
GEN-2017-121 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.7341 | 19.8579 | 0.1238
GEN-2017-121 | 03 CENTRAL | 533070 | SLATECRK4 | 138 | 5.7687 | 5.8321 | 0.0634
GEN-2017-121 | 03 CENTRAL | 533071 | WACO S 4 | 138 | 19.3433 | 19.4342 | 0.0909
GEN-2017-121 | 03 CENTRAL | 533072 | WACO 4 | 138 | 19.2932 | 19.3835 | 0.0903
GEN-2017-121 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 25.0809 | 25.2326 | 0.1517
GEN-2017-121 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.3575 | 23.3667 | 0.0092
GEN-2017-121 | 03 CENTRAL | 533540 | ARKCTYW2 | 69 | 6.838 | 6.8855 | 0.0475
GEN-2017-121 | 03 CENTRAL | 533541 | AKRON 2 | 69 | 7.11 | 7.1911 | 0.0811
GEN-2017-121 | 03 CENTRAL | 533543 | CRESWLN2 | 69 | 12.6612 | 12.8199 | 0.1587
GEN-2017-121 | 03 CENTRAL | 533545 | FLORAL 2 | 69 | 2.5367 | 2.5466 | 0.0099
GEN-2017-121 | 03 CENTRAL | 533546 | FLORALJ2 | 69 | 2.8749 | 2.8878 | 0.0129
GEN-2017-121 | 03 CENTRAL | 533547 | OAK 2 | 69 | 8.4758 | 8.5509 | 0.0751
GEN-2017-121 | 03 CENTRAL | 533548 | PARIS 2 | 69 | 7.2022 | 7.2546 | 0.0524
GEN-2017-121 | 03 CENTRAL | 533549 | RAINBOW2 | 69 | 6.4646 | 6.5098 | 0.0452
GEN-2017-121 | 03 CENTRAL | 533550 | RICHLAN2 | 69 | 6.1694 | 6.2007 | 0.0313
GEN-2017-121 | 03 CENTRAL | 533551 | SC1KING2 | 69 | 3.4624 | 3.4813 | 0.0189
GEN-2017-121 | 03 CENTRAL | 533553 | SC4ROME2 | 69 | 5.6658 | 5.6888 | 0.023
GEN-2017-121 | 03 CENTRAL | 533555 | SC7CRES2 | 69 | 12.6429 | 12.8011 | 0.1582
GEN-2017-121 | 03 CENTRAL | 533556 | STROTHR2 | 69 | 6.4665 | 6.5123 | 0.0458
GEN-2017-121 | 03 CENTRAL | 533557 | TIMBER 2 | 69 | 2.5497 | 2.5598 | 0.0101
GEN-2017-121 | 03 CENTRAL | 533558 | TIMBJCT2 | 69 | 8.6286 | 8.7478 | 0.1192
GEN-2017-121 | 03 CENTRAL | 533559 | UDALL 2 | 69 | 7.4193 | 7.497 | 0.0777
GEN-2017-121 | 03 CENTRAL | 533560 | WELLING2 | 69 | 4.7015 | 4.7125 | 0.011
GEN-2017-121 | 03 CENTRAL | 533561 | WINFLD 2 | 69 | 6.8994 | 6.9524 | 0.053
GEN-2017-121 | 03 CENTRAL | 533562 | PRAIRIE2 | 69 | 6.8286 | 6.877 | 0.0484
GEN-2017-121 | 03 CENTRAL | 533563 | PRAIRIJ2 | 69 | 7.4516 | 7.5093 | 0.0577
GEN-2017-121 | 03 CENTRAL | 533573 | CRESWLS2 | 69 | 12.6582 | 12.8169 | 0.1587
GEN-2017-121 | 03 CENTRAL | 533793 | ELPASO 2 | 69 | 12.1237 | 12.1519 | 0.0282
GEN-2017-121 | 03 CENTRAL | 533795 | GILL E 2 | 69 | 29.9115 | 30.0288 | 0.1173
GEN-2017-121 | 03 CENTRAL | 533796 | GILL W 2 | 69 | 29.9189 | 30.0363 | 0.1174
GEN-2017-121 | 03 CENTRAL | 533798 | GILLJCT2 | 69 | 21.1259 | 21.1803 | 0.0544
GEN-2017-121 | 03 CENTRAL | 533802 | HAYSVJS2 | 69 | 8.296 | 8.3095 | 0.0135
GEN-2017-121 | 03 CENTRAL | 533803 | HAYSV 2 | 69 | 8.9511 | 8.9611 | 0.01
GEN-2017-121 | 03 CENTRAL | 533804 | HAYSVJN2 | 69 | 14.0721 | 14.0975 | 0.0254
GEN-2017-121 | 03 CENTRAL | 533813 | MACARTH2 | 69 | 21.7853 | 21.844 | 0.0587
GEN-2017-121 | 03 CENTRAL | 533821 | MULVANE2 | 69 | 5.5688 | 5.5748 | 0.006
GEN-2017-121 | 03 CENTRAL | 533824 | OAKLAWN2 | 69 | 15.8374 | 15.8725 | 0.0351
GEN-2017-121 | 03 CENTRAL | 533836 | ROSEHIL2 | 69 | 5.6517 | 5.6686 | 0.0169
GEN-2017-121 | 03 CENTRAL | 533837 | RH JCT 2 | 69 | 6.911 | 6.9363 | 0.0253
GEN-2017-121 | 03 CENTRAL | 533850 | VULCAN 2 | 69 | 19.3442 | 19.3932 | 0.049
GEN-2017-121 | 03 CENTRAL | 533851 | VULCTP 2 | 69 | 22.7062 | 22.7733 | 0.0671
GEN-2017-121 | 03 CENTRAL | 533990 | EAST SUB 2 | 69 | 4.9633 | 4.9896 | 0.0263
GEN-2017-121 | 03 CENTRAL | 533991 | WEST SUB 2 | 69 | 5.3006 | 5.3312 | 0.0306
GEN-2017-121 | 03 CENTRAL | 533992 | VIKING SUB 2 | 69 | 4.8744 | 4.9 | 0.0256
GEN-2017-121 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1334 | 4.1352 | 0.0018
GEN-2017-121 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.2464 | 5.25 | 0.0036
GEN-2017-121 | 03 CENTRAL | 539002 | BLF-CRK4 | 138 | 4.9096 | 4.9134 | 0.0038
GEN-2017-121 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8253 | 5.8317 | 0.0064
GEN-2017-121 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.1987 | 12.2326 | 0.0339
GEN-2017-121 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.705 | 11.7337 | 0.0287
GEN-2017-121 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.8092 | 10.8122 | 0.003
GEN-2017-121 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.1306 | 16.1376 | 0.007
GEN-2017-121 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5372 | 7.5432 | 0.006
GEN-2017-121 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.339 | 10.3604 | 0.0214
GEN-2017-121 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.835 | 10.8618 | 0.0268
GEN-2017-121 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.8383 | 16.851 | 0.0127
GEN-2017-121 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.8019 | 10.8102 | 0.0083
GEN-2017-121 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.1639 | 5.1692 | 0.0053
GEN-2017-121 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2898 | 7.2934 | 0.0036
GEN-2017-121 | 03 CENTRAL | 587480 | GEN-2016-071 | 138 | 6.6718 | 6.7195 | 0.0477
GEN-2017-121 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8476 | 6.8493 | 0.0017
GEN-2017-121 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.3213 | 10.3256 | 0.0043
GEN-2017-121 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 5.5319 | 5.533 | 0.0011
GEN-2017-121 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.2709 | 8.2864 | 0.0155
GEN-2017-121 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.8383 | 16.851 | 0.0127
GEN-2017-121 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 28.9979 | 29.0807 | 0.0828
GEN-2017-121 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 21.3128 | 21.3626 | 0.0498
GEN-2017-121 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.828 | 31.9281 | 0.1001
GEN-2017-121 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.0098 | 9.0211 | 0.0113
GEN-2017-121 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 8.3424 | 9.1228 | 0.7804
GEN-2017-121 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 10.9355 | 10.9398 | 0.0043
GEN-2017-121 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.7797 | 7.7818 | 0.0021
GEN-2017-131 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0434 | 16.0466 | 0.0032
GEN-2017-131 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.1797 | 12.1825 | 0.0028
GEN-2017-131 | 03 CENTRAL | 510422 | COFFEYT4 | 138 | 10.3709 | 10.3839 | 0.013
GEN-2017-131 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 12.0421 | 12.0464 | 0.0043
GEN-2017-131 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.1474 | 11.1511 | 0.0037
GEN-2017-131 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.2974 | 18.3104 | 0.013
GEN-2017-131 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 5.1325 | 5.1329 | 0.0004
GEN-2017-131 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.7017 | 8.7031 | 0.0014
GEN-2017-131 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.7861 | 23.8161 | 0.03
GEN-2017-131 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.5044 | 28.5075 | 0.0031
GEN-2017-131 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2507 | 11.2543 | 0.0036
GEN-2017-131 | 03 CENTRAL | 532989 | BUTLERS4 | 138 | 11.2435 | 11.247 | 0.0035
GEN-2017-131 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.3049 | 11.3076 | 0.0027
GEN-2017-131 | 03 CENTRAL | 532996 | TIOGA 4 | 138 | 5.6682 | 5.695 | 0.0268
GEN-2017-131 | 03 CENTRAL | 532997 | OTTRCRK4 | 138 | 5.7335 | 5.7424 | 0.0089
GEN-2017-131 | 03 CENTRAL | 533001 | ALTOONA4 | 138 | 9.2967 | 9.4274 | 0.1307
GEN-2017-131 | 03 CENTRAL | 533002 | DEARING4 | 138 | 9.6984 | 9.7152 | 0.0168
GEN-2017-131 | 03 CENTRAL | 533003 | LIBERTY4 | 138 | 7.6471 | 7.6567 | 0.0096
GEN-2017-131 | 03 CENTRAL | 533004 | MONTGOM4 | 138 | 7.2849 | 7.3077 | 0.0228
GEN-2017-131 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 13.121 | 13.1716 | 0.0506
GEN-2017-131 | 03 CENTRAL | 533006 | TAYLOR 4 | 138 | 7.1049 | 7.1295 | 0.0246
GEN-2017-131 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 7.2805 | 7.2877 | 0.0072
GEN-2017-131 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.3867 | 25.4339 | 0.0472
GEN-2017-131 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.4297 | 25.4772 | 0.0475
GEN-2017-131 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.3106 | 25.358 | 0.0474
GEN-2017-131 | 03 CENTRAL | 533302 | EEUREKA3 | 115 | 4.3273 | 4.3299 | 0.0026
GEN-2017-131 | 03 CENTRAL | 533308 | VAUGHN 3 | 115 | 4.4968 | 4.4976 | 0.0008
GEN-2017-131 | 03 CENTRAL | 533315 | OTTRCRK3 | 115 | 5.203 | 5.208 | 0.005
GEN-2017-131 | 03 CENTRAL | 533583 | BUTLERN2 | 69 | 14.2372 | 14.2395 | 0.0023
GEN-2017-131 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.6152 | 14.6173 | 0.0021
GEN-2017-131 | 03 CENTRAL | 533602 | SKELLY 2 | 69 | 12.8805 | 12.8824 | 0.0019
GEN-2017-131 | 03 CENTRAL | 533609 | BUTLERS2 | 69 | 14.2298 | 14.2321 | 0.0023
GEN-2017-131 | 03 CENTRAL | 533610 | MIDIANE2 | 69 | 14.6105 | 14.6125 | 0.002
GEN-2017-131 | 03 CENTRAL | 533633 | COALCRK2 | 69 | 6.7682 | 6.7717 | 0.0035
GEN-2017-131 | 03 CENTRAL | 533634 | ENA 2 | 69 | 6.6786 | 6.6817 | 0.0031
GEN-2017-131 | 03 CENTRAL | 533643 | ORCHARD2 | 69 | 4.6548 | 4.6564 | 0.0016
GEN-2017-131 | 03 CENTRAL | 533646 | TIOGA 2 | 69 | 12.364 | 12.3829 | 0.0189
GEN-2017-131 | 03 CENTRAL | 533648 | UN6URBA2 | 69 | 3.7613 | 3.7627 | 0.0014
GEN-2017-131 | 03 CENTRAL | 533649 | UN7ROSE2 | 69 | 5.9351 | 5.9387 | 0.0036
GEN-2017-131 | 03 CENTRAL | 533657 | ASHGRV12 | 69 | 10.6239 | 10.6331 | 0.0092
GEN-2017-131 | 03 CENTRAL | 533658 | ASHGRV22 | 69 | 11.0415 | 11.0531 | 0.0116
GEN-2017-131 | 03 CENTRAL | 533659 | ASHGRJ12 | 69 | 11.3879 | 11.3984 | 0.0105
GEN-2017-131 | 03 CENTRAL | 533660 | ASHGRJ22 | 69 | 11.8681 | 11.8814 | 0.0133
GEN-2017-131 | 03 CENTRAL | 533661 | CGENTAP2 | 69 | 11.699 | 11.7102 | 0.0112
GEN-2017-131 | 03 CENTRAL | 533662 | CGENSUB2 | 69 | 12.471 | 12.4842 | 0.0132
GEN-2017-131 | 03 CENTRAL | 533663 | CHANP1 2 | 69 | 11.325 | 11.3345 | 0.0095
GEN-2017-131 | 03 CENTRAL | 533664 | CHANP2 2 | 69 | 11.3232 | 11.3328 | 0.0096
GEN-2017-131 | 03 CENTRAL | 533665 | CHANP3 2 | 69 | 11.5926 | 11.6021 | 0.0095
GEN-2017-131 | 03 CENTRAL | 533666 | CHANTAP2 | 69 | 11.4 | 11.4119 | 0.0119
GEN-2017-131 | 03 CENTRAL | 533671 | ALTAMNT2 | 69 | 2.9339 | 2.9341 | 0.0002
GEN-2017-131 | 03 CENTRAL | 533672 | ALTAMNS2 | 69 | 4.206 | 4.2065 | 0.0005
GEN-2017-131 | 03 CENTRAL | 533673 | ALTOO E2 | 69 | 4.3662 | 4.3798 | 0.0136
GEN-2017-131 | 03 CENTRAL | 533674 | ALTOO W2 | 69 | 3.1712 | 3.1783 | 0.0071
GEN-2017-131 | 03 CENTRAL | 533675 | ARGO 2 | 69 | 3.0949 | 3.102 | 0.0071
GEN-2017-131 | 03 CENTRAL | 533679 | CHERRYV2 | 69 | 4.1445 | 4.1466 | 0.0021
GEN-2017-131 | 03 CENTRAL | 533688 | DEARING2 | 69 | 8.3009 | 8.3078 | 0.0069
GEN-2017-131 | 03 CENTRAL | 533692 | YELLOWJ2 | 69 | 1.4656 | 1.4673 | 0.0017
GEN-2017-131 | 03 CENTRAL | 533694 | INDEPEN2 | 69 | 6.9302 | 6.9373 | 0.0071
GEN-2017-131 | 03 CENTRAL | 533695 | LABETTE2 | 69 | 4.2188 | 4.2193 | 0.0005
GEN-2017-131 | 03 CENTRAL | 533696 | LABETTS2 | 69 | 6.3954 | 6.3966 | 0.0012
GEN-2017-131 | 03 CENTRAL | 533698 | MONTGOM2 | 69 | 8.0404 | 8.0511 | 0.0107
GEN-2017-131 | 03 CENTRAL | 533699 | NEODESH2 | 69 | 2.78 | 2.7857 | 0.0057
GEN-2017-131 | 03 CENTRAL | 533700 | NEODJCT2 | 69 | 3.7586 | 3.7687 | 0.0101
GEN-2017-131 | 03 CENTRAL | 533701 | NEW ALB2 | 69 | 1.5552 | 1.5571 | 0.0019
GEN-2017-131 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.3295 | 6.3307 | 0.0012
GEN-2017-131 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.7666 | 8.769 | 0.0024
GEN-2017-131 | 03 CENTRAL | 533705 | STUDBKR2 | 69 | 1.8852 | 1.8879 | 0.0027
GEN-2017-131 | 03 CENTRAL | 533706 | RA5HIPR2 | 69 | 4.364 | 4.3776 | 0.0136
GEN-2017-131 | 03 CENTRAL | 533707 | RA6BROO2 | 69 | 2.6691 | 2.6742 | 0.0051
GEN-2017-131 | 03 CENTRAL | 533712 | WILLMS 2 | 69 | 7.1649 | 7.1734 | 0.0085
GEN-2017-131 | 03 CENTRAL | 533713 | WILLJCT2 | 69 | 7.5805 | 7.5899 | 0.0094
GEN-2017-131 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.5729 | 7.5742 | 0.0013
GEN-2017-131 | 03 CENTRAL | 533760 | ERIE 2 | 69 | 2.3345 | 2.335 | 0.0005
GEN-2017-131 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 24.0019 | 24.0212 | 0.0193
GEN-2017-131 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0269 | 24.0463 | 0.0194
GEN-2017-131 | 03 CENTRAL | 547469 | RIV4525 | 161 | 25.2888 | 25.2916 | 0.0028
GEN-2017-131 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.9292 | 23.9316 | 0.0024
GEN-2017-131 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 23.4097 | 23.4121 | 0.0024
GEN-2017-131 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.8314 | 24.834 | 0.0026
GEN-2017-131 | 03 CENTRAL | 588660 | GEN-2017-022 | 138 | 8.8945 | 9.0292 | 0.1347
GEN-2017-131 | 03 CENTRAL | 588664 | G17-022-TAP | 138 | 9.26 | 9.3944 | 0.1344
GEN-2017-131 | 03 CENTRAL | 760914 | GEN-2017-209 | 345 | 19.2079 | 19.209 | 0.0011
GEN-2017-131 | 03 CENTRAL | 760921 | G17-209-TAP | 345 | 19.7101 | 19.7113 | 0.0012
GEN-2017-183 | 03 CENTRAL | 300039 | 7FAIRPT | 345 | 12.8649 | 12.9083 | 0.0434
GEN-2017-183 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 18.2119 | 18.213 | 0.0011
GEN-2017-183 | 03 CENTRAL | 300073 | 5GENTRY | 161 | 10.2402 | 10.2458 | 0.0056
GEN-2017-183 | 03 CENTRAL | 300076 | 5FAIRPTB2 | 161 | 16.8476 | 16.8683 | 0.0207
GEN-2017-183 | 03 CENTRAL | 300249 | 2FAIRPT | 69 | 17.2788 | 17.2867 | 0.0079
GEN-2017-183 | 03 CENTRAL | 301347 | 5WINSLOW | 161 | 8.9292 | 8.9346 | 0.0054
GEN-2017-183 | 03 CENTRAL | 301559 | 5FAIRPTXF3 | 161 | 16.8658 | 16.8866 | 0.0208
GEN-2017-183 | 03 CENTRAL | 301564 | 5FAIRPTB1 | 161 | 16.8035 | 16.8241 | 0.0206
GEN-2017-183 | 03 CENTRAL | 345088 | 7MCCREDIE | 345 | 14.2488 | 14.2495 | 0.0007
GEN-2017-183 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 16.4534 | 16.4553 | 0.0019
GEN-2017-183 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.4848 | 22.486 | 0.0012
GEN-2017-183 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 16.5297 | 16.5377 | 0.008
GEN-2017-183 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8375 | 24.8418 | 0.0043
GEN-2017-183 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 28.3441 | 28.4251 | 0.081
GEN-2017-183 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 22.6158 | 22.6421 | 0.0263
GEN-2017-183 | 03 CENTRAL | 533211 | ARNOLD 3 | 115 | 8.4268 | 8.4283 | 0.0015
GEN-2017-183 | 03 CENTRAL | 533244 | JARBALO3 | 115 | 27.4156 | 27.431 | 0.0154
GEN-2017-183 | 03 CENTRAL | 533259 | NW LEAV3 | 115 | 17.6653 | 17.6733 | 0.008
GEN-2017-183 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 37.8135 | 37.8519 | 0.0384
GEN-2017-183 | 03 CENTRAL | 533272 | THORNTN3 | 115 | 16.583 | 16.59 | 0.007
GEN-2017-183 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 27.9745 | 27.9864 | 0.0119
GEN-2017-183 | 03 CENTRAL | 541137 | ALABAMA_CAP5 | 161 | 10.8076 | 10.8273 | 0.0197
GEN-2017-183 | 03 CENTRAL | 541144 | NASHUA_CAP5 | 161 | 24.6337 | 24.7059 | 0.0722
GEN-2017-183 | 03 CENTRAL | 541145 | RNRIDGE_CAP5 | 161 | 20.345 | 20.3778 | 0.0328
GEN-2017-183 | 03 CENTRAL | 541147 | ST JOE_CAP5 | 161 | 18.6768 | 18.7432 | 0.0664
GEN-2017-183 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 11.7091 | 11.7132 | 0.0041
GEN-2017-183 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.9451 | 20.9599 | 0.0148
GEN-2017-183 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 20.5681 | 20.7783 | 0.2102
GEN-2017-183 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.1109 | 19.1273 | 0.0164
GEN-2017-183 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.954 | 22.0014 | 0.0474
GEN-2017-183 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.5109 | 27.5409 | 0.03
GEN-2017-183 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 28.7286 | 28.8269 | 0.0983
GEN-2017-183 | 03 CENTRAL | 541204 | SMTHVL 5 | 161 | 21.4603 | 21.513 | 0.0527
GEN-2017-183 | 03 CENTRAL | 541214 | TWA 5 | 161 | 15.4235 | 15.4435 | 0.02
GEN-2017-183 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 13.7467 | 13.762 | 0.0153
GEN-2017-183 | 03 CENTRAL | 541221 | PLTCTY 5 | 161 | 15.6958 | 15.7201 | 0.0243
GEN-2017-183 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 34.9385 | 34.9521 | 0.0136
GEN-2017-183 | 03 CENTRAL | 541230 | RNRIDGE5 | 161 | 23.0607 | 23.1029 | 0.0422
GEN-2017-183 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 15.2307 | 15.2524 | 0.0217
GEN-2017-183 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 29.0797 | 29.1127 | 0.033
GEN-2017-183 | 03 CENTRAL | 541251 | MARYVLE5 | 161 | 11.5886 | 11.5916 | 0.003
GEN-2017-183 | 03 CENTRAL | 541253 | ST JOE 5 | 161 | 20.9384 | 21.0218 | 0.0834
GEN-2017-183 | 03 CENTRAL | 541254 | EAST 5 | 161 | 16.3302 | 16.3794 | 0.0492
GEN-2017-183 | 03 CENTRAL | 541255 | LAKE RD5 | 161 | 13.1964 | 13.2258 | 0.0294
GEN-2017-183 | 03 CENTRAL | 541256 | IND PRK5 | 161 | 15.8128 | 15.8574 | 0.0446
GEN-2017-183 | 03 CENTRAL | 541257 | COOK 5 | 161 | 14.6189 | 14.6577 | 0.0388
GEN-2017-183 | 03 CENTRAL | 541258 | WOODBIN5 | 161 | 17.6024 | 17.6606 | 0.0582
GEN-2017-183 | 03 CENTRAL | 541260 | RNRDGE 2 | 69 | 5.42 | 5.4207 | 0.0007
GEN-2017-183 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.8773 | 5.878 | 0.0007
GEN-2017-183 | 03 CENTRAL | 541318 | NCONGRS5 | 161 | 18.79 | 18.8187 | 0.0287
GEN-2017-183 | 03 CENTRAL | 541349 | POPE | 161 | 12.9703 | 12.9895 | 0.0192
GEN-2017-183 | 03 CENTRAL | 541350 | IATAN5 | 161 | 15.5111 | 15.5313 | 0.0202
GEN-2017-183 | 03 CENTRAL | 541351 | WESTON 5 | 161 | 13.3923 | 13.4078 | 0.0155
GEN-2017-183 | 03 CENTRAL | 541354 | ALABAMA5 | 161 | 11.5289 | 11.5513 | 0.0224
GEN-2017-183 | 03 CENTRAL | 541355 | EDMOND5 | 161 | 13.2104 | 13.2409 | 0.0305
GEN-2017-183 | 03 CENTRAL | 541358 | AMOIL 2 | 69 | 4.0377 | 4.0381 | 0.0004
GEN-2017-183 | 03 CENTRAL | 541359 | MRVL#2 | 69 | 3.7282 | 3.7283 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541362 | BURLNGTNJCT2 | 69 | 1.7275 | 1.7275 | 0
GEN-2017-183 | 03 CENTRAL | 541363 | TARKIO_2 | 69 | 0.9663 | 0.9663 | 0
GEN-2017-183 | 03 CENTRAL | 541364 | FAIRFAX2 | 69 | 0.8226 | 0.8226 | 0
GEN-2017-183 | 03 CENTRAL | 541365 | NTHWARD2 | 69 | 0.6958 | 0.6958 | 0
GEN-2017-183 | 03 CENTRAL | 541366 | MNDCITY2 | 69 | 1.4143 | 1.4144 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541367 | BRWNCRV2 | 69 | 1.7386 | 1.7387 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541368 | MIDWY1 2 | 69 | 4.0509 | 4.0513 | 0.0004
GEN-2017-183 | 03 CENTRAL | 541369 | MIDWAY_5 | 161 | 6.1762 | 6.1784 | 0.0022
GEN-2017-183 | 03 CENTRAL | 541376 | AMOILTP2 | 69 | 3.5989 | 3.5992 | 0.0003
GEN-2017-183 | 03 CENTRAL | 541377 | KELLOG 2 | 69 | 2.5137 | 2.5138 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541378 | MRVL#1 | 69 | 3.6919 | 3.692 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541379 | PICKRG_2 | 69 | 2.6105 | 2.6106 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541380 | NODAWAY2 | 69 | 3.0736 | 3.0737 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541381 | FILMORE2 | 69 | 3.2609 | 3.261 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541389 | MDWYTP 2 | 69 | 3.9153 | 3.9157 | 0.0004
GEN-2017-183 | 03 CENTRAL | 541390 | MIDWY2 2 | 69 | 4.056 | 4.0564 | 0.0004
GEN-2017-183 | 03 CENTRAL | 541391 | SAVANAH2 | 69 | 1.9033 | 1.9036 | 0.0003
GEN-2017-183 | 03 CENTRAL | 541392 | EDMOND2 | 69 | 3.6536 | 3.6546 | 0.001
GEN-2017-183 | 03 CENTRAL | 541394 | AVENUECTY 5 | 161 | 6.3985 | 6.4031 | 0.0046
GEN-2017-183 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 19.0326 | 19.1752 | 0.1426
GEN-2017-183 | 03 CENTRAL | 541401 | EASTOWN5 | 161 | 17.9997 | 18.0582 | 0.0585
GEN-2017-183 | 03 CENTRAL | 541408 | FILLMORE_TP2 | 69 | 3.5696 | 3.5698 | 0.0002
GEN-2017-183 | 03 CENTRAL | 541409 | PICKRG_TP_2 | 69 | 3.5696 | 3.5698 | 0.0002
GEN-2017-183 | 03 CENTRAL | 541411 | MC REAC1 | 345 | 10.9829 | 10.9865 | 0.0036
GEN-2017-183 | 03 CENTRAL | 541412 | MC REAC2 | 345 | 10.9829 | 10.9865 | 0.0036
GEN-2017-183 | 03 CENTRAL | 541413 | MC REAC3 | 345 | 10.9829 | 10.9865 | 0.0036
GEN-2017-183 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.5217 | 19.5592 | 0.0375
GEN-2017-183 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 9.3269 | 9.3311 | 0.0042
GEN-2017-183 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 8.1724 | 8.1756 | 0.0032
GEN-2017-183 | 03 CENTRAL | 541510 | HOLT 7 | 345 | 18.2528 | 18.2602 | 0.0074
GEN-2017-183 | 03 CENTRAL | 541511 | ROCKCK7 | 345 | 11.5493 | 11.5519 | 0.0026
GEN-2017-183 | 03 CENTRAL | 541517 | HOLT_REACT7 | 345 | 18.0651 | 18.0725 | 0.0074
GEN-2017-183 | 03 CENTRAL | 541537 | MULLINCRK1_1 | 69 | 2.1632 | 2.1632 | 0
GEN-2017-183 | 03 CENTRAL | 541538 | MULLINCRK1_2 | 69 | 2.5547 | 2.5548 | 0.0001
GEN-2017-183 | 03 CENTRAL | 541543 | OUTLAW | 345 | 8.8279 | 8.8293 | 0.0014
GEN-2017-183 | 03 CENTRAL | 542944 | BARRY_CAP 5 | 161 | 16.8421 | 16.862 | 0.0199
GEN-2017-183 | 03 CENTRAL | 542946 | GLADSTN_CAP5 | 161 | 16.8964 | 16.9154 | 0.019
GEN-2017-183 | 03 CENTRAL | 542948 | NEASTS_CAP5 | 161 | 37.4352 | 37.4845 | 0.0493
GEN-2017-183 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.6078 | 23.7308 | 0.123
GEN-2017-183 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 59.284 | 59.4306 | 0.1466
GEN-2017-183 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 53.5556 | 53.6732 | 0.1176
GEN-2017-183 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.436 | 24.4621 | 0.0261
GEN-2017-183 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 22.9112 | 23.2402 | 0.329
GEN-2017-183 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 31.3934 | 31.5568 | 0.1634
GEN-2017-183 | 03 CENTRAL | 542985 | NEASTS5 | 161 | 47.7872 | 47.8676 | 0.0804
GEN-2017-183 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 35.7572 | 35.8009 | 0.0437
GEN-2017-183 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 39.8025 | 39.8688 | 0.0663
GEN-2017-183 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 37.2674 | 37.3202 | 0.0528
GEN-2017-183 | 03 CENTRAL | 543015 | AVONDAL5 | 161 | 30.4695 | 30.513 | 0.0435
GEN-2017-183 | 03 CENTRAL | 543016 | GLADSTN5 | 161 | 18.7281 | 18.7514 | 0.0233
GEN-2017-183 | 03 CENTRAL | 543017 | WETHRBY5 | 161 | 16.9613 | 16.9783 | 0.017
GEN-2017-183 | 03 CENTRAL | 543019 | BARRY 5 | 161 | 18.6614 | 18.6859 | 0.0245
GEN-2017-183 | 03 CENTRAL | 543020 | BRMGHAM5 | 161 | 27.2097 | 27.2398 | 0.0301
GEN-2017-183 | 03 CENTRAL | 543022 | CLAYCM15 | 161 | 11.446 | 11.457 | 0.011
GEN-2017-183 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.9794 | 13.9873 | 0.0079
GEN-2017-183 | 03 CENTRAL | 543025 | LINECRK5 | 161 | 17.3558 | 17.3738 | 0.018
GEN-2017-183 | 03 CENTRAL | 543026 | TIFFANY5 | 161 | 20.1217 | 20.1513 | 0.0296
GEN-2017-183 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 34.0509 | 34.1019 | 0.051
GEN-2017-183 | 03 CENTRAL | 543028 | NASHUA-5 | 161 | 28.8506 | 28.9499 | 0.0993
GEN-2017-183 | 03 CENTRAL | 543029 | SHOLCRK5 | 161 | 17.7746 | 17.8012 | 0.0266
GEN-2017-183 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 58.4404 | 58.5827 | 0.1423
GEN-2017-183 | 03 CENTRAL | 543130 | HAWTHS_XF5 | 161 | 58.3787 | 58.5208 | 0.1421
GEN-2017-183 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 59.9683 | 60.12 | 0.1517
GEN-2017-183 | 03 CENTRAL | 543666 | NEASTN5 | 161 | 48.1822 | 48.2645 | 0.0823
GEN-2017-183 | 03 CENTRAL | 548814 | SUB M-161 | 161 | 21.1182 | 21.135 | 0.0168
GEN-2017-183 | 03 CENTRAL | 548820 | SUB N-161 | 161 | 17.147 | 17.1589 | 0.0119
GEN-2017-183 | 03 CENTRAL | 560746 | G13-002-TAP | 115 | 42.712 | 42.7141 | 0.0021
GEN-2017-183 | 03 CENTRAL | 583700 | GEN-2013-019 | 115 | 18.464 | 18.4644 | 0.0004
GEN-2017-183 | 03 CENTRAL | 585241 | GEN-2015-088 | 345 | 11.2758 | 11.2763 | 0.0005
GEN-2017-183 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 4.4327 | 4.4337 | 0.001
GEN-2017-183 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 13.3693 | 13.3841 | 0.0148
GEN-2017-183 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 8.2294 | 8.234 | 0.0046
GEN-2017-183 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 4.1235 | 4.1243 | 0.0008
GEN-2017-183 | 03 CENTRAL | 635000 | CBLUFFS3 | 345 | 31.8532 | 31.8547 | 0.0015
GEN-2017-183 | 03 CENTRAL | 635017 | ATCHSN 3 | 345 | 22.8036 | 22.8172 | 0.0136
GEN-2017-183 | 03 CENTRAL | 635018 | WESTBORO 3 | 345 | 21.1317 | 21.1428 | 0.0111
GEN-2017-183 | 03 CENTRAL | 635570 | ORIENT 3 | 345 | 18.7653 | 18.7662 | 0.0009
GEN-2017-183 | 03 CENTRAL | 637084 | J476 SHENHLL | 345 | 20.9926 | 21.0035 | 0.0109
GEN-2017-183 | 03 CENTRAL | 640139 | COOPER 3 | 345 | 29.6885 | 29.7225 | 0.034
GEN-2017-183 | 03 CENTRAL | 640140 | COOPER 5 | 161 | 18.4679 | 18.473 | 0.0051
GEN-2017-183 | 03 CENTRAL | 640141 | COOPER_ESST8 | 69 | 4.6918 | 4.692 | 0.0002
GEN-2017-183 | 03 CENTRAL | 640143 | COOPER_602 8 | 69 | 2.0097 | 2.0097 | 0
GEN-2017-183 | 03 CENTRAL | 640171 | FIRTH 7 | 115 | 6.999 | 6.999 | 0
GEN-2017-183 | 03 CENTRAL | 640234 | HUMBOLT5 | 161 | 7.9864 | 7.9869 | 0.0005
GEN-2017-183 | 03 CENTRAL | 640271 | MCCOOL 3 | 345 | 11.0498 | 11.05 | 0.0002
GEN-2017-183 | 03 CENTRAL | 640277 | MOORE 3 | 345 | 22.8789 | 22.8814 | 0.0025
GEN-2017-183 | 03 CENTRAL | 640278 | SHELDON7 | 115 | 44.152 | 44.154 | 0.002
GEN-2017-183 | 03 CENTRAL | 640446 | COOPER 8 | 69 | 4.7899 | 4.79 | 0.0001
GEN-2017-183 | 03 CENTRAL | 640525 | TOBIAS 3 | 345 | 11.2758 | 11.2763 | 0.0005
GEN-2017-183 | 03 CENTRAL | 640590 | MONOLITH 3 | 345 | 22.4249 | 22.4274 | 0.0025
GEN-2017-183 | 03 CENTRAL | 640591 | MONOLITH 7 | 115 | 42.712 | 42.7141 | 0.0021
GEN-2017-183 | 03 CENTRAL | 645454 | S3454 3 | 345 | 28.6548 | 28.6568 | 0.002
GEN-2017-183 | 03 CENTRAL | 645455 | S3455 3 | 345 | 31.7606 | 31.7629 | 0.0023
GEN-2017-183 | 03 CENTRAL | 645456 | S3456 3 | 345 | 34.3039 | 34.3064 | 0.0025
GEN-2017-183 | 03 CENTRAL | 645458 | S3458 3 | 345 | 30.6938 | 30.7028 | 0.009
GEN-2017-183 | 03 CENTRAL | 645459 | S3459 3 | 345 | 24.9657 | 24.9669 | 0.0012
GEN-2017-183 | 03 CENTRAL | 645740 | S3740 3 | 345 | 22.801 | 22.8026 | 0.0016
GEN-2017-183 | 03 CENTRAL | 646206 | S1206 5 | 161 | 44.6646 | 44.6662 | 0.0016
GEN-2017-183 | 03 CENTRAL | 646263 | S1263 5 | 161 | 8.1072 | 8.1077 | 0.0005
GEN-2017-183 | 03 CENTRAL | 646280 | S1280 5 | 161 | 10.3212 | 10.3221 | 0.0009
GEN-2017-183 | 03 CENTRAL | 650114 | NW68HOLDRG3 | 345 | 17.3276 | 17.3287 | 0.0011
GEN-2017-183 | 03 CENTRAL | 650185 | WAGENER 3 | 345 | 20.8797 | 20.8814 | 0.0017
GEN-2017-183 | 03 CENTRAL | 650189 | 103&ROKEBY3 | 345 | 20.7299 | 20.7319 | 0.002
GEN-2017-183 | 03 CENTRAL | 760746 | GEN-2017-115 | 345 | 12.5552 | 12.5586 | 0.0034
GEN-2017-183 | 03 CENTRAL | 761208 | GEN-2017-210 | 345 | 9.6779 | 9.6781 | 0.0002
GEN-2017-183 | 03 CENTRAL | 761292 | GEN-2017-181 | 345 | 6.6274 | 6.6276 | 0.0002
GEN-2017-183 | 03 CENTRAL | 761313 | GEN-2017-182 | 345 | 5.5797 | 5.5798 | 0.0001
GEN-2017-183 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.2073 | 8.8104 | 0.6031
GEN-2017-183 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.1053 | 17.6377 | 0.5324
GEN-2017-183 | 03 CENTRAL | 992001 | VSC2_1 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-183 | 03 CENTRAL | 992002 | VSC2_2 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-183 | 03 CENTRAL | 992003 | VSC2_3 | 345 | 7.1232 | 7.1234 | 0.0002
GEN-2017-183 | 03 CENTRAL | 992005 | VSC2_5 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-183 | 03 CENTRAL | 992006 | VSC2_6 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-184 | 03 CENTRAL | 300039 | 7FAIRPT | 345 | 12.8632 | 12.9083 | 0.0451
GEN-2017-184 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 18.2119 | 18.213 | 0.0011
GEN-2017-184 | 03 CENTRAL | 300073 | 5GENTRY | 161 | 10.2399 | 10.2458 | 0.0059
GEN-2017-184 | 03 CENTRAL | 300076 | 5FAIRPTB2 | 161 | 16.8468 | 16.8683 | 0.0215
GEN-2017-184 | 03 CENTRAL | 300249 | 2FAIRPT | 69 | 17.2785 | 17.2867 | 0.0082
GEN-2017-184 | 03 CENTRAL | 301347 | 5WINSLOW | 161 | 8.929 | 8.9346 | 0.0056
GEN-2017-184 | 03 CENTRAL | 301559 | 5FAIRPTXF3 | 161 | 16.865 | 16.8866 | 0.0216
GEN-2017-184 | 03 CENTRAL | 301564 | 5FAIRPTB1 | 161 | 16.8028 | 16.8241 | 0.0213
GEN-2017-184 | 03 CENTRAL | 345088 | 7MCCREDIE | 345 | 14.2488 | 14.2495 | 0.0007
GEN-2017-184 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 16.4533 | 16.4553 | 0.002
GEN-2017-184 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.4848 | 22.486 | 0.0012
GEN-2017-184 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 16.5294 | 16.5377 | 0.0083
GEN-2017-184 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8374 | 24.8418 | 0.0044
GEN-2017-184 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 28.3411 | 28.4251 | 0.084
GEN-2017-184 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 22.6149 | 22.6421 | 0.0272
GEN-2017-184 | 03 CENTRAL | 533211 | ARNOLD 3 | 115 | 8.4267 | 8.4283 | 0.0016
GEN-2017-184 | 03 CENTRAL | 533244 | JARBALO3 | 115 | 27.415 | 27.431 | 0.016
GEN-2017-184 | 03 CENTRAL | 533259 | NW LEAV3 | 115 | 17.6651 | 17.6733 | 0.0082
GEN-2017-184 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 37.8121 | 37.8519 | 0.0398
GEN-2017-184 | 03 CENTRAL | 533272 | THORNTN3 | 115 | 16.5828 | 16.59 | 0.0072
GEN-2017-184 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 27.9741 | 27.9864 | 0.0123
GEN-2017-184 | 03 CENTRAL | 541137 | ALABAMA_CAP5 | 161 | 10.8068 | 10.8273 | 0.0205
GEN-2017-184 | 03 CENTRAL | 541144 | NASHUA_CAP5 | 161 | 24.631 | 24.7059 | 0.0749
GEN-2017-184 | 03 CENTRAL | 541145 | RNRIDGE_CAP5 | 161 | 20.3437 | 20.3778 | 0.0341
GEN-2017-184 | 03 CENTRAL | 541147 | ST JOE_CAP5 | 161 | 18.6744 | 18.7432 | 0.0688
GEN-2017-184 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 11.7089 | 11.7132 | 0.0043
GEN-2017-184 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.9445 | 20.9599 | 0.0154
GEN-2017-184 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 20.5603 | 20.7783 | 0.218
GEN-2017-184 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.1103 | 19.1273 | 0.017
GEN-2017-184 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.9522 | 22.0014 | 0.0492
GEN-2017-184 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.5098 | 27.5409 | 0.0311
GEN-2017-184 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 28.7249 | 28.8269 | 0.102
GEN-2017-184 | 03 CENTRAL | 541204 | SMTHVL 5 | 161 | 21.4583 | 21.513 | 0.0547
GEN-2017-184 | 03 CENTRAL | 541214 | TWA 5 | 161 | 15.4228 | 15.4435 | 0.0207
GEN-2017-184 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 13.7461 | 13.762 | 0.0159
GEN-2017-184 | 03 CENTRAL | 541221 | PLTCTY 5 | 161 | 15.6949 | 15.7201 | 0.0252
GEN-2017-184 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 34.938 | 34.9521 | 0.0141
GEN-2017-184 | 03 CENTRAL | 541230 | RNRIDGE5 | 161 | 23.0591 | 23.1029 | 0.0438
GEN-2017-184 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 15.2299 | 15.2524 | 0.0225
GEN-2017-184 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 29.0785 | 29.1127 | 0.0342
GEN-2017-184 | 03 CENTRAL | 541251 | MARYVLE5 | 161 | 11.5885 | 11.5916 | 0.0031
GEN-2017-184 | 03 CENTRAL | 541253 | ST JOE 5 | 161 | 20.9353 | 21.0218 | 0.0865
GEN-2017-184 | 03 CENTRAL | 541254 | EAST 5 | 161 | 16.3284 | 16.3794 | 0.051
GEN-2017-184 | 03 CENTRAL | 541255 | LAKE RD5 | 161 | 13.1953 | 13.2258 | 0.0305
GEN-2017-184 | 03 CENTRAL | 541256 | IND PRK5 | 161 | 15.8112 | 15.8574 | 0.0462
GEN-2017-184 | 03 CENTRAL | 541257 | COOK 5 | 161 | 14.6175 | 14.6577 | 0.0402
GEN-2017-184 | 03 CENTRAL | 541258 | WOODBIN5 | 161 | 17.6003 | 17.6606 | 0.0603
GEN-2017-184 | 03 CENTRAL | 541260 | RNRDGE 2 | 69 | 5.42 | 5.4207 | 0.0007
GEN-2017-184 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.8773 | 5.878 | 0.0007
GEN-2017-184 | 03 CENTRAL | 541318 | NCONGRS5 | 161 | 18.789 | 18.8187 | 0.0297
GEN-2017-184 | 03 CENTRAL | 541349 | POPE | 161 | 12.9695 | 12.9895 | 0.02
GEN-2017-184 | 03 CENTRAL | 541350 | IATAN5 | 161 | 15.5104 | 15.5313 | 0.0209
GEN-2017-184 | 03 CENTRAL | 541351 | WESTON 5 | 161 | 13.3917 | 13.4078 | 0.0161
GEN-2017-184 | 03 CENTRAL | 541354 | ALABAMA5 | 161 | 11.528 | 11.5513 | 0.0233
GEN-2017-184 | 03 CENTRAL | 541355 | EDMOND5 | 161 | 13.2093 | 13.2409 | 0.0316
GEN-2017-184 | 03 CENTRAL | 541358 | AMOIL 2 | 69 | 4.0377 | 4.0381 | 0.0004
GEN-2017-184 | 03 CENTRAL | 541359 | MRVL#2 | 69 | 3.7281 | 3.7283 | 0.0002
GEN-2017-184 | 03 CENTRAL | 541362 | BURLNGTNJCT2 | 69 | 1.7275 | 1.7275 | 0
GEN-2017-184 | 03 CENTRAL | 541363 | TARKIO_2 | 69 | 0.9663 | 0.9663 | 0
GEN-2017-184 | 03 CENTRAL | 541364 | FAIRFAX2 | 69 | 0.8226 | 0.8226 | 0
GEN-2017-184 | 03 CENTRAL | 541365 | NTHWARD2 | 69 | 0.6958 | 0.6958 | 0
GEN-2017-184 | 03 CENTRAL | 541366 | MNDCITY2 | 69 | 1.4143 | 1.4144 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541367 | BRWNCRV2 | 69 | 1.7386 | 1.7387 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541368 | MIDWY1 2 | 69 | 4.0509 | 4.0513 | 0.0004
GEN-2017-184 | 03 CENTRAL | 541369 | MIDWAY_5 | 161 | 6.1761 | 6.1784 | 0.0023
GEN-2017-184 | 03 CENTRAL | 541376 | AMOILTP2 | 69 | 3.5989 | 3.5992 | 0.0003
GEN-2017-184 | 03 CENTRAL | 541377 | KELLOG 2 | 69 | 2.5137 | 2.5138 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541378 | MRVL#1 | 69 | 3.6919 | 3.692 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541379 | PICKRG_2 | 69 | 2.6105 | 2.6106 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541380 | NODAWAY2 | 69 | 3.0736 | 3.0737 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541381 | FILMORE2 | 69 | 3.2609 | 3.261 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541389 | MDWYTP 2 | 69 | 3.9153 | 3.9157 | 0.0004
GEN-2017-184 | 03 CENTRAL | 541390 | MIDWY2 2 | 69 | 4.056 | 4.0564 | 0.0004
GEN-2017-184 | 03 CENTRAL | 541391 | SAVANAH2 | 69 | 1.9033 | 1.9036 | 0.0003
GEN-2017-184 | 03 CENTRAL | 541392 | EDMOND2 | 69 | 3.6536 | 3.6546 | 0.001
GEN-2017-184 | 03 CENTRAL | 541394 | AVENUECTY 5 | 161 | 6.3984 | 6.4031 | 0.0047
GEN-2017-184 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 19.0273 | 19.1752 | 0.1479
GEN-2017-184 | 03 CENTRAL | 541401 | EASTOWN5 | 161 | 17.9975 | 18.0582 | 0.0607
GEN-2017-184 | 03 CENTRAL | 541408 | FILLMORE_TP2 | 69 | 3.5696 | 3.5698 | 0.0002
GEN-2017-184 | 03 CENTRAL | 541409 | PICKRG_TP_2 | 69 | 3.5696 | 3.5698 | 0.0002
GEN-2017-184 | 03 CENTRAL | 541411 | MC REAC1 | 345 | 10.9828 | 10.9865 | 0.0037
GEN-2017-184 | 03 CENTRAL | 541412 | MC REAC2 | 345 | 10.9828 | 10.9865 | 0.0037
GEN-2017-184 | 03 CENTRAL | 541413 | MC REAC3 | 345 | 10.9828 | 10.9865 | 0.0037
GEN-2017-184 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.5203 | 19.5592 | 0.0389
GEN-2017-184 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 9.3268 | 9.3311 | 0.0043
GEN-2017-184 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 8.1723 | 8.1756 | 0.0033
GEN-2017-184 | 03 CENTRAL | 541510 | HOLT 7 | 345 | 18.2525 | 18.2602 | 0.0077
GEN-2017-184 | 03 CENTRAL | 541511 | ROCKCK7 | 345 | 11.5492 | 11.5519 | 0.0027
GEN-2017-184 | 03 CENTRAL | 541517 | HOLT_REACT7 | 345 | 18.0649 | 18.0725 | 0.0076
GEN-2017-184 | 03 CENTRAL | 541537 | MULLINCRK1_1 | 69 | 2.1632 | 2.1632 | 0
GEN-2017-184 | 03 CENTRAL | 541538 | MULLINCRK1_2 | 69 | 2.5547 | 2.5548 | 0.0001
GEN-2017-184 | 03 CENTRAL | 541543 | OUTLAW | 345 | 8.8278 | 8.8293 | 0.0015
GEN-2017-184 | 03 CENTRAL | 542944 | BARRY_CAP 5 | 161 | 16.8413 | 16.862 | 0.0207
GEN-2017-184 | 03 CENTRAL | 542946 | GLADSTN_CAP5 | 161 | 16.8957 | 16.9154 | 0.0197
GEN-2017-184 | 03 CENTRAL | 542948 | NEASTS_CAP5 | 161 | 37.4333 | 37.4845 | 0.0512
GEN-2017-184 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.6032 | 23.7308 | 0.1276
GEN-2017-184 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 59.2786 | 59.4306 | 0.152
GEN-2017-184 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 53.5512 | 53.6732 | 0.122
GEN-2017-184 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.435 | 24.4621 | 0.0271
GEN-2017-184 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 22.8991 | 23.2402 | 0.3411
GEN-2017-184 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 31.3873 | 31.5568 | 0.1695
GEN-2017-184 | 03 CENTRAL | 542985 | NEASTS5 | 161 | 47.7842 | 47.8676 | 0.0834
GEN-2017-184 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 35.7556 | 35.8009 | 0.0453
GEN-2017-184 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 39.8001 | 39.8688 | 0.0687
GEN-2017-184 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 37.2655 | 37.3202 | 0.0547
GEN-2017-184 | 03 CENTRAL | 543015 | AVONDAL5 | 161 | 30.4679 | 30.513 | 0.0451
GEN-2017-184 | 03 CENTRAL | 543016 | GLADSTN5 | 161 | 18.7272 | 18.7514 | 0.0242
GEN-2017-184 | 03 CENTRAL | 543017 | WETHRBY5 | 161 | 16.9607 | 16.9783 | 0.0176
GEN-2017-184 | 03 CENTRAL | 543019 | BARRY 5 | 161 | 18.6605 | 18.6859 | 0.0254
GEN-2017-184 | 03 CENTRAL | 543020 | BRMGHAM5 | 161 | 27.2085 | 27.2398 | 0.0313
GEN-2017-184 | 03 CENTRAL | 543022 | CLAYCM15 | 161 | 11.4456 | 11.457 | 0.0114
GEN-2017-184 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.9791 | 13.9873 | 0.0082
GEN-2017-184 | 03 CENTRAL | 543025 | LINECRK5 | 161 | 17.3552 | 17.3738 | 0.0186
GEN-2017-184 | 03 CENTRAL | 543026 | TIFFANY5 | 161 | 20.1206 | 20.1513 | 0.0307
GEN-2017-184 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 34.0489 | 34.1019 | 0.053
GEN-2017-184 | 03 CENTRAL | 543028 | NASHUA-5 | 161 | 28.8469 | 28.9499 | 0.103
GEN-2017-184 | 03 CENTRAL | 543029 | SHOLCRK5 | 161 | 17.7736 | 17.8012 | 0.0276
GEN-2017-184 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 58.4351 | 58.5827 | 0.1476
GEN-2017-184 | 03 CENTRAL | 543130 | HAWTHS_XF5 | 161 | 58.3734 | 58.5208 | 0.1474
GEN-2017-184 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 59.9627 | 60.12 | 0.1573
GEN-2017-184 | 03 CENTRAL | 543666 | NEASTN5 | 161 | 48.1791 | 48.2645 | 0.0854
GEN-2017-184 | 03 CENTRAL | 548814 | SUB M-161 | 161 | 21.1176 | 21.135 | 0.0174
GEN-2017-184 | 03 CENTRAL | 548820 | SUB N-161 | 161 | 17.1466 | 17.1589 | 0.0123
GEN-2017-184 | 03 CENTRAL | 560746 | G13-002-TAP | 115 | 42.712 | 42.7141 | 0.0021
GEN-2017-184 | 03 CENTRAL | 583700 | GEN-2013-019 | 115 | 18.464 | 18.4644 | 0.0004
GEN-2017-184 | 03 CENTRAL | 585241 | GEN-2015-088 | 345 | 11.2758 | 11.2763 | 0.0005
GEN-2017-184 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 4.4327 | 4.4337 | 0.001
GEN-2017-184 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 13.3687 | 13.3841 | 0.0154
GEN-2017-184 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 8.2292 | 8.234 | 0.0048
GEN-2017-184 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 4.1235 | 4.1243 | 0.0008
GEN-2017-184 | 03 CENTRAL | 635000 | CBLUFFS3 | 345 | 31.8531 | 31.8547 | 0.0016
GEN-2017-184 | 03 CENTRAL | 635017 | ATCHSN 3 | 345 | 22.8031 | 22.8172 | 0.0141
GEN-2017-184 | 03 CENTRAL | 635018 | WESTBORO 3 | 345 | 21.1313 | 21.1428 | 0.0115
GEN-2017-184 | 03 CENTRAL | 635570 | ORIENT 3 | 345 | 18.7653 | 18.7662 | 0.0009
GEN-2017-184 | 03 CENTRAL | 637084 | J476 SHENHLL | 345 | 20.9922 | 21.0035 | 0.0113
GEN-2017-184 | 03 CENTRAL | 640139 | COOPER 3 | 345 | 29.6872 | 29.7225 | 0.0353
GEN-2017-184 | 03 CENTRAL | 640140 | COOPER 5 | 161 | 18.4677 | 18.473 | 0.0053
GEN-2017-184 | 03 CENTRAL | 640141 | COOPER_ESST8 | 69 | 4.6918 | 4.692 | 0.0002
GEN-2017-184 | 03 CENTRAL | 640143 | COOPER_602 8 | 69 | 2.0097 | 2.0097 | 0
GEN-2017-184 | 03 CENTRAL | 640171 | FIRTH 7 | 115 | 6.999 | 6.999 | 0
GEN-2017-184 | 03 CENTRAL | 640234 | HUMBOLT5 | 161 | 7.9864 | 7.9869 | 0.0005
GEN-2017-184 | 03 CENTRAL | 640271 | MCCOOL 3 | 345 | 11.0498 | 11.05 | 0.0002
GEN-2017-184 | 03 CENTRAL | 640277 | MOORE 3 | 345 | 22.8788 | 22.8814 | 0.0026
GEN-2017-184 | 03 CENTRAL | 640278 | SHELDON7 | 115 | 44.1519 | 44.154 | 0.0021
GEN-2017-184 | 03 CENTRAL | 640446 | COOPER 8 | 69 | 4.7899 | 4.79 | 0.0001
GEN-2017-184 | 03 CENTRAL | 640525 | TOBIAS 3 | 345 | 11.2758 | 11.2763 | 0.0005
GEN-2017-184 | 03 CENTRAL | 640590 | MONOLITH 3 | 345 | 22.4248 | 22.4274 | 0.0026
GEN-2017-184 | 03 CENTRAL | 640591 | MONOLITH 7 | 115 | 42.712 | 42.7141 | 0.0021
GEN-2017-184 | 03 CENTRAL | 645454 | S3454 3 | 345 | 28.6547 | 28.6568 | 0.0021
GEN-2017-184 | 03 CENTRAL | 645455 | S3455 3 | 345 | 31.7605 | 31.7629 | 0.0024
GEN-2017-184 | 03 CENTRAL | 645456 | S3456 3 | 345 | 34.3038 | 34.3064 | 0.0026
GEN-2017-184 | 03 CENTRAL | 645458 | S3458 3 | 345 | 30.6934 | 30.7028 | 0.0094
GEN-2017-184 | 03 CENTRAL | 645459 | S3459 3 | 345 | 24.9657 | 24.9669 | 0.0012
GEN-2017-184 | 03 CENTRAL | 645740 | S3740 3 | 345 | 22.8009 | 22.8026 | 0.0017
GEN-2017-184 | 03 CENTRAL | 646206 | S1206 5 | 161 | 44.6646 | 44.6662 | 0.0016
GEN-2017-184 | 03 CENTRAL | 646263 | S1263 5 | 161 | 8.1072 | 8.1077 | 0.0005
GEN-2017-184 | 03 CENTRAL | 646280 | S1280 5 | 161 | 10.3212 | 10.3221 | 0.0009
GEN-2017-184 | 03 CENTRAL | 650114 | NW68HOLDRG3 | 345 | 17.3276 | 17.3287 | 0.0011
GEN-2017-184 | 03 CENTRAL | 650185 | WAGENER 3 | 345 | 20.8796 | 20.8814 | 0.0018
GEN-2017-184 | 03 CENTRAL | 650189 | 103&ROKEBY3 | 345 | 20.7298 | 20.7319 | 0.0021
GEN-2017-184 | 03 CENTRAL | 760746 | GEN-2017-115 | 345 | 12.555 | 12.5586 | 0.0036
GEN-2017-184 | 03 CENTRAL | 761208 | GEN-2017-210 | 345 | 9.6779 | 9.6781 | 0.0002
GEN-2017-184 | 03 CENTRAL | 761292 | GEN-2017-181 | 345 | 6.6274 | 6.6276 | 0.0002
GEN-2017-184 | 03 CENTRAL | 761313 | GEN-2017-182 | 345 | 5.5797 | 5.5798 | 0.0001
GEN-2017-184 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.1864 | 8.8104 | 0.624
GEN-2017-184 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.0861 | 17.6377 | 0.5516
GEN-2017-184 | 03 CENTRAL | 992001 | VSC2_1 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-184 | 03 CENTRAL | 992002 | VSC2_2 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-184 | 03 CENTRAL | 992003 | VSC2_3 | 345 | 7.1232 | 7.1234 | 0.0002
GEN-2017-184 | 03 CENTRAL | 992005 | VSC2_5 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-184 | 03 CENTRAL | 992006 | VSC2_6 | 276 | 5.7604 | 5.7605 | 0.0001
GEN-2017-188 | 03 CENTRAL | 300649 | 2JASPER | 69 | 4.9492 | 4.9503 | 0.0011
GEN-2017-188 | 03 CENTRAL | 300653 | 2MEDOC | 69 | 2.493 | 2.4933 | 0.0003
GEN-2017-188 | 03 CENTRAL | 300744 | 2DMNDGR | 69 | 2.6054 | 2.6061 | 0.0007
GEN-2017-188 | 03 CENTRAL | 300745 | 2DMNDTP | 69 | 5.5988 | 5.6021 | 0.0033
GEN-2017-188 | 03 CENTRAL | 300751 | 2REEDS | 69 | 6.5658 | 6.5697 | 0.0039
GEN-2017-188 | 03 CENTRAL | 505485 | WASHBURN5 | 161 | 8.1091 | 8.1115 | 0.0024
GEN-2017-188 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.8854 | 15.9199 | 0.0345
GEN-2017-188 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.9055 | 17.025 | 0.1195
GEN-2017-188 | 03 CENTRAL | 505490 | CARTHG 2 | 69 | 14.0922 | 14.1176 | 0.0254
GEN-2017-188 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 27.7596 | 27.7653 | 0.0057
GEN-2017-188 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 5.1242 | 5.1329 | 0.0087
GEN-2017-188 | 03 CENTRAL | 532932 | LITCH 5 | 161 | 9.1063 | 9.2895 | 0.1832
GEN-2017-188 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.6867 | 8.7077 | 0.021
GEN-2017-188 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.6821 | 8.7031 | 0.021
GEN-2017-188 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.7914 | 23.8161 | 0.0247
GEN-2017-188 | 03 CENTRAL | 532938 | FRANKLIN5 | 161 | 7.9854 | 8.0942 | 0.1088
GEN-2017-188 | 03 CENTRAL | 533652 | WARE 2 | 69 | 3.5497 | 3.5537 | 0.004
GEN-2017-188 | 03 CENTRAL | 533756 | AQUARS 2 | 69 | 8.2955 | 8.3453 | 0.0498
GEN-2017-188 | 03 CENTRAL | 533759 | DEPAUL 2 | 69 | 9.6013 | 9.6665 | 0.0652
GEN-2017-188 | 03 CENTRAL | 533761 | GIRARD 2 | 69 | 4.6759 | 4.6846 | 0.0087
GEN-2017-188 | 03 CENTRAL | 533762 | GIR JCT2 | 69 | 6.6767 | 6.6946 | 0.0179
GEN-2017-188 | 03 CENTRAL | 533763 | HUDSON-2 | 69 | 4.7996 | 4.8103 | 0.0107
GEN-2017-188 | 03 CENTRAL | 533764 | HUDSJCT2 | 69 | 8.3401 | 8.3902 | 0.0501
GEN-2017-188 | 03 CENTRAL | 533765 | LITCH N2 | 69 | 13.039 | 13.1654 | 0.1264
GEN-2017-188 | 03 CENTRAL | 533766 | LITCH S2 | 69 | 13.0398 | 13.1662 | 0.1264
GEN-2017-188 | 03 CENTRAL | 533767 | MULBERY2 | 69 | 8.379 | 8.4252 | 0.0462
GEN-2017-188 | 03 CENTRAL | 533769 | PITNAC 2 | 69 | 11.4575 | 11.5537 | 0.0962
GEN-2017-188 | 03 CENTRAL | 533770 | PITTSBG2 | 69 | 8.7446 | 8.7992 | 0.0546
GEN-2017-188 | 03 CENTRAL | 533771 | ROUSE 2 | 69 | 9.7418 | 9.8097 | 0.0679
GEN-2017-188 | 03 CENTRAL | 533772 | SE1GREE2 | 69 | 6.3095 | 6.3162 | 0.0067
GEN-2017-188 | 03 CENTRAL | 533773 | SOPITT 2 | 69 | 5.7394 | 5.7547 | 0.0153
GEN-2017-188 | 03 CENTRAL | 533774 | SHEFFLD2 | 69 | 4.4189 | 4.4276 | 0.0087
GEN-2017-188 | 03 CENTRAL | 533775 | FRONTEN2 | 69 | 8.8133 | 8.8664 | 0.0531
GEN-2017-188 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0258 | 24.0463 | 0.0205
GEN-2017-188 | 03 CENTRAL | 533876 | FRANKLIN2 | 69 | 11.4212 | 11.4988 | 0.0776
GEN-2017-188 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 7.7047 | 7.7143 | 0.0096
GEN-2017-188 | 03 CENTRAL | 543651 | PRQN_WIND5 | 161 | 6.7631 | 6.7698 | 0.0067
GEN-2017-188 | 03 CENTRAL | 547459 | WWR477 | 161 | 23.4105 | 23.4919 | 0.0814
GEN-2017-188 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 16.6875 | 16.7944 | 0.1069
GEN-2017-188 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 20.3561 | 20.5172 | 0.1611
GEN-2017-188 | 03 CENTRAL | 547469 | RIV4525 | 161 | 25.1981 | 25.2916 | 0.0935
GEN-2017-188 | 03 CENTRAL | 547470 | JOP145 5 | 161 | 19.7092 | 19.7988 | 0.0896
GEN-2017-188 | 03 CENTRAL | 547471 | NEO184 5 | 161 | 14.6384 | 14.6657 | 0.0273
GEN-2017-188 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 18.0954 | 18.1418 | 0.0464
GEN-2017-188 | 03 CENTRAL | 547476 | ASB349 5 | 161 | 11.0774 | 11.4526 | 0.3752
GEN-2017-188 | 03 CENTRAL | 547477 | CJ 366 5 | 161 | 12.7119 | 12.871 | 0.1591
GEN-2017-188 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 15.5297 | 15.5643 | 0.0346
GEN-2017-188 | 03 CENTRAL | 547480 | MON383 5 | 161 | 12.098 | 12.1117 | 0.0137
GEN-2017-188 | 03 CENTRAL | 547485 | CAR395 5 | 161 | 12.5119 | 12.6202 | 0.1083
GEN-2017-188 | 03 CENTRAL | 547490 | FIR417 5 | 161 | 14.7152 | 14.8659 | 0.1507
GEN-2017-188 | 03 CENTRAL | 547491 | PUR421 5 | 161 | 9.6965 | 9.84 | 0.1435
GEN-2017-188 | 03 CENTRAL | 547494 | OAK432 5 | 161 | 18.3878 | 18.5187 | 0.1309
GEN-2017-188 | 03 CENTRAL | 547498 | STL439 5 | 161 | 25.7044 | 25.8025 | 0.0981
GEN-2017-188 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.8505 | 23.9316 | 0.0811
GEN-2017-188 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 23.3327 | 23.4121 | 0.0794
GEN-2017-188 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.7448 | 24.834 | 0.0892
GEN-2017-188 | 03 CENTRAL | 547527 | WEB436 2 | 69 | 9.7318 | 9.7413 | 0.0095
GEN-2017-188 | 03 CENTRAL | 547533 | ATL109 2 | 69 | 21.3157 | 21.3643 | 0.0486
GEN-2017-188 | 03 CENTRAL | 547534 | ORO110 2 | 69 | 18.3825 | 18.4196 | 0.0371
GEN-2017-188 | 03 CENTRAL | 547539 | JOP145 2 | 69 | 21.4567 | 21.5003 | 0.0436
GEN-2017-188 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 18.0918 | 18.1148 | 0.023
GEN-2017-188 | 03 CENTRAL | 547556 | OAK280 2 | 69 | 16.2675 | 16.2963 | 0.0288
GEN-2017-188 | 03 CENTRAL | 547574 | JOP341 2 | 69 | 18.5595 | 18.5934 | 0.0339
GEN-2017-188 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 15.3911 | 15.4191 | 0.028
GEN-2017-188 | 03 CENTRAL | 588500 | GEN-2017-005 | 161 | 7.0544 | 7.0863 | 0.0319
GEN-2017-188 | 03 CENTRAL | 588504 | G17-005-TAP | 161 | 7.142 | 7.1749 | 0.0329
GEN-2017-188 | 03 CENTRAL | 588980 | GEN-2017-060 | 161 | 6.306 | 6.311 | 0.005
GEN-2017-188 | 03 CENTRAL | 589200 | GEN-2017-082 | 161 | 7.6322 | 7.7977 | 0.1655
GEN-2017-188 | 03 CENTRAL | 760242 | GEN-2017-188 | 161 | 1.505 | 1.981 | 0.476
GEN-2017-195 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 13.6715 | 13.6745 | 0.003
GEN-2017-195 | 03 CENTRAL | 300124 | 5HOLDENB2 | 161 | 7.7997 | 7.8006 | 0.0009
GEN-2017-195 | 03 CENTRAL | 300692 | 2CLINTN | 69 | 13.8912 | 13.8925 | 0.0013
GEN-2017-195 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.044 | 16.0466 | 0.0026
GEN-2017-195 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.816 | 24.8163 | 0.0003
GEN-2017-195 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.2325 | 13.2338 | 0.0013
GEN-2017-195 | 03 CENTRAL | 301477 | 5OSCEOKCTP | 161 | 6.6369 | 6.6373 | 0.0004
GEN-2017-195 | 03 CENTRAL | 301522 | 5OSCEOKC | 161 | 6.6296 | 6.63 | 0.0004
GEN-2017-195 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 16.4538 | 16.4553 | 0.0015
GEN-2017-195 | 03 CENTRAL | 505502 | TRUMAN 5 | 161 | 7.514 | 7.5144 | 0.0004
GEN-2017-195 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.5884 | 11.5886 | 0.0002
GEN-2017-195 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.1818 | 12.1825 | 0.0007
GEN-2017-195 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.6897 | 19.6901 | 0.0004
GEN-2017-195 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 16.5254 | 16.5377 | 0.0123
GEN-2017-195 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8293 | 24.8418 | 0.0125
GEN-2017-195 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.5986 | 10.6006 | 0.002
GEN-2017-195 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6248 | 19.6479 | 0.0231
GEN-2017-195 | 03 CENTRAL | 532769 | LANG 7 | 345 | 19.3679 | 19.3903 | 0.0224
GEN-2017-195 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.6576 | 13.6661 | 0.0085
GEN-2017-195 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6959 | 11.6973 | 0.0014
GEN-2017-195 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 28.3539 | 28.4251 | 0.0712
GEN-2017-195 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.6919 | 17.7815 | 0.0896
GEN-2017-195 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 22.4614 | 22.6421 | 0.1807
GEN-2017-195 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.9666 | 15.9817 | 0.0151
GEN-2017-195 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 12.0443 | 12.0464 | 0.0021
GEN-2017-195 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.1493 | 11.1511 | 0.0018
GEN-2017-195 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7981 | 9.7991 | 0.001
GEN-2017-195 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.5235 | 9.5244 | 0.0009
GEN-2017-195 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 21.4754 | 21.4794 | 0.004
GEN-2017-195 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2773 | 7.2777 | 0.0004
GEN-2017-195 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0722 | 6.0724 | 0.0002
GEN-2017-195 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0436 | 5.0437 | 0.0001
GEN-2017-195 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.1363 | 7.1376 | 0.0013
GEN-2017-195 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.4044 | 19.4083 | 0.0039
GEN-2017-195 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9477 | 6.9479 | 0.0002
GEN-2017-195 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.3048 | 18.3104 | 0.0056
GEN-2017-195 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.9698 | 18.9731 | 0.0033
GEN-2017-195 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.621 | 5.6211 | 0.0001
GEN-2017-195 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 25.0827 | 25.0892 | 0.0065
GEN-2017-195 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.7032 | 18.7116 | 0.0084
GEN-2017-195 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.2186 | 14.2196 | 0.001
GEN-2017-195 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5497 | 16.5586 | 0.0089
GEN-2017-195 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.4275 | 10.4286 | 0.0011
GEN-2017-195 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2505 | 9.2513 | 0.0008
GEN-2017-195 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7943 | 13.8005 | 0.0062
GEN-2017-195 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.5132 | 10.516 | 0.0028
GEN-2017-195 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.9094 | 13.9216 | 0.0122
GEN-2017-195 | 03 CENTRAL | 532852 | JEC 6 | 230 | 25.9784 | 25.9872 | 0.0088
GEN-2017-195 | 03 CENTRAL | 532853 | LAWHILL6 | 230 | 14.1183 | 14.1311 | 0.0128
GEN-2017-195 | 03 CENTRAL | 532854 | LEC U5 6 | 230 | 13.9856 | 13.9981 | 0.0125
GEN-2017-195 | 03 CENTRAL | 532855 | MIDLAND6 | 230 | 12.5323 | 12.5424 | 0.0101
GEN-2017-195 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.4988 | 22.5589 | 0.0601
GEN-2017-195 | 03 CENTRAL | 532857 | TECHILL6 | 230 | 11.1863 | 11.1979 | 0.0116
GEN-2017-195 | 03 CENTRAL | 532861 | EMANHAT6 | 230 | 10.5845 | 10.5859 | 0.0014
GEN-2017-195 | 03 CENTRAL | 532862 | MCDOWEL6 | 230 | 7.3274 | 7.3287 | 0.0013
GEN-2017-195 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.5136 | 14.5206 | 0.007
GEN-2017-195 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8391 | 13.8406 | 0.0015
GEN-2017-195 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.4767 | 8.4778 | 0.0011
GEN-2017-195 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 5.0448 | 5.0452 | 0.0004
GEN-2017-195 | 03 CENTRAL | 532912 | EDWRDVL5 | 161 | 22.2971 | 22.3296 | 0.0325
GEN-2017-195 | 03 CENTRAL | 532914 | SPRGHL 5 | 161 | 11.1621 | 11.1769 | 0.0148
GEN-2017-195 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.7025 | 8.7031 | 0.0006
GEN-2017-195 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.8129 | 23.8161 | 0.0032
GEN-2017-195 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.5043 | 28.5075 | 0.0032
GEN-2017-195 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.4308 | 25.4339 | 0.0031
GEN-2017-195 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.474 | 25.4772 | 0.0032
GEN-2017-195 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.3549 | 25.358 | 0.0031
GEN-2017-195 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.9245 | 31.9281 | 0.0036
GEN-2017-195 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.4738 | 31.4772 | 0.0034
GEN-2017-195 | 03 CENTRAL | 533151 | AUBURN 3 | 115 | 22.0667 | 22.0804 | 0.0137
GEN-2017-195 | 03 CENTRAL | 533153 | COLINE 3 | 115 | 18.1184 | 18.1272 | 0.0088
GEN-2017-195 | 03 CENTRAL | 533155 | CROOKED3 | 115 | 20.8706 | 20.8829 | 0.0123
GEN-2017-195 | 03 CENTRAL | 533163 | HOYT 3 | 115 | 23.5511 | 23.5613 | 0.0102
GEN-2017-195 | 03 CENTRAL | 533166 | INDIANH3 | 115 | 17.8618 | 17.8707 | 0.0089
GEN-2017-195 | 03 CENTRAL | 533167 | KEENE 3 | 115 | 10.0564 | 10.0586 | 0.0022
GEN-2017-195 | 03 CENTRAL | 533176 | SHAWNEE3 | 115 | 13.3357 | 13.3412 | 0.0055
GEN-2017-195 | 03 CENTRAL | 533181 | TECHILW3 | 115 | 25.4547 | 25.4755 | 0.0208
GEN-2017-195 | 03 CENTRAL | 533182 | TECHILE3 | 115 | 25.5098 | 25.5307 | 0.0209
GEN-2017-195 | 03 CENTRAL | 533187 | 27CROCO3 | 115 | 18.6188 | 18.6295 | 0.0107
GEN-2017-195 | 03 CENTRAL | 533194 | SHERWOD3 | 115 | 20.1623 | 20.1737 | 0.0114
GEN-2017-195 | 03 CENTRAL | 533203 | TEC E 3 | 115 | 24.262 | 24.2808 | 0.0188
GEN-2017-195 | 03 CENTRAL | 533211 | ARNOLD 3 | 115 | 8.4263 | 8.4283 | 0.002
GEN-2017-195 | 03 CENTRAL | 533232 | BALDCRK3 | 115 | 14.5245 | 14.5315 | 0.007
GEN-2017-195 | 03 CENTRAL | 533236 | FAIRGDS3 | 115 | 19.0106 | 19.0239 | 0.0133
GEN-2017-195 | 03 CENTRAL | 533240 | EUDORA 3 | 115 | 11.93 | 11.9369 | 0.0069
GEN-2017-195 | 03 CENTRAL | 533244 | JARBALO3 | 115 | 27.4043 | 27.431 | 0.0267
GEN-2017-195 | 03 CENTRAL | 533248 | LEC U3 3 | 115 | 25.5054 | 25.5266 | 0.0212
GEN-2017-195 | 03 CENTRAL | 533249 | LEC U4 3 | 115 | 25.4726 | 25.493 | 0.0204
GEN-2017-195 | 03 CENTRAL | 533250 | LWRNCHL3 | 115 | 27.1052 | 27.1289 | 0.0237
GEN-2017-195 | 03 CENTRAL | 533252 | MIDLADN3 | 115 | 26.0347 | 26.058 | 0.0233
GEN-2017-195 | 03 CENTRAL | 533253 | MOCKBRD3 | 115 | 17.9286 | 17.9393 | 0.0107
GEN-2017-195 | 03 CENTRAL | 533254 | MOONLIT3 | 115 | 11.3607 | 11.3713 | 0.0106
GEN-2017-195 | 03 CENTRAL | 533259 | NW LEAV3 | 115 | 17.6636 | 17.6733 | 0.0097
GEN-2017-195 | 03 CENTRAL | 533261 | PENTAGN3 | 115 | 22.5812 | 22.6124 | 0.0312
GEN-2017-195 | 03 CENTRAL | 533264 | 6TH ST 3 | 115 | 18.5808 | 18.5924 | 0.0116
GEN-2017-195 | 03 CENTRAL | 533265 | SOUTHTN3 | 115 | 11.4179 | 11.4287 | 0.0108
GEN-2017-195 | 03 CENTRAL | 533267 | SPRINGH3 | 115 | 10.0718 | 10.0803 | 0.0085
GEN-2017-195 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 37.8066 | 37.8519 | 0.0453
GEN-2017-195 | 03 CENTRAL | 533269 | STULL 3 | 115 | 12.0616 | 12.0663 | 0.0047
GEN-2017-195 | 03 CENTRAL | 533270 | STULL T3 | 115 | 12.1846 | 12.1894 | 0.0048
GEN-2017-195 | 03 CENTRAL | 533272 | THORNTN3 | 115 | 16.5812 | 16.59 | 0.0088
GEN-2017-195 | 03 CENTRAL | 533273 | TIMBRLN3 | 115 | 13.6718 | 13.6873 | 0.0155
GEN-2017-195 | 03 CENTRAL | 533278 | WAVERLY3 | 115 | 14.8665 | 14.8846 | 0.0181
GEN-2017-195 | 03 CENTRAL | 533280 | WREN 3 | 115 | 18.9637 | 18.9759 | 0.0122
GEN-2017-195 | 03 CENTRAL | 533281 | MNTCLLO3 | 115 | 23.6708 | 23.7119 | 0.0411
GEN-2017-195 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 27.9224 | 27.9864 | 0.064
GEN-2017-195 | 03 CENTRAL | 533301 | EAST ST3 | 115 | 10.3263 | 10.3281 | 0.0018
GEN-2017-195 | 03 CENTRAL | 533304 | LANG 3 | 115 | 16.1328 | 16.1377 | 0.0049
GEN-2017-195 | 03 CENTRAL | 533305 | MORRIS 3 | 115 | 13.1515 | 13.1544 | 0.0029
GEN-2017-195 | 03 CENTRAL | 533306 | READING3 | 115 | 7.3471 | 7.3482 | 0.0011
GEN-2017-195 | 03 CENTRAL | 533307 | PRAIRIE3 | 115 | 10.4634 | 10.4653 | 0.0019
GEN-2017-195 | 03 CENTRAL | 533309 | WEMPORI3 | 115 | 11.4407 | 11.4428 | 0.0021
GEN-2017-195 | 03 CENTRAL | 533335 | MCDOWEL3 | 115 | 19.4061 | 19.4097 | 0.0036
GEN-2017-195 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.9007 | 3.9008 | 0.0001
GEN-2017-195 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4749 | 3.475 | 0.0001
GEN-2017-195 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5483 | 3.5484 | 0.0001
GEN-2017-195 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1632 | 3.1633 | 0.0001
GEN-2017-195 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1574 | 5.1575 | 0.0001
GEN-2017-195 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5469 | 3.5469 | 0
GEN-2017-195 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8218 | 4.8219 | 0.0001
GEN-2017-195 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2347 | 6.2348 | 0.0001
GEN-2017-195 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0449 | 24.0463 | 0.0014
GEN-2017-195 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.8418 | 20.9599 | 0.1181
GEN-2017-195 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.063 | 19.1273 | 0.0643
GEN-2017-195 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.9685 | 22.0014 | 0.0329
GEN-2017-195 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.5201 | 27.5409 | 0.0208
GEN-2017-195 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 16.7028 | 16.7169 | 0.0141
GEN-2017-195 | 03 CENTRAL | 541210 | MARTCTY5 | 161 | 28.2857 | 28.3481 | 0.0624
GEN-2017-195 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 7.66 | 7.6608 | 0.0008
GEN-2017-195 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 34.9076 | 34.9521 | 0.0445
GEN-2017-195 | 03 CENTRAL | 541239 | HSNVL 5 | 161 | 15.7304 | 15.7418 | 0.0114
GEN-2017-195 | 03 CENTRAL | 541240 | ADRIAN 5 | 161 | 8.5222 | 8.525 | 0.0028
GEN-2017-195 | 03 CENTRAL | 541242 | CLINTON5 | 161 | 13.6194 | 13.6224 | 0.003
GEN-2017-195 | 03 CENTRAL | 541243 | LKWINBG5 | 161 | 25.6037 | 25.6303 | 0.0266
GEN-2017-195 | 03 CENTRAL | 541259 | TURNER_RD5 | 161 | 18.507 | 18.5361 | 0.0291
GEN-2017-195 | 03 CENTRAL | 541280 | PHILL 2 | 69 | 10.398 | 10.4001 | 0.0021
GEN-2017-195 | 03 CENTRAL | 541290 | BELTONS2 | 69 | 10.1313 | 10.134 | 0.0027
GEN-2017-195 | 03 CENTRAL | 541291 | FREEMAN2 | 69 | 4.5308 | 4.5314 | 0.0006
GEN-2017-195 | 03 CENTRAL | 541313 | HARRIS | 161 | 26.7717 | 26.7958 | 0.0241
GEN-2017-195 | 03 CENTRAL | 541340 | BELTONS5 | 161 | 19.6435 | 19.6777 | 0.0342
GEN-2017-195 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 21.1453 | 21.184 | 0.0387
GEN-2017-195 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 23.2547 | 23.3053 | 0.0506
GEN-2017-195 | 03 CENTRAL | 541343 | S.HARP 2 | 69 | 4.582 | 4.5826 | 0.0006
GEN-2017-195 | 03 CENTRAL | 541344 | PECULRS5 | 161 | 21.746 | 21.789 | 0.043
GEN-2017-195 | 03 CENTRAL | 541350 | IATAN5 | 161 | 15.5252 | 15.5313 | 0.0061
GEN-2017-195 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 19.1637 | 19.1752 | 0.0115
GEN-2017-195 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.5332 | 19.5592 | 0.026
GEN-2017-195 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 9.3291 | 9.3311 | 0.002
GEN-2017-195 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 8.1741 | 8.1756 | 0.0015
GEN-2017-195 | 03 CENTRAL | 541540 | FREEMAN_SP2 | 69 | 4.2234 | 4.2239 | 0.0005
GEN-2017-195 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6764 | 2.6766 | 0.0002
GEN-2017-195 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 35.3164 | 35.493 | 0.1766
GEN-2017-195 | 03 CENTRAL | 542947 | MERRIAM_CAP5 | 161 | 27.4324 | 27.4995 | 0.0671
GEN-2017-195 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 30.7759 | 30.8392 | 0.0633
GEN-2017-195 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.8608 | 28.678 | 0.8172
GEN-2017-195 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.1969 | 30.3737 | 0.1768
GEN-2017-195 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.7563 | 26.0141 | 0.2578
GEN-2017-195 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.7924 | 40.9926 | 0.2002
GEN-2017-195 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.6989 | 23.7308 | 0.0319
GEN-2017-195 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.198 | 24.4621 | 0.2641
GEN-2017-195 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 44.3875 | 44.6667 | 0.2792
GEN-2017-195 | 03 CENTRAL | 542979 | PFLUMM 5 | 161 | 30.1996 | 30.3109 | 0.1113
GEN-2017-195 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.2143 | 23.2402 | 0.0259
GEN-2017-195 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.4192 | 27.5599 | 0.1407
GEN-2017-195 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 31.506 | 31.5568 | 0.0508
GEN-2017-195 | 03 CENTRAL | 542992 | BENDIX 5 | 161 | 30.3375 | 30.4037 | 0.0662
GEN-2017-195 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 37.4471 | 37.5409 | 0.0938
GEN-2017-195 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 20.0379 | 20.0703 | 0.0324
GEN-2017-195 | 03 CENTRAL | 543001 | FOREST 5 | 161 | 32.0889 | 32.1522 | 0.0633
GEN-2017-195 | 03 CENTRAL | 543002 | MARTCIT5 | 161 | 25.2711 | 25.325 | 0.0539
GEN-2017-195 | 03 CENTRAL | 543007 | SWOPE S5 | 161 | 22.2426 | 22.2668 | 0.0242
GEN-2017-195 | 03 CENTRAL | 543008 | BUNKRDG5 | 161 | 24.514 | 24.5473 | 0.0333
GEN-2017-195 | 03 CENTRAL | 543010 | WINJT S5 | 161 | 23.8224 | 23.8501 | 0.0277
GEN-2017-195 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 37.1117 | 37.2389 | 0.1272
GEN-2017-195 | 03 CENTRAL | 543032 | MERRIAM5 | 161 | 32.6111 | 32.7059 | 0.0948
GEN-2017-195 | 03 CENTRAL | 543033 | BRKRIDG5 | 161 | 24.5978 | 24.6645 | 0.0667
GEN-2017-195 | 03 CENTRAL | 543034 | KNLWRTH5 | 161 | 27.5571 | 27.6326 | 0.0755
GEN-2017-195 | 03 CENTRAL | 543036 | OLATHE 5 | 161 | 27.4803 | 27.5824 | 0.1021
GEN-2017-195 | 03 CENTRAL | 543037 | QUARRY 5 | 161 | 16.2537 | 16.2953 | 0.0416
GEN-2017-195 | 03 CENTRAL | 543038 | LENEXA 5 | 161 | 37.7482 | 37.9286 | 0.1804
GEN-2017-195 | 03 CENTRAL | 543040 | ROEPARK5 | 161 | 30.7475 | 30.8103 | 0.0628
GEN-2017-195 | 03 CENTRAL | 543041 | SHAWNEE5 | 161 | 27.9259 | 27.9878 | 0.0619
GEN-2017-195 | 03 CENTRAL | 543043 | MURLEN 5 | 161 | 18.5364 | 18.5862 | 0.0498
GEN-2017-195 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 17.9713 | 18.0258 | 0.0545
GEN-2017-195 | 03 CENTRAL | 543045 | SWITZER5 | 161 | 19.892 | 19.9418 | 0.0498
GEN-2017-195 | 03 CENTRAL | 543046 | OXFORD 5 | 161 | 21.3052 | 21.3643 | 0.0591
GEN-2017-195 | 03 CENTRAL | 543047 | OVERLPK5 | 161 | 32.8888 | 33.0037 | 0.1149
GEN-2017-195 | 03 CENTRAL | 543048 | COLLEGE5 | 161 | 30.7551 | 30.8867 | 0.1316
GEN-2017-195 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 31.1823 | 31.3159 | 0.1336
GEN-2017-195 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2135 | 23.2809 | 0.0674
GEN-2017-195 | 03 CENTRAL | 543052 | REEDER 5 | 161 | 21.4964 | 21.5472 | 0.0508
GEN-2017-195 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.098 | 25.1614 | 0.0634
GEN-2017-195 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.861 | 10.8838 | 0.0228
GEN-2017-195 | 03 CENTRAL | 543055 | SEOTTWA5 | 161 | 7.4669 | 7.4731 | 0.0062
GEN-2017-195 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.7408 | 16.7879 | 0.0471
GEN-2017-195 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 20.9962 | 21.0447 | 0.0485
GEN-2017-195 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3248 | 9.3343 | 0.0095
GEN-2017-195 | 03 CENTRAL | 543066 | S.OTTWA5 | 161 | 7.4355 | 7.4414 | 0.0059
GEN-2017-195 | 03 CENTRAL | 543067 | CENTENL5 | 161 | 10.8244 | 10.8329 | 0.0085
GEN-2017-195 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.4912 | 14.5118 | 0.0206
GEN-2017-195 | 03 CENTRAL | 543069 | PAOLA 5 | 161 | 10.9223 | 10.9303 | 0.008
GEN-2017-195 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.1932 | 10.2093 | 0.0161
GEN-2017-195 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.2794 | 29.442 | 0.1626
GEN-2017-195 | 03 CENTRAL | 543112 | OSAWAT 5 | 161 | 10.8298 | 10.8375 | 0.0077
GEN-2017-195 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8403 | 13.8632 | 0.0229
GEN-2017-195 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.2654 | 22.3562 | 0.0908
GEN-2017-195 | 03 CENTRAL | 543135 | OSAWTM_CAP5 | 161 | 10.1909 | 10.1978 | 0.0069
GEN-2017-195 | 03 CENTRAL | 543166 | NEASTOTTW5 | 161 | 6.4487 | 6.4533 | 0.0046
GEN-2017-195 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.703 | 26.8364 | 0.1334
GEN-2017-195 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.703 | 26.8364 | 0.1334
GEN-2017-195 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8153 | 2.8156 | 0.0003
GEN-2017-195 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6732 | 0.6733 | 0.0001
GEN-2017-195 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6448 | 0.6449 | 0.0001
GEN-2017-195 | 03 CENTRAL | 546651 | BARBER 5 | 161 | 30.721 | 30.7716 | 0.0506
GEN-2017-195 | 03 CENTRAL | 546655 | KAW W 5 | 161 | 24.2243 | 24.2569 | 0.0326
GEN-2017-195 | 03 CENTRAL | 546722 | MAYSOTH5 | 161 | 22.4288 | 22.4545 | 0.0257
GEN-2017-195 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.4541 | 27.5029 | 0.0488
GEN-2017-195 | 03 CENTRAL | 547469 | RIV4525 | 161 | 25.2912 | 25.2916 | 0.0004
GEN-2017-195 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.9312 | 23.9316 | 0.0004
GEN-2017-195 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.8336 | 24.834 | 0.0004
GEN-2017-195 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.1067 | 13.1075 | 0.0008
GEN-2017-195 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.8074 | 10.8102 | 0.0028
GEN-2017-195 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.1691 | 5.1692 | 0.0001
GEN-2017-195 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2922 | 7.2934 | 0.0012
GEN-2017-195 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.0595 | 13.0604 | 0.0009
GEN-2017-195 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 4.4329 | 4.4337 | 0.0008
GEN-2017-195 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 13.3711 | 13.3841 | 0.013
GEN-2017-195 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 8.2299 | 8.234 | 0.0041
GEN-2017-195 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 4.1236 | 4.1243 | 0.0007
GEN-2017-195 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.2862 | 8.2864 | 0.0002
GEN-2017-195 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.0777 | 29.0807 | 0.003
GEN-2017-195 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 21.3588 | 21.3626 | 0.0038
GEN-2017-195 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.9245 | 31.9281 | 0.0036
GEN-2017-195 | 03 CENTRAL | 760914 | GEN-2017-209 | 345 | 19.1504 | 19.209 | 0.0586
GEN-2017-195 | 03 CENTRAL | 760921 | G17-209-TAP | 345 | 19.6494 | 19.7113 | 0.0619
GEN-2017-195 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 7.3612 | 7.3625 | 0.0013
GEN-2017-195 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 12.1361 | 12.1404 | 0.0043
GEN-2017-195 | 03 CENTRAL | 761901 | GEN-2017-125 | 345 | 5.3261 | 5.3333 | 0.0072
GEN-2017-195 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.7823 | 28.5995 | 0.8172
GEN-2017-196 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 13.6738 | 13.6745 | 0.0007
GEN-2017-196 | 03 CENTRAL | 300124 | 5HOLDENB2 | 161 | 7.8004 | 7.8006 | 0.0002
GEN-2017-196 | 03 CENTRAL | 300692 | 2CLINTN | 69 | 13.8922 | 13.8925 | 0.0003
GEN-2017-196 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.046 | 16.0466 | 0.0006
GEN-2017-196 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.8162 | 24.8163 | 0.0001
GEN-2017-196 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.2335 | 13.2338 | 0.0003
GEN-2017-196 | 03 CENTRAL | 301477 | 5OSCEOKCTP | 161 | 6.6372 | 6.6373 | 0.0001
GEN-2017-196 | 03 CENTRAL | 301522 | 5OSCEOKC | 161 | 6.6299 | 6.63 | 0.0001
GEN-2017-196 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 16.455 | 16.4553 | 0.0003
GEN-2017-196 | 03 CENTRAL | 505502 | TRUMAN 5 | 161 | 7.5143 | 7.5144 | 0.0001
GEN-2017-196 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.5886 | 11.5886 | 0
GEN-2017-196 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.1823 | 12.1825 | 0.0002
GEN-2017-196 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.69 | 19.6901 | 0.0001
GEN-2017-196 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 16.5346 | 16.5377 | 0.0031
GEN-2017-196 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8387 | 24.8418 | 0.0031
GEN-2017-196 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.6001 | 10.6006 | 0.0005
GEN-2017-196 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6422 | 19.6479 | 0.0057
GEN-2017-196 | 03 CENTRAL | 532769 | LANG 7 | 345 | 19.3848 | 19.3903 | 0.0055
GEN-2017-196 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.664 | 13.6661 | 0.0021
GEN-2017-196 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6969 | 11.6973 | 0.0004
GEN-2017-196 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 28.4075 | 28.4251 | 0.0176
GEN-2017-196 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.7592 | 17.7815 | 0.0223
GEN-2017-196 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 22.5971 | 22.6421 | 0.045
GEN-2017-196 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.978 | 15.9817 | 0.0037
GEN-2017-196 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 12.0459 | 12.0464 | 0.0005
GEN-2017-196 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.1507 | 11.1511 | 0.0004
GEN-2017-196 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7989 | 9.7991 | 0.0002
GEN-2017-196 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.5242 | 9.5244 | 0.0002
GEN-2017-196 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 21.4784 | 21.4794 | 0.001
GEN-2017-196 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2776 | 7.2777 | 0.0001
GEN-2017-196 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0724 | 6.0724 | 0
GEN-2017-196 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0437 | 5.0437 | 0
GEN-2017-196 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.1372 | 7.1376 | 0.0004
GEN-2017-196 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.4074 | 19.4083 | 0.0009
GEN-2017-196 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9478 | 6.9479 | 0.0001
GEN-2017-196 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.309 | 18.3104 | 0.0014
GEN-2017-196 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.9723 | 18.9731 | 0.0008
GEN-2017-196 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.621 | 5.6211 | 0.0001
GEN-2017-196 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 25.0876 | 25.0892 | 0.0016
GEN-2017-196 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.7096 | 18.7116 | 0.002
GEN-2017-196 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.2193 | 14.2196 | 0.0003
GEN-2017-196 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5564 | 16.5586 | 0.0022
GEN-2017-196 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.4283 | 10.4286 | 0.0003
GEN-2017-196 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2511 | 9.2513 | 0.0002
GEN-2017-196 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7989 | 13.8005 | 0.0016
GEN-2017-196 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.5153 | 10.516 | 0.0007
GEN-2017-196 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.9186 | 13.9216 | 0.003
GEN-2017-196 | 03 CENTRAL | 532852 | JEC 6 | 230 | 25.985 | 25.9872 | 0.0022
GEN-2017-196 | 03 CENTRAL | 532853 | LAWHILL6 | 230 | 14.1279 | 14.1311 | 0.0032
GEN-2017-196 | 03 CENTRAL | 532854 | LEC U5 6 | 230 | 13.995 | 13.9981 | 0.0031
GEN-2017-196 | 03 CENTRAL | 532855 | MIDLAND6 | 230 | 12.5399 | 12.5424 | 0.0025
GEN-2017-196 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.544 | 22.5589 | 0.0149
GEN-2017-196 | 03 CENTRAL | 532857 | TECHILL6 | 230 | 11.195 | 11.1979 | 0.0029
GEN-2017-196 | 03 CENTRAL | 532861 | EMANHAT6 | 230 | 10.5856 | 10.5859 | 0.0003
GEN-2017-196 | 03 CENTRAL | 532862 | MCDOWEL6 | 230 | 7.3284 | 7.3287 | 0.0003
GEN-2017-196 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.5189 | 14.5206 | 0.0017
GEN-2017-196 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8402 | 13.8406 | 0.0004
GEN-2017-196 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.4775 | 8.4778 | 0.0003
GEN-2017-196 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 5.0451 | 5.0452 | 0.0001
GEN-2017-196 | 03 CENTRAL | 532912 | EDWRDVL5 | 161 | 22.3216 | 22.3296 | 0.008
GEN-2017-196 | 03 CENTRAL | 532914 | SPRGHL 5 | 161 | 11.1732 | 11.1769 | 0.0037
GEN-2017-196 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.7029 | 8.7031 | 0.0002
GEN-2017-196 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.8153 | 23.8161 | 0.0008
GEN-2017-196 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.5067 | 28.5075 | 0.0008
GEN-2017-196 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.4331 | 25.4339 | 0.0008
GEN-2017-196 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.4764 | 25.4772 | 0.0008
GEN-2017-196 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.3572 | 25.358 | 0.0008
GEN-2017-196 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.9272 | 31.9281 | 0.0009
GEN-2017-196 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.4764 | 31.4772 | 0.0008
GEN-2017-196 | 03 CENTRAL | 533151 | AUBURN 3 | 115 | 22.077 | 22.0804 | 0.0034
GEN-2017-196 | 03 CENTRAL | 533153 | COLINE 3 | 115 | 18.125 | 18.1272 | 0.0022
GEN-2017-196 | 03 CENTRAL | 533155 | CROOKED3 | 115 | 20.8798 | 20.8829 | 0.0031
GEN-2017-196 | 03 CENTRAL | 533163 | HOYT 3 | 115 | 23.5588 | 23.5613 | 0.0025
GEN-2017-196 | 03 CENTRAL | 533166 | INDIANH3 | 115 | 17.8685 | 17.8707 | 0.0022
GEN-2017-196 | 03 CENTRAL | 533167 | KEENE 3 | 115 | 10.058 | 10.0586 | 0.0006
GEN-2017-196 | 03 CENTRAL | 533176 | SHAWNEE3 | 115 | 13.3398 | 13.3412 | 0.0014
GEN-2017-196 | 03 CENTRAL | 533181 | TECHILW3 | 115 | 25.4704 | 25.4755 | 0.0051
GEN-2017-196 | 03 CENTRAL | 533182 | TECHILE3 | 115 | 25.5255 | 25.5307 | 0.0052
GEN-2017-196 | 03 CENTRAL | 533187 | 27CROCO3 | 115 | 18.6269 | 18.6295 | 0.0026
GEN-2017-196 | 03 CENTRAL | 533194 | SHERWOD3 | 115 | 20.1709 | 20.1737 | 0.0028
GEN-2017-196 | 03 CENTRAL | 533203 | TEC E 3 | 115 | 24.2762 | 24.2808 | 0.0046
GEN-2017-196 | 03 CENTRAL | 533211 | ARNOLD 3 | 115 | 8.4278 | 8.4283 | 0.0005
GEN-2017-196 | 03 CENTRAL | 533232 | BALDCRK3 | 115 | 14.5298 | 14.5315 | 0.0017
GEN-2017-196 | 03 CENTRAL | 533236 | FAIRGDS3 | 115 | 19.0206 | 19.0239 | 0.0033
GEN-2017-196 | 03 CENTRAL | 533240 | EUDORA 3 | 115 | 11.9352 | 11.9369 | 0.0017
GEN-2017-196 | 03 CENTRAL | 533244 | JARBALO3 | 115 | 27.4244 | 27.431 | 0.0066
GEN-2017-196 | 03 CENTRAL | 533248 | LEC U3 3 | 115 | 25.5214 | 25.5266 | 0.0052
GEN-2017-196 | 03 CENTRAL | 533249 | LEC U4 3 | 115 | 25.488 | 25.493 | 0.005
GEN-2017-196 | 03 CENTRAL | 533250 | LWRNCHL3 | 115 | 27.123 | 27.1289 | 0.0059
GEN-2017-196 | 03 CENTRAL | 533252 | MIDLADN3 | 115 | 26.0522 | 26.058 | 0.0058
GEN-2017-196 | 03 CENTRAL | 533253 | MOCKBRD3 | 115 | 17.9366 | 17.9393 | 0.0027
GEN-2017-196 | 03 CENTRAL | 533254 | MOONLIT3 | 115 | 11.3687 | 11.3713 | 0.0026
GEN-2017-196 | 03 CENTRAL | 533259 | NW LEAV3 | 115 | 17.6709 | 17.6733 | 0.0024
GEN-2017-196 | 03 CENTRAL | 533261 | PENTAGN3 | 115 | 22.6046 | 22.6124 | 0.0078
GEN-2017-196 | 03 CENTRAL | 533264 | 6TH ST 3 | 115 | 18.5895 | 18.5924 | 0.0029
GEN-2017-196 | 03 CENTRAL | 533265 | SOUTHTN3 | 115 | 11.426 | 11.4287 | 0.0027
GEN-2017-196 | 03 CENTRAL | 533267 | SPRINGH3 | 115 | 10.0782 | 10.0803 | 0.0021
GEN-2017-196 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 37.8407 | 37.8519 | 0.0112
GEN-2017-196 | 03 CENTRAL | 533269 | STULL 3 | 115 | 12.0652 | 12.0663 | 0.0011
GEN-2017-196 | 03 CENTRAL | 533270 | STULL T3 | 115 | 12.1882 | 12.1894 | 0.0012
GEN-2017-196 | 03 CENTRAL | 533272 | THORNTN3 | 115 | 16.5878 | 16.59 | 0.0022
GEN-2017-196 | 03 CENTRAL | 533273 | TIMBRLN3 | 115 | 13.6835 | 13.6873 | 0.0038
GEN-2017-196 | 03 CENTRAL | 533278 | WAVERLY3 | 115 | 14.8801 | 14.8846 | 0.0045
GEN-2017-196 | 03 CENTRAL | 533280 | WREN 3 | 115 | 18.9729 | 18.9759 | 0.003
GEN-2017-196 | 03 CENTRAL | 533281 | MNTCLLO3 | 115 | 23.7017 | 23.7119 | 0.0102
GEN-2017-196 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 27.9705 | 27.9864 | 0.0159
GEN-2017-196 | 03 CENTRAL | 533301 | EAST ST3 | 115 | 10.3277 | 10.3281 | 0.0004
GEN-2017-196 | 03 CENTRAL | 533304 | LANG 3 | 115 | 16.1365 | 16.1377 | 0.0012
GEN-2017-196 | 03 CENTRAL | 533305 | MORRIS 3 | 115 | 13.1537 | 13.1544 | 0.0007
GEN-2017-196 | 03 CENTRAL | 533306 | READING3 | 115 | 7.3479 | 7.3482 | 0.0003
GEN-2017-196 | 03 CENTRAL | 533307 | PRAIRIE3 | 115 | 10.4648 | 10.4653 | 0.0005
GEN-2017-196 | 03 CENTRAL | 533309 | WEMPORI3 | 115 | 11.4423 | 11.4428 | 0.0005
GEN-2017-196 | 03 CENTRAL | 533335 | MCDOWEL3 | 115 | 19.4088 | 19.4097 | 0.0009
GEN-2017-196 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.9008 | 3.9008 | 0
GEN-2017-196 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.475 | 3.475 | 0
GEN-2017-196 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5483 | 3.5484 | 0.0001
GEN-2017-196 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1633 | 3.1633 | 0
GEN-2017-196 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1575 | 5.1575 | 0
GEN-2017-196 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5469 | 3.5469 | 0
GEN-2017-196 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8219 | 4.8219 | 0
GEN-2017-196 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2348 | 6.2348 | 0
GEN-2017-196 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.046 | 24.0463 | 0.0003
GEN-2017-196 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.9306 | 20.9599 | 0.0293
GEN-2017-196 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.1113 | 19.1273 | 0.016
GEN-2017-196 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.9932 | 22.0014 | 0.0082
GEN-2017-196 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.5358 | 27.5409 | 0.0051
GEN-2017-196 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 16.7134 | 16.7169 | 0.0035
GEN-2017-196 | 03 CENTRAL | 541210 | MARTCTY5 | 161 | 28.3327 | 28.3481 | 0.0154
GEN-2017-196 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 7.6606 | 7.6608 | 0.0002
GEN-2017-196 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 34.9411 | 34.9521 | 0.011
GEN-2017-196 | 03 CENTRAL | 541239 | HSNVL 5 | 161 | 15.7389 | 15.7418 | 0.0029
GEN-2017-196 | 03 CENTRAL | 541240 | ADRIAN 5 | 161 | 8.5243 | 8.525 | 0.0007
GEN-2017-196 | 03 CENTRAL | 541242 | CLINTON5 | 161 | 13.6217 | 13.6224 | 0.0007
GEN-2017-196 | 03 CENTRAL | 541243 | LKWINBG5 | 161 | 25.6237 | 25.6303 | 0.0066
GEN-2017-196 | 03 CENTRAL | 541259 | TURNER_RD5 | 161 | 18.5289 | 18.5361 | 0.0072
GEN-2017-196 | 03 CENTRAL | 541280 | PHILL 2 | 69 | 10.3996 | 10.4001 | 0.0005
GEN-2017-196 | 03 CENTRAL | 541290 | BELTONS2 | 69 | 10.1333 | 10.134 | 0.0007
GEN-2017-196 | 03 CENTRAL | 541291 | FREEMAN2 | 69 | 4.5312 | 4.5314 | 0.0002
GEN-2017-196 | 03 CENTRAL | 541313 | HARRIS | 161 | 26.7898 | 26.7958 | 0.006
GEN-2017-196 | 03 CENTRAL | 541340 | BELTONS5 | 161 | 19.6693 | 19.6777 | 0.0084
GEN-2017-196 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 21.1744 | 21.184 | 0.0096
GEN-2017-196 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 23.2927 | 23.3053 | 0.0126
GEN-2017-196 | 03 CENTRAL | 541343 | S.HARP 2 | 69 | 4.5824 | 4.5826 | 0.0002
GEN-2017-196 | 03 CENTRAL | 541344 | PECULRS5 | 161 | 21.7783 | 21.789 | 0.0107
GEN-2017-196 | 03 CENTRAL | 541350 | IATAN5 | 161 | 15.5298 | 15.5313 | 0.0015
GEN-2017-196 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 19.1723 | 19.1752 | 0.0029
GEN-2017-196 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.5528 | 19.5592 | 0.0064
GEN-2017-196 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 9.3306 | 9.3311 | 0.0005
GEN-2017-196 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 8.1752 | 8.1756 | 0.0004
GEN-2017-196 | 03 CENTRAL | 541540 | FREEMAN_SP2 | 69 | 4.2238 | 4.2239 | 0.0001
GEN-2017-196 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2017-196 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 35.4492 | 35.493 | 0.0438
GEN-2017-196 | 03 CENTRAL | 542947 | MERRIAM_CAP5 | 161 | 27.4828 | 27.4995 | 0.0167
GEN-2017-196 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 30.8235 | 30.8392 | 0.0157
GEN-2017-196 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.4713 | 28.678 | 0.2067
GEN-2017-196 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.3298 | 30.3737 | 0.0439
GEN-2017-196 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.9498 | 26.0141 | 0.0643
GEN-2017-196 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.9429 | 40.9926 | 0.0497
GEN-2017-196 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.7229 | 23.7308 | 0.0079
GEN-2017-196 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.3962 | 24.4621 | 0.0659
GEN-2017-196 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 44.5973 | 44.6667 | 0.0694
GEN-2017-196 | 03 CENTRAL | 542979 | PFLUMM 5 | 161 | 30.2833 | 30.3109 | 0.0276
GEN-2017-196 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.2338 | 23.2402 | 0.0064
GEN-2017-196 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5249 | 27.5599 | 0.035
GEN-2017-196 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 31.5442 | 31.5568 | 0.0126
GEN-2017-196 | 03 CENTRAL | 542992 | BENDIX 5 | 161 | 30.3873 | 30.4037 | 0.0164
GEN-2017-196 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 37.5177 | 37.5409 | 0.0232
GEN-2017-196 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 20.0623 | 20.0703 | 0.008
GEN-2017-196 | 03 CENTRAL | 543001 | FOREST 5 | 161 | 32.1365 | 32.1522 | 0.0157
GEN-2017-196 | 03 CENTRAL | 543002 | MARTCIT5 | 161 | 25.3116 | 25.325 | 0.0134
GEN-2017-196 | 03 CENTRAL | 543007 | SWOPE S5 | 161 | 22.2608 | 22.2668 | 0.006
GEN-2017-196 | 03 CENTRAL | 543008 | BUNKRDG5 | 161 | 24.539 | 24.5473 | 0.0083
GEN-2017-196 | 03 CENTRAL | 543010 | WINJT S5 | 161 | 23.8432 | 23.8501 | 0.0069
GEN-2017-196 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 37.2073 | 37.2389 | 0.0316
GEN-2017-196 | 03 CENTRAL | 543032 | MERRIAM5 | 161 | 32.6824 | 32.7059 | 0.0235
GEN-2017-196 | 03 CENTRAL | 543033 | BRKRIDG5 | 161 | 24.648 | 24.6645 | 0.0165
GEN-2017-196 | 03 CENTRAL | 543034 | KNLWRTH5 | 161 | 27.6139 | 27.6326 | 0.0187
GEN-2017-196 | 03 CENTRAL | 543036 | OLATHE 5 | 161 | 27.557 | 27.5824 | 0.0254
GEN-2017-196 | 03 CENTRAL | 543037 | QUARRY 5 | 161 | 16.285 | 16.2953 | 0.0103
GEN-2017-196 | 03 CENTRAL | 543038 | LENEXA 5 | 161 | 37.8838 | 37.9286 | 0.0448
GEN-2017-196 | 03 CENTRAL | 543040 | ROEPARK5 | 161 | 30.7947 | 30.8103 | 0.0156
GEN-2017-196 | 03 CENTRAL | 543041 | SHAWNEE5 | 161 | 27.9725 | 27.9878 | 0.0153
GEN-2017-196 | 03 CENTRAL | 543043 | MURLEN 5 | 161 | 18.5738 | 18.5862 | 0.0124
GEN-2017-196 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 18.0123 | 18.0258 | 0.0135
GEN-2017-196 | 03 CENTRAL | 543045 | SWITZER5 | 161 | 19.9294 | 19.9418 | 0.0124
GEN-2017-196 | 03 CENTRAL | 543046 | OXFORD 5 | 161 | 21.3496 | 21.3643 | 0.0147
GEN-2017-196 | 03 CENTRAL | 543047 | OVERLPK5 | 161 | 32.9752 | 33.0037 | 0.0285
GEN-2017-196 | 03 CENTRAL | 543048 | COLLEGE5 | 161 | 30.854 | 30.8867 | 0.0327
GEN-2017-196 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 31.2828 | 31.3159 | 0.0331
GEN-2017-196 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2642 | 23.2809 | 0.0167
GEN-2017-196 | 03 CENTRAL | 543052 | REEDER 5 | 161 | 21.5346 | 21.5472 | 0.0126
GEN-2017-196 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.1457 | 25.1614 | 0.0157
GEN-2017-196 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8782 | 10.8838 | 0.0056
GEN-2017-196 | 03 CENTRAL | 543055 | SEOTTWA5 | 161 | 7.4716 | 7.4731 | 0.0015
GEN-2017-196 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.7762 | 16.7879 | 0.0117
GEN-2017-196 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 21.0327 | 21.0447 | 0.012
GEN-2017-196 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.332 | 9.3343 | 0.0023
GEN-2017-196 | 03 CENTRAL | 543066 | S.OTTWA5 | 161 | 7.4399 | 7.4414 | 0.0015
GEN-2017-196 | 03 CENTRAL | 543067 | CENTENL5 | 161 | 10.8308 | 10.8329 | 0.0021
GEN-2017-196 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.5067 | 14.5118 | 0.0051
GEN-2017-196 | 03 CENTRAL | 543069 | PAOLA 5 | 161 | 10.9283 | 10.9303 | 0.002
GEN-2017-196 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.2053 | 10.2093 | 0.004
GEN-2017-196 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.4016 | 29.442 | 0.0404
GEN-2017-196 | 03 CENTRAL | 543112 | OSAWAT 5 | 161 | 10.8356 | 10.8375 | 0.0019
GEN-2017-196 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8575 | 13.8632 | 0.0057
GEN-2017-196 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.3337 | 22.3562 | 0.0225
GEN-2017-196 | 03 CENTRAL | 543135 | OSAWTM_CAP5 | 161 | 10.1961 | 10.1978 | 0.0017
GEN-2017-196 | 03 CENTRAL | 543166 | NEASTOTTW5 | 161 | 6.4522 | 6.4533 | 0.0011
GEN-2017-196 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8033 | 26.8364 | 0.0331
GEN-2017-196 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8033 | 26.8364 | 0.0331
GEN-2017-196 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8155 | 2.8156 | 0.0001
GEN-2017-196 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2017-196 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2017-196 | 03 CENTRAL | 546651 | BARBER 5 | 161 | 30.7591 | 30.7716 | 0.0125
GEN-2017-196 | 03 CENTRAL | 546655 | KAW W 5 | 161 | 24.2488 | 24.2569 | 0.0081
GEN-2017-196 | 03 CENTRAL | 546722 | MAYSOTH5 | 161 | 22.4481 | 22.4545 | 0.0064
GEN-2017-196 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.4908 | 27.5029 | 0.0121
GEN-2017-196 | 03 CENTRAL | 547469 | RIV4525 | 161 | 25.2915 | 25.2916 | 0.0001
GEN-2017-196 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.9315 | 23.9316 | 0.0001
GEN-2017-196 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.8339 | 24.834 | 0.0001
GEN-2017-196 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.1073 | 13.1075 | 0.0002
GEN-2017-196 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.8095 | 10.8102 | 0.0007
GEN-2017-196 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.1692 | 5.1692 | 0
GEN-2017-196 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2931 | 7.2934 | 0.0003
GEN-2017-196 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.0602 | 13.0604 | 0.0002
GEN-2017-196 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 4.4335 | 4.4337 | 0.0002
GEN-2017-196 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 13.3809 | 13.3841 | 0.0032
GEN-2017-196 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 8.233 | 8.234 | 0.001
GEN-2017-196 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 4.1241 | 4.1243 | 0.0002
GEN-2017-196 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.2864 | 8.2864 | 0
GEN-2017-196 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.08 | 29.0807 | 0.0007
GEN-2017-196 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 21.3617 | 21.3626 | 0.0009
GEN-2017-196 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.9272 | 31.9281 | 0.0009
GEN-2017-196 | 03 CENTRAL | 760914 | GEN-2017-209 | 345 | 19.1944 | 19.209 | 0.0146
GEN-2017-196 | 03 CENTRAL | 760921 | G17-209-TAP | 345 | 19.6959 | 19.7113 | 0.0154
GEN-2017-196 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 7.3622 | 7.3625 | 0.0003
GEN-2017-196 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 12.1393 | 12.1404 | 0.0011
GEN-2017-196 | 03 CENTRAL | 761901 | GEN-2017-125 | 345 | 5.3315 | 5.3333 | 0.0018
GEN-2017-196 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.3928 | 28.5995 | 0.2067
GEN-2017-220 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0454 | 16.0466 | 0.0012
GEN-2017-220 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.816 | 24.8163 | 0.0003
GEN-2017-220 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.2333 | 13.2338 | 0.0005
GEN-2017-220 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 10.7575 | 10.7581 | 0.0006
GEN-2017-220 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 17.6805 | 17.6864 | 0.0059
GEN-2017-220 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.6759 | 13.6766 | 0.0007
GEN-2017-220 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1963 | 5.1964 | 0.0001
GEN-2017-220 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 9.2068 | 9.2074 | 0.0006
GEN-2017-220 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.4576 | 10.4597 | 0.0021
GEN-2017-220 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.7004 | 7.7007 | 0.0003
GEN-2017-220 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.0955 | 12.1006 | 0.0051
GEN-2017-220 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.2678 | 3.2678 | 0
GEN-2017-220 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 20.2681 | 20.2775 | 0.0094
GEN-2017-220 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 25.0031 | 25.0074 | 0.0043
GEN-2017-220 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.2436 | 9.2441 | 0.0005
GEN-2017-220 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.9035 | 9.9041 | 0.0006
GEN-2017-220 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 17.8571 | 17.8606 | 0.0035
GEN-2017-220 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 18.2224 | 18.2244 | 0.002
GEN-2017-220 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 12.4831 | 12.4847 | 0.0016
GEN-2017-220 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 7.7523 | 7.7526 | 0.0003
GEN-2017-220 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.5632 | 12.5699 | 0.0067
GEN-2017-220 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.5451 | 12.5518 | 0.0067
GEN-2017-220 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 31.9787 | 31.9832 | 0.0045
GEN-2017-220 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.4369 | 12.4487 | 0.0118
GEN-2017-220 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.4303 | 14.4353 | 0.005
GEN-2017-220 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.6337 | 6.6347 | 0.001
GEN-2017-220 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.4561 | 11.4591 | 0.003
GEN-2017-220 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.7629 | 8.7637 | 0.0008
GEN-2017-220 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 14.1229 | 14.1251 | 0.0022
GEN-2017-220 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 12.3671 | 12.3706 | 0.0035
GEN-2017-220 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.1258 | 12.131 | 0.0052
GEN-2017-220 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.0133 | 11.0224 | 0.0091
GEN-2017-220 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 12.1275 | 12.1289 | 0.0014
GEN-2017-220 | 03 CENTRAL | 515686 | GEN-2011-014 | 345 | 10.9707 | 10.9718 | 0.0011
GEN-2017-220 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 20.7635 | 20.7645 | 0.001
GEN-2017-220 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 7.1309 | 7.1309 | 0
GEN-2017-220 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.9479 | 8.9498 | 0.0019
GEN-2017-220 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.1087 | 15.1275 | 0.0188
GEN-2017-220 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 16.8533 | 16.859 | 0.0057
GEN-2017-220 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.7858 | 10.7885 | 0.0027
GEN-2017-220 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.3932 | 12.3967 | 0.0035
GEN-2017-220 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 5.9054 | 5.906 | 0.0006
GEN-2017-220 | 03 CENTRAL | 516106 | BOBCAT 7 | 345 | 15.4224 | 15.4264 | 0.004
GEN-2017-220 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 11.1319 | 11.1338 | 0.0019
GEN-2017-220 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 11.1209 | 11.1228 | 0.0019
GEN-2017-220 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.7744 | 10.7771 | 0.0027
GEN-2017-220 | 03 CENTRAL | 520425 | PIC4 | 138 | 8.3651 | 8.3652 | 0.0001
GEN-2017-220 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.5275 | 10.5296 | 0.0021
GEN-2017-220 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 12.4274 | 12.4304 | 0.003
GEN-2017-220 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 20.4723 | 20.4732 | 0.0009
GEN-2017-220 | 03 CENTRAL | 520553 | SEILING4 | 138 | 7.0554 | 7.0555 | 0.0001
GEN-2017-220 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 7.0287 | 7.0297 | 0.001
GEN-2017-220 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 8.2511 | 8.2513 | 0.0002
GEN-2017-220 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.9738 | 8.9739 | 0.0001
GEN-2017-220 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 21.2256 | 21.2265 | 0.0009
GEN-2017-220 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.6045 | 7.6058 | 0.0013
GEN-2017-220 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.2254 | 5.2261 | 0.0007
GEN-2017-220 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.2775 | 8.2787 | 0.0012
GEN-2017-220 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 12.0776 | 12.0792 | 0.0016
GEN-2017-220 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 9.0635 | 9.0643 | 0.0008
GEN-2017-220 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 10.5227 | 10.5237 | 0.001
GEN-2017-220 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.4107 | 13.4172 | 0.0065
GEN-2017-220 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.8682 | 9.87 | 0.0018
GEN-2017-220 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.7672 | 7.7683 | 0.0011
GEN-2017-220 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 8.064 | 8.0652 | 0.0012
GEN-2017-220 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8373 | 24.8418 | 0.0045
GEN-2017-220 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.5977 | 10.6006 | 0.0029
GEN-2017-220 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6248 | 19.6479 | 0.0231
GEN-2017-220 | 03 CENTRAL | 532769 | LANG 7 | 345 | 19.3679 | 19.3903 | 0.0224
GEN-2017-220 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.6597 | 13.6661 | 0.0064
GEN-2017-220 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6719 | 11.6973 | 0.0254
GEN-2017-220 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.6206 | 11.6284 | 0.0078
GEN-2017-220 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.7762 | 17.7815 | 0.0053
GEN-2017-220 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.9666 | 15.9817 | 0.0151
GEN-2017-220 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7933 | 9.7991 | 0.0058
GEN-2017-220 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.5189 | 9.5244 | 0.0055
GEN-2017-220 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 21.1498 | 21.4794 | 0.3296
GEN-2017-220 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2493 | 7.2777 | 0.0284
GEN-2017-220 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.054 | 6.0724 | 0.0184
GEN-2017-220 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0315 | 5.0437 | 0.0122
GEN-2017-220 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.1251 | 7.1376 | 0.0125
GEN-2017-220 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.3313 | 19.4083 | 0.077
GEN-2017-220 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9411 | 6.9479 | 0.0068
GEN-2017-220 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.308 | 18.3104 | 0.0024
GEN-2017-220 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.9301 | 18.9731 | 0.043
GEN-2017-220 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6169 | 5.6211 | 0.0042
GEN-2017-220 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 24.8169 | 25.0892 | 0.2723
GEN-2017-220 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.704 | 18.7116 | 0.0076
GEN-2017-220 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1828 | 14.2196 | 0.0368
GEN-2017-220 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5534 | 16.5586 | 0.0052
GEN-2017-220 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.4209 | 10.4286 | 0.0077
GEN-2017-220 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2453 | 9.2513 | 0.006
GEN-2017-220 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7969 | 13.8005 | 0.0036
GEN-2017-220 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.489 | 10.516 | 0.027
GEN-2017-220 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.5544 | 22.5589 | 0.0045
GEN-2017-220 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.5164 | 14.5206 | 0.0042
GEN-2017-220 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0452 | 9.0493 | 0.0041
GEN-2017-220 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8347 | 13.8406 | 0.0059
GEN-2017-220 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.6037 | 10.6084 | 0.0047
GEN-2017-220 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.0035 | 12.01 | 0.0065
GEN-2017-220 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.0174 | 6.019 | 0.0016
GEN-2017-220 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.4444 | 28.5075 | 0.0631
GEN-2017-220 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2468 | 11.2543 | 0.0075
GEN-2017-220 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.3083 | 19.3365 | 0.0282
GEN-2017-220 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2997 | 11.3076 | 0.0079
GEN-2017-220 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.4931 | 22.5244 | 0.0313
GEN-2017-220 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4689 | 6.4708 | 0.0019
GEN-2017-220 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.5314 | 8.5384 | 0.007
GEN-2017-220 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1228 | 7.127 | 0.0042
GEN-2017-220 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.9988 | 11.0113 | 0.0125
GEN-2017-220 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3607 | 8.3679 | 0.0072
GEN-2017-220 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.9519 | 19.982 | 0.0301
GEN-2017-220 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.7293 | 21.7704 | 0.0411
GEN-2017-220 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5565 | 14.5731 | 0.0166
GEN-2017-220 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 19.0139 | 19.041 | 0.0271
GEN-2017-220 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.6132 | 17.6456 | 0.0324
GEN-2017-220 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.1507 | 25.1902 | 0.0395
GEN-2017-220 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.8103 | 31.9281 | 0.1178
GEN-2017-220 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.7373 | 31.8544 | 0.1171
GEN-2017-220 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 22.2111 | 22.251 | 0.0399
GEN-2017-220 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 22.2084 | 22.2483 | 0.0399
GEN-2017-220 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.2055 | 22.2454 | 0.0399
GEN-2017-220 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.3836 | 17.4119 | 0.0283
GEN-2017-220 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.5713 | 20.6073 | 0.036
GEN-2017-220 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.4325 | 17.4636 | 0.0311
GEN-2017-220 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.0867 | 21.1331 | 0.0464
GEN-2017-220 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.8823 | 20.9143 | 0.032
GEN-2017-220 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.4223 | 31.4772 | 0.0549
GEN-2017-220 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.8879 | 11.8943 | 0.0064
GEN-2017-220 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.9335 | 17.9597 | 0.0262
GEN-2017-220 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.5651 | 19.6083 | 0.0432
GEN-2017-220 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.8324 | 19.8579 | 0.0255
GEN-2017-220 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.7048 | 23.768 | 0.0632
GEN-2017-220 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 25.1865 | 25.2326 | 0.0461
GEN-2017-220 | 03 CENTRAL | 533304 | LANG 3 | 115 | 16.133 | 16.1377 | 0.0047
GEN-2017-220 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.6616 | 2.6619 | 0.0003
GEN-2017-220 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9749 | 3.9757 | 0.0008
GEN-2017-220 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.307 | 7.308 | 0.001
GEN-2017-220 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.996 | 9.9998 | 0.0038
GEN-2017-220 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.1902 | 10.1941 | 0.0039
GEN-2017-220 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 19.3761 | 19.3909 | 0.0148
GEN-2017-220 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.2605 | 8.2634 | 0.0029
GEN-2017-220 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.4483 | 8.4514 | 0.0031
GEN-2017-220 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.3411 | 23.3667 | 0.0256
GEN-2017-220 | 03 CENTRAL | 533419 | HEC 3 | 115 | 18.1113 | 18.1243 | 0.013
GEN-2017-220 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.8355 | 18.8496 | 0.0141
GEN-2017-220 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.7362 | 8.738 | 0.0018
GEN-2017-220 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 11.0622 | 11.0651 | 0.0029
GEN-2017-220 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.8037 | 8.8082 | 0.0045
GEN-2017-220 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7921 | 6.7948 | 0.0027
GEN-2017-220 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.4543 | 11.4575 | 0.0032
GEN-2017-220 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 7.0544 | 7.0556 | 0.0012
GEN-2017-220 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0468 | 4.0472 | 0.0004
GEN-2017-220 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.5297 | 7.5312 | 0.0015
GEN-2017-220 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3763 | 6.3773 | 0.001
GEN-2017-220 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1801 | 6.1811 | 0.001
GEN-2017-220 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5577 | 6.5588 | 0.0011
GEN-2017-220 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.6107 | 14.6173 | 0.0066
GEN-2017-220 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5483 | 3.5484 | 0.0001
GEN-2017-220 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1632 | 3.1633 | 0.0001
GEN-2017-220 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1574 | 5.1575 | 0.0001
GEN-2017-220 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5469 | 3.5469 | 0
GEN-2017-220 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8218 | 4.8219 | 0.0001
GEN-2017-220 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2347 | 6.2348 | 0.0001
GEN-2017-220 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 20.4097 | 20.4269 | 0.0172
GEN-2017-220 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1339 | 4.1352 | 0.0013
GEN-2017-220 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.248 | 5.25 | 0.002
GEN-2017-220 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8293 | 5.8317 | 0.0024
GEN-2017-220 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.2217 | 12.2326 | 0.0109
GEN-2017-220 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.7238 | 11.7337 | 0.0099
GEN-2017-220 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.3133 | 12.3166 | 0.0033
GEN-2017-220 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.5295 | 3.5296 | 0.0001
GEN-2017-220 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.8041 | 10.8122 | 0.0081
GEN-2017-220 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.1189 | 16.1376 | 0.0187
GEN-2017-220 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.4359 | 2.4359 | 0
GEN-2017-220 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5391 | 7.5432 | 0.0041
GEN-2017-220 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5737 | 8.5782 | 0.0045
GEN-2017-220 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.3527 | 10.3604 | 0.0077
GEN-2017-220 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.8532 | 10.8618 | 0.0086
GEN-2017-220 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.5438 | 8.5453 | 0.0015
GEN-2017-220 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.6891 | 6.6895 | 0.0004
GEN-2017-220 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.0701 | 10.0711 | 0.001
GEN-2017-220 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.6062 | 12.6096 | 0.0034
GEN-2017-220 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3152 | 4.3154 | 0.0002
GEN-2017-220 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.0498 | 13.0517 | 0.0019
GEN-2017-220 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.4762 | 8.4795 | 0.0033
GEN-2017-220 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.4204 | 9.4212 | 0.0008
GEN-2017-220 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.4359 | 2.4359 | 0
GEN-2017-220 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.4359 | 2.4359 | 0
GEN-2017-220 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.1828 | 13.1933 | 0.0105
GEN-2017-220 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.791 | 16.851 | 0.06
GEN-2017-220 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 12.9019 | 12.9081 | 0.0062
GEN-2017-220 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.1442 | 18.1688 | 0.0246
GEN-2017-220 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0478 | 11.0552 | 0.0074
GEN-2017-220 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.6425 | 11.6475 | 0.005
GEN-2017-220 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.2479 | 11.255 | 0.0071
GEN-2017-220 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.2479 | 11.255 | 0.0071
GEN-2017-220 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.5365 | 9.5415 | 0.005
GEN-2017-220 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.7824 | 8.7867 | 0.0043
GEN-2017-220 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.264 | 3.264 | 0
GEN-2017-220 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2017-220 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.6752 | 28.678 | 0.0028
GEN-2017-220 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5575 | 27.5599 | 0.0024
GEN-2017-220 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8342 | 26.8364 | 0.0022
GEN-2017-220 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8342 | 26.8364 | 0.0022
GEN-2017-220 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8156 | 2.8156 | 0
GEN-2017-220 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2017-220 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2017-220 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.0964 | 13.1075 | 0.0111
GEN-2017-220 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.5726 | 11.5792 | 0.0066
GEN-2017-220 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.7562 | 6.7564 | 0.0002
GEN-2017-220 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.783 | 10.8102 | 0.0272
GEN-2017-220 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.1657 | 5.1692 | 0.0035
GEN-2017-220 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.4884 | 12.4942 | 0.0058
GEN-2017-220 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2815 | 7.2934 | 0.0119
GEN-2017-220 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.0493 | 13.0604 | 0.0111
GEN-2017-220 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.5014 | 6.5018 | 0.0004
GEN-2017-220 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.666 | 16.6716 | 0.0056
GEN-2017-220 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 8.9661 | 8.9679 | 0.0018
GEN-2017-220 | 03 CENTRAL | 585420 | COWBOY_RIDGE | 345 | 6.8933 | 6.8943 | 0.001
GEN-2017-220 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 10.888 | 10.8907 | 0.0027
GEN-2017-220 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.9918 | 9.994 | 0.0022
GEN-2017-220 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.2269 | 7.227 | 0.0001
GEN-2017-220 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.175 | 10.18 | 0.005
GEN-2017-220 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.3357 | 15.339 | 0.0033
GEN-2017-220 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.6188 | 5.619 | 0.0002
GEN-2017-220 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8438 | 6.8493 | 0.0055
GEN-2017-220 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.3123 | 10.3256 | 0.0133
GEN-2017-220 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 5.5325 | 5.533 | 0.0005
GEN-2017-220 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.276 | 8.2864 | 0.0104
GEN-2017-220 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.5731 | 8.577 | 0.0039
GEN-2017-220 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.9629 | 9.9682 | 0.0053
GEN-2017-220 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 12.4978 | 12.5005 | 0.0027
GEN-2017-220 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.791 | 16.851 | 0.06
GEN-2017-220 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 28.9832 | 29.0807 | 0.0975
GEN-2017-220 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 10.74 | 10.7406 | 0.0006
GEN-2017-220 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 21.0331 | 21.3626 | 0.3295
GEN-2017-220 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.8103 | 31.9281 | 0.1178
GEN-2017-220 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.015 | 9.0211 | 0.0061
GEN-2017-220 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.1193 | 9.1228 | 0.0035
GEN-2017-220 | 03 CENTRAL | 761901 | GEN-2017-125 | 345 | 5.3329 | 5.3333 | 0.0004
GEN-2017-220 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.5967 | 28.5995 | 0.0028
GEN-2017-220 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 10.9376 | 10.9398 | 0.0022
GEN-2017-220 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.7807 | 7.7818 | 0.0011
GEN-2017-220 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4764 | 5.4765 | 0.0001
GEN-2017-220 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.1002 | 4.1003 | 0.0001
GEN-2017-220 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.8108 | 3.8109 | 0.0001
GEN-2017-220 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.7623 | 4.7624 | 0.0001
GEN-2017-221 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0457 | 16.0466 | 0.0009
GEN-2017-221 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.8161 | 24.8163 | 0.0002
GEN-2017-221 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.2334 | 13.2338 | 0.0004
GEN-2017-221 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 10.7577 | 10.7581 | 0.0004
GEN-2017-221 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 17.682 | 17.6864 | 0.0044
GEN-2017-221 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.6761 | 13.6766 | 0.0005
GEN-2017-221 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1963 | 5.1964 | 0.0001
GEN-2017-221 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 9.2069 | 9.2074 | 0.0005
GEN-2017-221 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.4581 | 10.4597 | 0.0016
GEN-2017-221 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.7005 | 7.7007 | 0.0002
GEN-2017-221 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.0968 | 12.1006 | 0.0038
GEN-2017-221 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.2678 | 3.2678 | 0
GEN-2017-221 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 20.2705 | 20.2775 | 0.007
GEN-2017-221 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 25.0042 | 25.0074 | 0.0032
GEN-2017-221 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.2437 | 9.2441 | 0.0004
GEN-2017-221 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.9036 | 9.9041 | 0.0005
GEN-2017-221 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 17.858 | 17.8606 | 0.0026
GEN-2017-221 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 18.2229 | 18.2244 | 0.0015
GEN-2017-221 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 12.4835 | 12.4847 | 0.0012
GEN-2017-221 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 7.7524 | 7.7526 | 0.0002
GEN-2017-221 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.5649 | 12.5699 | 0.005
GEN-2017-221 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.5468 | 12.5518 | 0.005
GEN-2017-221 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 31.9798 | 31.9832 | 0.0034
GEN-2017-221 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.4399 | 12.4487 | 0.0088
GEN-2017-221 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.4316 | 14.4353 | 0.0037
GEN-2017-221 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.634 | 6.6347 | 0.0007
GEN-2017-221 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.4569 | 11.4591 | 0.0022
GEN-2017-221 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.7631 | 8.7637 | 0.0006
GEN-2017-221 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 14.1235 | 14.1251 | 0.0016
GEN-2017-221 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 12.368 | 12.3706 | 0.0026
GEN-2017-221 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.1272 | 12.131 | 0.0038
GEN-2017-221 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.0156 | 11.0224 | 0.0068
GEN-2017-221 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 12.1279 | 12.1289 | 0.001
GEN-2017-221 | 03 CENTRAL | 515686 | GEN-2011-014 | 345 | 10.971 | 10.9718 | 0.0008
GEN-2017-221 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 20.7638 | 20.7645 | 0.0007
GEN-2017-221 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 7.1309 | 7.1309 | 0
GEN-2017-221 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.9484 | 8.9498 | 0.0014
GEN-2017-221 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.1135 | 15.1275 | 0.014
GEN-2017-221 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 16.8548 | 16.859 | 0.0042
GEN-2017-221 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.7865 | 10.7885 | 0.002
GEN-2017-221 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.394 | 12.3967 | 0.0027
GEN-2017-221 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 5.9055 | 5.906 | 0.0005
GEN-2017-221 | 03 CENTRAL | 516106 | BOBCAT 7 | 345 | 15.4234 | 15.4264 | 0.003
GEN-2017-221 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 11.1324 | 11.1338 | 0.0014
GEN-2017-221 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 11.1214 | 11.1228 | 0.0014
GEN-2017-221 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.7751 | 10.7771 | 0.002
GEN-2017-221 | 03 CENTRAL | 520425 | PIC4 | 138 | 8.3651 | 8.3652 | 0.0001
GEN-2017-221 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.528 | 10.5296 | 0.0016
GEN-2017-221 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 12.4281 | 12.4304 | 0.0023
GEN-2017-221 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 20.4725 | 20.4732 | 0.0007
GEN-2017-221 | 03 CENTRAL | 520553 | SEILING4 | 138 | 7.0554 | 7.0555 | 0.0001
GEN-2017-221 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 7.0289 | 7.0297 | 0.0008
GEN-2017-221 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 8.2512 | 8.2513 | 0.0001
GEN-2017-221 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.9738 | 8.9739 | 0.0001
GEN-2017-221 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 21.2258 | 21.2265 | 0.0007
GEN-2017-221 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.6048 | 7.6058 | 0.001
GEN-2017-221 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.2256 | 5.2261 | 0.0005
GEN-2017-221 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.2778 | 8.2787 | 0.0009
GEN-2017-221 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 12.078 | 12.0792 | 0.0012
GEN-2017-221 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 9.0637 | 9.0643 | 0.0006
GEN-2017-221 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 10.523 | 10.5237 | 0.0007
GEN-2017-221 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.4123 | 13.4172 | 0.0049
GEN-2017-221 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.8686 | 9.87 | 0.0014
GEN-2017-221 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.7675 | 7.7683 | 0.0008
GEN-2017-221 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 8.0643 | 8.0652 | 0.0009
GEN-2017-221 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8385 | 24.8418 | 0.0033
GEN-2017-221 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.5984 | 10.6006 | 0.0022
GEN-2017-221 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6307 | 19.6479 | 0.0172
GEN-2017-221 | 03 CENTRAL | 532769 | LANG 7 | 345 | 19.3736 | 19.3903 | 0.0167
GEN-2017-221 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.6614 | 13.6661 | 0.0047
GEN-2017-221 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6783 | 11.6973 | 0.019
GEN-2017-221 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.6225 | 11.6284 | 0.0059
GEN-2017-221 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.7776 | 17.7815 | 0.0039
GEN-2017-221 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.9704 | 15.9817 | 0.0113
GEN-2017-221 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7948 | 9.7991 | 0.0043
GEN-2017-221 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.5203 | 9.5244 | 0.0041
GEN-2017-221 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 21.2326 | 21.4794 | 0.2468
GEN-2017-221 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2565 | 7.2777 | 0.0212
GEN-2017-221 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0587 | 6.0724 | 0.0137
GEN-2017-221 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0346 | 5.0437 | 0.0091
GEN-2017-221 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.1283 | 7.1376 | 0.0093
GEN-2017-221 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.3508 | 19.4083 | 0.0575
GEN-2017-221 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9428 | 6.9479 | 0.0051
GEN-2017-221 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.3086 | 18.3104 | 0.0018
GEN-2017-221 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.941 | 18.9731 | 0.0321
GEN-2017-221 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6179 | 5.6211 | 0.0032
GEN-2017-221 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 24.8855 | 25.0892 | 0.2037
GEN-2017-221 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.706 | 18.7116 | 0.0056
GEN-2017-221 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1921 | 14.2196 | 0.0275
GEN-2017-221 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5547 | 16.5586 | 0.0039
GEN-2017-221 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.4228 | 10.4286 | 0.0058
GEN-2017-221 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2468 | 9.2513 | 0.0045
GEN-2017-221 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7978 | 13.8005 | 0.0027
GEN-2017-221 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.4958 | 10.516 | 0.0202
GEN-2017-221 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.5556 | 22.5589 | 0.0033
GEN-2017-221 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.5175 | 14.5206 | 0.0031
GEN-2017-221 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0462 | 9.0493 | 0.0031
GEN-2017-221 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8362 | 13.8406 | 0.0044
GEN-2017-221 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.6049 | 10.6084 | 0.0035
GEN-2017-221 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.0052 | 12.01 | 0.0048
GEN-2017-221 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.0178 | 6.019 | 0.0012
GEN-2017-221 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.4604 | 28.5075 | 0.0471
GEN-2017-221 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2487 | 11.2543 | 0.0056
GEN-2017-221 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.3154 | 19.3365 | 0.0211
GEN-2017-221 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.3017 | 11.3076 | 0.0059
GEN-2017-221 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.501 | 22.5244 | 0.0234
GEN-2017-221 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4694 | 6.4708 | 0.0014
GEN-2017-221 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.5332 | 8.5384 | 0.0052
GEN-2017-221 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1239 | 7.127 | 0.0031
GEN-2017-221 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 11.0019 | 11.0113 | 0.0094
GEN-2017-221 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3625 | 8.3679 | 0.0054
GEN-2017-221 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.9595 | 19.982 | 0.0225
GEN-2017-221 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.7397 | 21.7704 | 0.0307
GEN-2017-221 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5607 | 14.5731 | 0.0124
GEN-2017-221 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 19.0208 | 19.041 | 0.0202
GEN-2017-221 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.6214 | 17.6456 | 0.0242
GEN-2017-221 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.1607 | 25.1902 | 0.0295
GEN-2017-221 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.8401 | 31.9281 | 0.088
GEN-2017-221 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.7669 | 31.8544 | 0.0875
GEN-2017-221 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 22.2212 | 22.251 | 0.0298
GEN-2017-221 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 22.2185 | 22.2483 | 0.0298
GEN-2017-221 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.2156 | 22.2454 | 0.0298
GEN-2017-221 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.3908 | 17.4119 | 0.0211
GEN-2017-221 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.5804 | 20.6073 | 0.0269
GEN-2017-221 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.4404 | 17.4636 | 0.0232
GEN-2017-221 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.0985 | 21.1331 | 0.0346
GEN-2017-221 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.8904 | 20.9143 | 0.0239
GEN-2017-221 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.4362 | 31.4772 | 0.041
GEN-2017-221 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.8895 | 11.8943 | 0.0048
GEN-2017-221 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.9401 | 17.9597 | 0.0196
GEN-2017-221 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.5761 | 19.6083 | 0.0322
GEN-2017-221 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.8389 | 19.8579 | 0.019
GEN-2017-221 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.7208 | 23.768 | 0.0472
GEN-2017-221 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 25.1982 | 25.2326 | 0.0344
GEN-2017-221 | 03 CENTRAL | 533304 | LANG 3 | 115 | 16.1342 | 16.1377 | 0.0035
GEN-2017-221 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.6617 | 2.6619 | 0.0002
GEN-2017-221 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9751 | 3.9757 | 0.0006
GEN-2017-221 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.3072 | 7.308 | 0.0008
GEN-2017-221 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.997 | 9.9998 | 0.0028
GEN-2017-221 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.1912 | 10.1941 | 0.0029
GEN-2017-221 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 19.3798 | 19.3909 | 0.0111
GEN-2017-221 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.2612 | 8.2634 | 0.0022
GEN-2017-221 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.4491 | 8.4514 | 0.0023
GEN-2017-221 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.3476 | 23.3667 | 0.0191
GEN-2017-221 | 03 CENTRAL | 533419 | HEC 3 | 115 | 18.1146 | 18.1243 | 0.0097
GEN-2017-221 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.8391 | 18.8496 | 0.0105
GEN-2017-221 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.7366 | 8.738 | 0.0014
GEN-2017-221 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 11.0629 | 11.0651 | 0.0022
GEN-2017-221 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.8048 | 8.8082 | 0.0034
GEN-2017-221 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7928 | 6.7948 | 0.002
GEN-2017-221 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.4551 | 11.4575 | 0.0024
GEN-2017-221 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 7.0547 | 7.0556 | 0.0009
GEN-2017-221 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0469 | 4.0472 | 0.0003
GEN-2017-221 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.5301 | 7.5312 | 0.0011
GEN-2017-221 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3766 | 6.3773 | 0.0007
GEN-2017-221 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1803 | 6.1811 | 0.0008
GEN-2017-221 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5579 | 6.5588 | 0.0009
GEN-2017-221 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.6124 | 14.6173 | 0.0049
GEN-2017-221 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5483 | 3.5484 | 0.0001
GEN-2017-221 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1633 | 3.1633 | 0
GEN-2017-221 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1574 | 5.1575 | 0.0001
GEN-2017-221 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5469 | 3.5469 | 0
GEN-2017-221 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8218 | 4.8219 | 0.0001
GEN-2017-221 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2348 | 6.2348 | 0
GEN-2017-221 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 20.4141 | 20.4269 | 0.0128
GEN-2017-221 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1342 | 4.1352 | 0.001
GEN-2017-221 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.2485 | 5.25 | 0.0015
GEN-2017-221 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8299 | 5.8317 | 0.0018
GEN-2017-221 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.2245 | 12.2326 | 0.0081
GEN-2017-221 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.7263 | 11.7337 | 0.0074
GEN-2017-221 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.3141 | 12.3166 | 0.0025
GEN-2017-221 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.5295 | 3.5296 | 0.0001
GEN-2017-221 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.8062 | 10.8122 | 0.006
GEN-2017-221 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.1237 | 16.1376 | 0.0139
GEN-2017-221 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.4359 | 2.4359 | 0
GEN-2017-221 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5401 | 7.5432 | 0.0031
GEN-2017-221 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5748 | 8.5782 | 0.0034
GEN-2017-221 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.3547 | 10.3604 | 0.0057
GEN-2017-221 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.8554 | 10.8618 | 0.0064
GEN-2017-221 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.5442 | 8.5453 | 0.0011
GEN-2017-221 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.6892 | 6.6895 | 0.0003
GEN-2017-221 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.0704 | 10.0711 | 0.0007
GEN-2017-221 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.6071 | 12.6096 | 0.0025
GEN-2017-221 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3153 | 4.3154 | 0.0001
GEN-2017-221 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.0503 | 13.0517 | 0.0014
GEN-2017-221 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.477 | 8.4795 | 0.0025
GEN-2017-221 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.4206 | 9.4212 | 0.0006
GEN-2017-221 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.4359 | 2.4359 | 0
GEN-2017-221 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.4359 | 2.4359 | 0
GEN-2017-221 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.1854 | 13.1933 | 0.0079
GEN-2017-221 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.8062 | 16.851 | 0.0448
GEN-2017-221 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 12.9034 | 12.9081 | 0.0047
GEN-2017-221 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.1504 | 18.1688 | 0.0184
GEN-2017-221 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0497 | 11.0552 | 0.0055
GEN-2017-221 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.6438 | 11.6475 | 0.0037
GEN-2017-221 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.2497 | 11.255 | 0.0053
GEN-2017-221 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.2497 | 11.255 | 0.0053
GEN-2017-221 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.5378 | 9.5415 | 0.0037
GEN-2017-221 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.7835 | 8.7867 | 0.0032
GEN-2017-221 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.264 | 3.264 | 0
GEN-2017-221 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2017-221 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.6759 | 28.678 | 0.0021
GEN-2017-221 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5581 | 27.5599 | 0.0018
GEN-2017-221 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8347 | 26.8364 | 0.0017
GEN-2017-221 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8347 | 26.8364 | 0.0017
GEN-2017-221 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8156 | 2.8156 | 0
GEN-2017-221 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2017-221 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2017-221 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.0992 | 13.1075 | 0.0083
GEN-2017-221 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.5743 | 11.5792 | 0.0049
GEN-2017-221 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.7563 | 6.7564 | 0.0001
GEN-2017-221 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.7899 | 10.8102 | 0.0203
GEN-2017-221 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.1666 | 5.1692 | 0.0026
GEN-2017-221 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.4899 | 12.4942 | 0.0043
GEN-2017-221 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2845 | 7.2934 | 0.0089
GEN-2017-221 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.0521 | 13.0604 | 0.0083
GEN-2017-221 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.5015 | 6.5018 | 0.0003
GEN-2017-221 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.6674 | 16.6716 | 0.0042
GEN-2017-221 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 8.9666 | 8.9679 | 0.0013
GEN-2017-221 | 03 CENTRAL | 585420 | COWBOY_RIDGE | 345 | 6.8935 | 6.8943 | 0.0008
GEN-2017-221 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 10.8887 | 10.8907 | 0.002
GEN-2017-221 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.9923 | 9.994 | 0.0017
GEN-2017-221 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.2269 | 7.227 | 0.0001
GEN-2017-221 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.1763 | 10.18 | 0.0037
GEN-2017-221 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.3365 | 15.339 | 0.0025
GEN-2017-221 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.6189 | 5.619 | 0.0001
GEN-2017-221 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8452 | 6.8493 | 0.0041
GEN-2017-221 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.3157 | 10.3256 | 0.0099
GEN-2017-221 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 5.5326 | 5.533 | 0.0004
GEN-2017-221 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.2787 | 8.2864 | 0.0077
GEN-2017-221 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.5741 | 8.577 | 0.0029
GEN-2017-221 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.9643 | 9.9682 | 0.0039
GEN-2017-221 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 12.4985 | 12.5005 | 0.002
GEN-2017-221 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.8062 | 16.851 | 0.0448
GEN-2017-221 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.0079 | 29.0807 | 0.0728
GEN-2017-221 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 10.7402 | 10.7406 | 0.0004
GEN-2017-221 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 21.1158 | 21.3626 | 0.2468
GEN-2017-221 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.8401 | 31.9281 | 0.088
GEN-2017-221 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.0165 | 9.0211 | 0.0046
GEN-2017-221 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.1202 | 9.1228 | 0.0026
GEN-2017-221 | 03 CENTRAL | 761901 | GEN-2017-125 | 345 | 5.333 | 5.3333 | 0.0003
GEN-2017-221 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.5974 | 28.5995 | 0.0021
GEN-2017-221 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 10.9382 | 10.9398 | 0.0016
GEN-2017-221 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.781 | 7.7818 | 0.0008
GEN-2017-221 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4764 | 5.4765 | 0.0001
GEN-2017-221 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.1002 | 4.1003 | 0.0001
GEN-2017-221 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.8108 | 3.8109 | 0.0001
GEN-2017-221 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.7623 | 4.7624 | 0.0001
GEN-2017-226 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0448 | 16.0466 | 0.0018
GEN-2017-226 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.8159 | 24.8163 | 0.0004
GEN-2017-226 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.233 | 13.2338 | 0.0008
GEN-2017-226 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 17.6796 | 17.6864 | 0.0068
GEN-2017-226 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.0928 | 12.1006 | 0.0078
GEN-2017-226 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 20.2727 | 20.2775 | 0.0048
GEN-2017-226 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.5619 | 12.5699 | 0.008
GEN-2017-226 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.5439 | 12.5518 | 0.0079
GEN-2017-226 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.4346 | 12.4487 | 0.0141
GEN-2017-226 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.4293 | 14.4353 | 0.006
GEN-2017-226 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.6335 | 6.6347 | 0.0012
GEN-2017-226 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.4555 | 11.4591 | 0.0036
GEN-2017-226 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 12.3688 | 12.3706 | 0.0018
GEN-2017-226 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.1231 | 12.131 | 0.0079
GEN-2017-226 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.0115 | 11.0224 | 0.0109
GEN-2017-226 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.9488 | 8.9498 | 0.001
GEN-2017-226 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.1186 | 15.1275 | 0.0089
GEN-2017-226 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 16.856 | 16.859 | 0.003
GEN-2017-226 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.7871 | 10.7885 | 0.0014
GEN-2017-226 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.3949 | 12.3967 | 0.0018
GEN-2017-226 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 5.9053 | 5.906 | 0.0007
GEN-2017-226 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.774 | 10.7771 | 0.0031
GEN-2017-226 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.6042 | 7.6058 | 0.0016
GEN-2017-226 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.2253 | 5.2261 | 0.0008
GEN-2017-226 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.4139 | 13.4172 | 0.0033
GEN-2017-226 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8376 | 24.8418 | 0.0042
GEN-2017-226 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.5978 | 10.6006 | 0.0028
GEN-2017-226 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6278 | 19.6479 | 0.0201
GEN-2017-226 | 03 CENTRAL | 532769 | LANG 7 | 345 | 19.3708 | 19.3903 | 0.0195
GEN-2017-226 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.6604 | 13.6661 | 0.0057
GEN-2017-226 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6732 | 11.6973 | 0.0241
GEN-2017-226 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.6209 | 11.6284 | 0.0075
GEN-2017-226 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.7767 | 17.7815 | 0.0048
GEN-2017-226 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.9685 | 15.9817 | 0.0132
GEN-2017-226 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7899 | 9.7991 | 0.0092
GEN-2017-226 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.5157 | 9.5244 | 0.0087
GEN-2017-226 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 21.345 | 21.4794 | 0.1344
GEN-2017-226 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2662 | 7.2777 | 0.0115
GEN-2017-226 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.065 | 6.0724 | 0.0074
GEN-2017-226 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0387 | 5.0437 | 0.005
GEN-2017-226 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.1273 | 7.1376 | 0.0103
GEN-2017-226 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.3078 | 19.4083 | 0.1005
GEN-2017-226 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9397 | 6.9479 | 0.0082
GEN-2017-226 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.3067 | 18.3104 | 0.0037
GEN-2017-226 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.9048 | 18.9731 | 0.0683
GEN-2017-226 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.616 | 5.6211 | 0.0051
GEN-2017-226 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 24.8681 | 25.0892 | 0.2211
GEN-2017-226 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.7009 | 18.7116 | 0.0107
GEN-2017-226 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1753 | 14.2196 | 0.0443
GEN-2017-226 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5513 | 16.5586 | 0.0073
GEN-2017-226 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.4164 | 10.4286 | 0.0122
GEN-2017-226 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2418 | 9.2513 | 0.0095
GEN-2017-226 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7954 | 13.8005 | 0.0051
GEN-2017-226 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.4938 | 10.516 | 0.0222
GEN-2017-226 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.5548 | 22.5589 | 0.0041
GEN-2017-226 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.5167 | 14.5206 | 0.0039
GEN-2017-226 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0449 | 9.0493 | 0.0044
GEN-2017-226 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8348 | 13.8406 | 0.0058
GEN-2017-226 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.5977 | 10.6084 | 0.0107
GEN-2017-226 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.9954 | 12.01 | 0.0146
GEN-2017-226 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.0154 | 6.019 | 0.0036
GEN-2017-226 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.3714 | 28.5075 | 0.1361
GEN-2017-226 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2373 | 11.2543 | 0.017
GEN-2017-226 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2731 | 19.3365 | 0.0634
GEN-2017-226 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2896 | 11.3076 | 0.018
GEN-2017-226 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.4515 | 22.5244 | 0.0729
GEN-2017-226 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4666 | 6.4708 | 0.0042
GEN-2017-226 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.5006 | 8.5384 | 0.0378
GEN-2017-226 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1092 | 7.127 | 0.0178
GEN-2017-226 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.934 | 11.0113 | 0.0773
GEN-2017-226 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3232 | 8.3679 | 0.0447
GEN-2017-226 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.9144 | 19.982 | 0.0676
GEN-2017-226 | 03 CENTRAL | 533033 | CANAL 4 | 138 | 16.6518 | 16.7214 | 0.0696
GEN-2017-226 | 03 CENTRAL | 533034 | CENTENN4 | 138 | 14.8596 | 14.9798 | 0.1202
GEN-2017-226 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.6081 | 21.7704 | 0.1623
GEN-2017-226 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5233 | 14.5731 | 0.0498
GEN-2017-226 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.9791 | 19.041 | 0.0619
GEN-2017-226 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.4518 | 17.6456 | 0.1938
GEN-2017-226 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.0866 | 25.1902 | 0.1036
GEN-2017-226 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.1047 | 31.9281 | 0.8234
GEN-2017-226 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.0359 | 31.8544 | 0.8185
GEN-2017-226 | 03 CENTRAL | 533043 | FOWLER 4 | 138 | 16.4099 | 16.4825 | 0.0726
GEN-2017-226 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 22.1055 | 22.251 | 0.1455
GEN-2017-226 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 22.1029 | 22.2483 | 0.1454
GEN-2017-226 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.1002 | 22.2454 | 0.1452
GEN-2017-226 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.2706 | 17.4119 | 0.1413
GEN-2017-226 | 03 CENTRAL | 533050 | HOOVERS4 | 138 | 17.2672 | 17.4082 | 0.141
GEN-2017-226 | 03 CENTRAL | 533051 | INTERST4 | 138 | 15.9219 | 16.0265 | 0.1046
GEN-2017-226 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.4793 | 20.6073 | 0.128
GEN-2017-226 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.2834 | 17.4636 | 0.1802
GEN-2017-226 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.8638 | 21.1331 | 0.2693
GEN-2017-226 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.8393 | 20.9143 | 0.075
GEN-2017-226 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.3617 | 31.4772 | 0.1155
GEN-2017-226 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.8795 | 11.8943 | 0.0148
GEN-2017-226 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.8628 | 17.9597 | 0.0969
GEN-2017-226 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3152 | 19.6083 | 0.2931
GEN-2017-226 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.7879 | 19.8579 | 0.07
GEN-2017-226 | 03 CENTRAL | 533073 | WACO N 4 | 138 | 19.2142 | 19.3332 | 0.119
GEN-2017-226 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.3458 | 23.768 | 0.4222
GEN-2017-226 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 25.1557 | 25.2326 | 0.0769
GEN-2017-226 | 03 CENTRAL | 533304 | LANG 3 | 115 | 16.1328 | 16.1377 | 0.0049
GEN-2017-226 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.661 | 2.6619 | 0.0009
GEN-2017-226 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9737 | 3.9757 | 0.002
GEN-2017-226 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.3069 | 7.308 | 0.0011
GEN-2017-226 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.9955 | 9.9998 | 0.0043
GEN-2017-226 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.1897 | 10.1941 | 0.0044
GEN-2017-226 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 19.3739 | 19.3909 | 0.017
GEN-2017-226 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.26 | 8.2634 | 0.0034
GEN-2017-226 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.4478 | 8.4514 | 0.0036
GEN-2017-226 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.3365 | 23.3667 | 0.0302
GEN-2017-226 | 03 CENTRAL | 533419 | HEC 3 | 115 | 18.1093 | 18.1243 | 0.015
GEN-2017-226 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.8334 | 18.8496 | 0.0162
GEN-2017-226 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.736 | 8.738 | 0.002
GEN-2017-226 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 11.0619 | 11.0651 | 0.0032
GEN-2017-226 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7943 | 8.8082 | 0.0139
GEN-2017-226 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7865 | 6.7948 | 0.0083
GEN-2017-226 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.454 | 11.4575 | 0.0035
GEN-2017-226 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 7.0543 | 7.0556 | 0.0013
GEN-2017-226 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0467 | 4.0472 | 0.0005
GEN-2017-226 | 03 CENTRAL | 533505 | NCTYSVC2 | 69 | 4.0736 | 4.0741 | 0.0005
GEN-2017-226 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.5295 | 7.5312 | 0.0017
GEN-2017-226 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3761 | 6.3773 | 0.0012
GEN-2017-226 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1799 | 6.1811 | 0.0012
GEN-2017-226 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5575 | 6.5588 | 0.0013
GEN-2017-226 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.6014 | 14.6173 | 0.0159
GEN-2017-226 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5483 | 3.5484 | 0.0001
GEN-2017-226 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1632 | 3.1633 | 0.0001
GEN-2017-226 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1574 | 5.1575 | 0.0001
GEN-2017-226 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5469 | 3.5469 | 0
GEN-2017-226 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8218 | 4.8219 | 0.0001
GEN-2017-226 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2347 | 6.2348 | 0.0001
GEN-2017-226 | 03 CENTRAL | 533732 | BURRTON2 | 69 | 2.9974 | 2.9995 | 0.0021
GEN-2017-226 | 03 CENTRAL | 533736 | HALSTED2 | 69 | 7.5513 | 7.5649 | 0.0136
GEN-2017-226 | 03 CENTRAL | 533742 | MOUND 2 | 69 | 7.3221 | 7.3318 | 0.0097
GEN-2017-226 | 03 CENTRAL | 533743 | MUD CRK2 | 69 | 5.4552 | 5.4616 | 0.0064
GEN-2017-226 | 03 CENTRAL | 533744 | MUDCRKJ2 | 69 | 6.1672 | 6.1754 | 0.0082
GEN-2017-226 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 20.3619 | 20.4269 | 0.065
GEN-2017-226 | 03 CENTRAL | 533788 | COWSKIN2 | 69 | 16.3168 | 16.3854 | 0.0686
GEN-2017-226 | 03 CENTRAL | 533799 | GRANT 2 | 69 | 12.7571 | 12.7812 | 0.0241
GEN-2017-226 | 03 CENTRAL | 533800 | GRANT J2 | 69 | 10.0137 | 10.0302 | 0.0165
GEN-2017-226 | 03 CENTRAL | 533805 | HOOVERN2 | 69 | 30.9876 | 31.1742 | 0.1866
GEN-2017-226 | 03 CENTRAL | 533806 | HOOVERS2 | 69 | 31.011 | 31.1978 | 0.1868
GEN-2017-226 | 03 CENTRAL | 533814 | MASCOT 2 | 69 | 20.1288 | 20.1926 | 0.0638
GEN-2017-226 | 03 CENTRAL | 533818 | MEAD N 2 | 69 | 25.8338 | 25.945 | 0.1112
GEN-2017-226 | 03 CENTRAL | 533820 | MOSSMAN2 | 69 | 18.2562 | 18.3009 | 0.0447
GEN-2017-226 | 03 CENTRAL | 533831 | RENEW 2 | 69 | 17.8316 | 17.879 | 0.0474
GEN-2017-226 | 03 CENTRAL | 533835 | 17TH TP2 | 69 | 25.1836 | 25.2869 | 0.1033
GEN-2017-226 | 03 CENTRAL | 533840 | 17TH 2 | 69 | 27.3952 | 27.5138 | 0.1186
GEN-2017-226 | 03 CENTRAL | 533849 | VISTAPK2 | 69 | 17.3369 | 17.391 | 0.0541
GEN-2017-226 | 03 CENTRAL | 533854 | WESTLNK2 | 69 | 15.3953 | 15.4514 | 0.0561
GEN-2017-226 | 03 CENTRAL | 533855 | WATER1 2 | 69 | 23.9689 | 24.0682 | 0.0993
GEN-2017-226 | 03 CENTRAL | 533859 | RIPLEYE2 | 69 | 22.9191 | 23.0017 | 0.0826
GEN-2017-226 | 03 CENTRAL | 533860 | RIPLEYM2 | 69 | 22.9224 | 23.005 | 0.0826
GEN-2017-226 | 03 CENTRAL | 533861 | BU5FURL2 | 69 | 7.2793 | 7.2858 | 0.0065
GEN-2017-226 | 03 CENTRAL | 533874 | SG9STMK2 | 69 | 16.2865 | 16.3548 | 0.0683
GEN-2017-226 | 03 CENTRAL | 533879 | GODDTAP2 | 69 | 8.3036 | 8.3203 | 0.0167
GEN-2017-226 | 03 CENTRAL | 533880 | GODDARD2 | 69 | 6.3977 | 6.4076 | 0.0099
GEN-2017-226 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8282 | 5.8317 | 0.0035
GEN-2017-226 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.2151 | 12.2326 | 0.0175
GEN-2017-226 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.7185 | 11.7337 | 0.0152
GEN-2017-226 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.8077 | 10.8122 | 0.0045
GEN-2017-226 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.1272 | 16.1376 | 0.0104
GEN-2017-226 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.3489 | 10.3604 | 0.0115
GEN-2017-226 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.848 | 10.8618 | 0.0138
GEN-2017-226 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.1882 | 13.1933 | 0.0051
GEN-2017-226 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.8239 | 16.851 | 0.0271
GEN-2017-226 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.1557 | 18.1688 | 0.0131
GEN-2017-226 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0517 | 11.0552 | 0.0035
GEN-2017-226 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.2516 | 11.255 | 0.0034
GEN-2017-226 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.2516 | 11.255 | 0.0034
GEN-2017-226 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.5391 | 9.5415 | 0.0024
GEN-2017-226 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.7846 | 8.7867 | 0.0021
GEN-2017-226 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2017-226 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.6751 | 28.678 | 0.0029
GEN-2017-226 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5568 | 27.5599 | 0.0031
GEN-2017-226 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8335 | 26.8364 | 0.0029
GEN-2017-226 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8335 | 26.8364 | 0.0029
GEN-2017-226 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8156 | 2.8156 | 0
GEN-2017-226 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2017-226 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2017-226 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.0901 | 13.1075 | 0.0174
GEN-2017-226 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.576 | 11.5792 | 0.0032
GEN-2017-226 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.7878 | 10.8102 | 0.0224
GEN-2017-226 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.165 | 5.1692 | 0.0042
GEN-2017-226 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2836 | 7.2934 | 0.0098
GEN-2017-226 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.0431 | 13.0604 | 0.0173
GEN-2017-226 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.6686 | 16.6716 | 0.003
GEN-2017-226 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 8.967 | 8.9679 | 0.0009
GEN-2017-226 | 03 CENTRAL | 585420 | COWBOY_RIDGE | 345 | 6.8938 | 6.8943 | 0.0005
GEN-2017-226 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 10.8893 | 10.8907 | 0.0014
GEN-2017-226 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.9929 | 9.994 | 0.0011
GEN-2017-226 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.1776 | 10.18 | 0.0024
GEN-2017-226 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.3374 | 15.339 | 0.0016
GEN-2017-226 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8441 | 6.8493 | 0.0052
GEN-2017-226 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.3129 | 10.3256 | 0.0127
GEN-2017-226 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 5.5324 | 5.533 | 0.0006
GEN-2017-226 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.2739 | 8.2864 | 0.0125
GEN-2017-226 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.5733 | 8.577 | 0.0037
GEN-2017-226 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.9632 | 9.9682 | 0.005
GEN-2017-226 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.8239 | 16.851 | 0.0271
GEN-2017-226 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 28.3981 | 29.0807 | 0.6826
GEN-2017-226 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 21.2298 | 21.3626 | 0.1328
GEN-2017-226 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.1047 | 31.9281 | 0.8234
GEN-2017-226 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.0138 | 9.0211 | 0.0073
GEN-2017-226 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.1148 | 9.1228 | 0.008
GEN-2017-226 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.5966 | 28.5995 | 0.0029
GEN-2017-226 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 10.9372 | 10.9398 | 0.0026
GEN-2017-226 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.7806 | 7.7818 | 0.0012
GEN-2017-227 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0448 | 16.0466 | 0.0018
GEN-2017-227 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.8159 | 24.8163 | 0.0004
GEN-2017-227 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.233 | 13.2338 | 0.0008
GEN-2017-227 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 17.6796 | 17.6864 | 0.0068
GEN-2017-227 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.0929 | 12.1006 | 0.0077
GEN-2017-227 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 20.2727 | 20.2775 | 0.0048
GEN-2017-227 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.562 | 12.5699 | 0.0079
GEN-2017-227 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.5439 | 12.5518 | 0.0079
GEN-2017-227 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.4347 | 12.4487 | 0.014
GEN-2017-227 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.4294 | 14.4353 | 0.0059
GEN-2017-227 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.6335 | 6.6347 | 0.0012
GEN-2017-227 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.4555 | 11.4591 | 0.0036
GEN-2017-227 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 12.3688 | 12.3706 | 0.0018
GEN-2017-227 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.1232 | 12.131 | 0.0078
GEN-2017-227 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.0115 | 11.0224 | 0.0109
GEN-2017-227 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.9488 | 8.9498 | 0.001
GEN-2017-227 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.1186 | 15.1275 | 0.0089
GEN-2017-227 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 16.856 | 16.859 | 0.003
GEN-2017-227 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.7871 | 10.7885 | 0.0014
GEN-2017-227 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.3949 | 12.3967 | 0.0018
GEN-2017-227 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 5.9053 | 5.906 | 0.0007
GEN-2017-227 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.774 | 10.7771 | 0.0031
GEN-2017-227 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.6042 | 7.6058 | 0.0016
GEN-2017-227 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.2253 | 5.2261 | 0.0008
GEN-2017-227 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.4139 | 13.4172 | 0.0033
GEN-2017-227 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8376 | 24.8418 | 0.0042
GEN-2017-227 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.5978 | 10.6006 | 0.0028
GEN-2017-227 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 19.6278 | 19.6479 | 0.0201
GEN-2017-227 | 03 CENTRAL | 532769 | LANG 7 | 345 | 19.3708 | 19.3903 | 0.0195
GEN-2017-227 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.6604 | 13.6661 | 0.0057
GEN-2017-227 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.6733 | 11.6973 | 0.024
GEN-2017-227 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.6209 | 11.6284 | 0.0075
GEN-2017-227 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.7767 | 17.7815 | 0.0048
GEN-2017-227 | 03 CENTRAL | 532776 | READWF 7 | 345 | 15.9686 | 15.9817 | 0.0131
GEN-2017-227 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7899 | 9.7991 | 0.0092
GEN-2017-227 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.5158 | 9.5244 | 0.0086
GEN-2017-227 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 21.3456 | 21.4794 | 0.1338
GEN-2017-227 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2662 | 7.2777 | 0.0115
GEN-2017-227 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.065 | 6.0724 | 0.0074
GEN-2017-227 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0388 | 5.0437 | 0.0049
GEN-2017-227 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.1274 | 7.1376 | 0.0102
GEN-2017-227 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.3082 | 19.4083 | 0.1001
GEN-2017-227 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9397 | 6.9479 | 0.0082
GEN-2017-227 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.3068 | 18.3104 | 0.0036
GEN-2017-227 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.9051 | 18.9731 | 0.068
GEN-2017-227 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.616 | 5.6211 | 0.0051
GEN-2017-227 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 24.8691 | 25.0892 | 0.2201
GEN-2017-227 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.7009 | 18.7116 | 0.0107
GEN-2017-227 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1755 | 14.2196 | 0.0441
GEN-2017-227 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5513 | 16.5586 | 0.0073
GEN-2017-227 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.4164 | 10.4286 | 0.0122
GEN-2017-227 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2418 | 9.2513 | 0.0095
GEN-2017-227 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7954 | 13.8005 | 0.0051
GEN-2017-227 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.4938 | 10.516 | 0.0222
GEN-2017-227 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.5548 | 22.5589 | 0.0041
GEN-2017-227 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.5167 | 14.5206 | 0.0039
GEN-2017-227 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0449 | 9.0493 | 0.0044
GEN-2017-227 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8348 | 13.8406 | 0.0058
GEN-2017-227 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.5977 | 10.6084 | 0.0107
GEN-2017-227 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.9954 | 12.01 | 0.0146
GEN-2017-227 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.0154 | 6.019 | 0.0036
GEN-2017-227 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.372 | 28.5075 | 0.1355
GEN-2017-227 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2373 | 11.2543 | 0.017
GEN-2017-227 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2733 | 19.3365 | 0.0632
GEN-2017-227 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2897 | 11.3076 | 0.0179
GEN-2017-227 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.4518 | 22.5244 | 0.0726
GEN-2017-227 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4666 | 6.4708 | 0.0042
GEN-2017-227 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.5008 | 8.5384 | 0.0376
GEN-2017-227 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1093 | 7.127 | 0.0177
GEN-2017-227 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.9343 | 11.0113 | 0.077
GEN-2017-227 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3234 | 8.3679 | 0.0445
GEN-2017-227 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.9146 | 19.982 | 0.0674
GEN-2017-227 | 03 CENTRAL | 533033 | CANAL 4 | 138 | 16.6521 | 16.7214 | 0.0693
GEN-2017-227 | 03 CENTRAL | 533034 | CENTENN4 | 138 | 14.8601 | 14.9798 | 0.1197
GEN-2017-227 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.6088 | 21.7704 | 0.1616
GEN-2017-227 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5235 | 14.5731 | 0.0496
GEN-2017-227 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.9794 | 19.041 | 0.0616
GEN-2017-227 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.4526 | 17.6456 | 0.193
GEN-2017-227 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.087 | 25.1902 | 0.1032
GEN-2017-227 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.108 | 31.9281 | 0.8201
GEN-2017-227 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.0392 | 31.8544 | 0.8152
GEN-2017-227 | 03 CENTRAL | 533043 | FOWLER 4 | 138 | 16.4102 | 16.4825 | 0.0723
GEN-2017-227 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 22.106 | 22.251 | 0.145
GEN-2017-227 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 22.1035 | 22.2483 | 0.1448
GEN-2017-227 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.1007 | 22.2454 | 0.1447
GEN-2017-227 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.2711 | 17.4119 | 0.1408
GEN-2017-227 | 03 CENTRAL | 533050 | HOOVERS4 | 138 | 17.2678 | 17.4082 | 0.1404
GEN-2017-227 | 03 CENTRAL | 533051 | INTERST4 | 138 | 15.9223 | 16.0265 | 0.1042
GEN-2017-227 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.4798 | 20.6073 | 0.1275
GEN-2017-227 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.2841 | 17.4636 | 0.1795
GEN-2017-227 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.8649 | 21.1331 | 0.2682
GEN-2017-227 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.8396 | 20.9143 | 0.0747
GEN-2017-227 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.3622 | 31.4772 | 0.115
GEN-2017-227 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.8796 | 11.8943 | 0.0147
GEN-2017-227 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.8632 | 17.9597 | 0.0965
GEN-2017-227 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3164 | 19.6083 | 0.2919
GEN-2017-227 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.7882 | 19.8579 | 0.0697
GEN-2017-227 | 03 CENTRAL | 533073 | WACO N 4 | 138 | 19.2147 | 19.3332 | 0.1185
GEN-2017-227 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.3475 | 23.768 | 0.4205
GEN-2017-227 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 25.156 | 25.2326 | 0.0766
GEN-2017-227 | 03 CENTRAL | 533304 | LANG 3 | 115 | 16.1328 | 16.1377 | 0.0049
GEN-2017-227 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.661 | 2.6619 | 0.0009
GEN-2017-227 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9737 | 3.9757 | 0.002
GEN-2017-227 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.3069 | 7.308 | 0.0011
GEN-2017-227 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.9956 | 9.9998 | 0.0042
GEN-2017-227 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.1897 | 10.1941 | 0.0044
GEN-2017-227 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 19.3739 | 19.3909 | 0.017
GEN-2017-227 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.2601 | 8.2634 | 0.0033
GEN-2017-227 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.4478 | 8.4514 | 0.0036
GEN-2017-227 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.3367 | 23.3667 | 0.03
GEN-2017-227 | 03 CENTRAL | 533419 | HEC 3 | 115 | 18.1094 | 18.1243 | 0.0149
GEN-2017-227 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.8335 | 18.8496 | 0.0161
GEN-2017-227 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.736 | 8.738 | 0.002
GEN-2017-227 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 11.0619 | 11.0651 | 0.0032
GEN-2017-227 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7943 | 8.8082 | 0.0139
GEN-2017-227 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7865 | 6.7948 | 0.0083
GEN-2017-227 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.454 | 11.4575 | 0.0035
GEN-2017-227 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 7.0543 | 7.0556 | 0.0013
GEN-2017-227 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0467 | 4.0472 | 0.0005
GEN-2017-227 | 03 CENTRAL | 533505 | NCTYSVC2 | 69 | 4.0736 | 4.0741 | 0.0005
GEN-2017-227 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.5295 | 7.5312 | 0.0017
GEN-2017-227 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3761 | 6.3773 | 0.0012
GEN-2017-227 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1799 | 6.1811 | 0.0012
GEN-2017-227 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5575 | 6.5588 | 0.0013
GEN-2017-227 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.6015 | 14.6173 | 0.0158
GEN-2017-227 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5483 | 3.5484 | 0.0001
GEN-2017-227 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1632 | 3.1633 | 0.0001
GEN-2017-227 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1574 | 5.1575 | 0.0001
GEN-2017-227 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5469 | 3.5469 | 0
GEN-2017-227 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8218 | 4.8219 | 0.0001
GEN-2017-227 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2347 | 6.2348 | 0.0001
GEN-2017-227 | 03 CENTRAL | 533732 | BURRTON2 | 69 | 2.9974 | 2.9995 | 0.0021
GEN-2017-227 | 03 CENTRAL | 533736 | HALSTED2 | 69 | 7.5513 | 7.5649 | 0.0136
GEN-2017-227 | 03 CENTRAL | 533742 | MOUND 2 | 69 | 7.3221 | 7.3318 | 0.0097
GEN-2017-227 | 03 CENTRAL | 533743 | MUD CRK2 | 69 | 5.4553 | 5.4616 | 0.0063
GEN-2017-227 | 03 CENTRAL | 533744 | MUDCRKJ2 | 69 | 6.1673 | 6.1754 | 0.0081
GEN-2017-227 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 20.3622 | 20.4269 | 0.0647
GEN-2017-227 | 03 CENTRAL | 533788 | COWSKIN2 | 69 | 16.3171 | 16.3854 | 0.0683
GEN-2017-227 | 03 CENTRAL | 533799 | GRANT 2 | 69 | 12.7572 | 12.7812 | 0.024
GEN-2017-227 | 03 CENTRAL | 533800 | GRANT J2 | 69 | 10.0138 | 10.0302 | 0.0164
GEN-2017-227 | 03 CENTRAL | 533805 | HOOVERN2 | 69 | 30.9884 | 31.1742 | 0.1858
GEN-2017-227 | 03 CENTRAL | 533806 | HOOVERS2 | 69 | 31.0117 | 31.1978 | 0.1861
GEN-2017-227 | 03 CENTRAL | 533814 | MASCOT 2 | 69 | 20.129 | 20.1926 | 0.0636
GEN-2017-227 | 03 CENTRAL | 533818 | MEAD N 2 | 69 | 25.8343 | 25.945 | 0.1107
GEN-2017-227 | 03 CENTRAL | 533820 | MOSSMAN2 | 69 | 18.2563 | 18.3009 | 0.0446
GEN-2017-227 | 03 CENTRAL | 533831 | RENEW 2 | 69 | 17.8318 | 17.879 | 0.0472
GEN-2017-227 | 03 CENTRAL | 533835 | 17TH TP2 | 69 | 25.184 | 25.2869 | 0.1029
GEN-2017-227 | 03 CENTRAL | 533840 | 17TH 2 | 69 | 27.3957 | 27.5138 | 0.1181
GEN-2017-227 | 03 CENTRAL | 533849 | VISTAPK2 | 69 | 17.3371 | 17.391 | 0.0539
GEN-2017-227 | 03 CENTRAL | 533854 | WESTLNK2 | 69 | 15.3956 | 15.4514 | 0.0558
GEN-2017-227 | 03 CENTRAL | 533855 | WATER1 2 | 69 | 23.9693 | 24.0682 | 0.0989
GEN-2017-227 | 03 CENTRAL | 533859 | RIPLEYE2 | 69 | 22.9195 | 23.0017 | 0.0822
GEN-2017-227 | 03 CENTRAL | 533860 | RIPLEYM2 | 69 | 22.9227 | 23.005 | 0.0823
GEN-2017-227 | 03 CENTRAL | 533861 | BU5FURL2 | 69 | 7.2793 | 7.2858 | 0.0065
GEN-2017-227 | 03 CENTRAL | 533874 | SG9STMK2 | 69 | 16.2867 | 16.3548 | 0.0681
GEN-2017-227 | 03 CENTRAL | 533879 | GODDTAP2 | 69 | 8.3037 | 8.3203 | 0.0166
GEN-2017-227 | 03 CENTRAL | 533880 | GODDARD2 | 69 | 6.3978 | 6.4076 | 0.0098
GEN-2017-227 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8282 | 5.8317 | 0.0035
GEN-2017-227 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.2152 | 12.2326 | 0.0174
GEN-2017-227 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.7186 | 11.7337 | 0.0151
GEN-2017-227 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.8077 | 10.8122 | 0.0045
GEN-2017-227 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.1272 | 16.1376 | 0.0104
GEN-2017-227 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.349 | 10.3604 | 0.0114
GEN-2017-227 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.848 | 10.8618 | 0.0138
GEN-2017-227 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.1883 | 13.1933 | 0.005
GEN-2017-227 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.824 | 16.851 | 0.027
GEN-2017-227 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.1558 | 18.1688 | 0.013
GEN-2017-227 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0517 | 11.0552 | 0.0035
GEN-2017-227 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.2516 | 11.255 | 0.0034
GEN-2017-227 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.2516 | 11.255 | 0.0034
GEN-2017-227 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.5391 | 9.5415 | 0.0024
GEN-2017-227 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.7847 | 8.7867 | 0.002
GEN-2017-227 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2017-227 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.6751 | 28.678 | 0.0029
GEN-2017-227 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5568 | 27.5599 | 0.0031
GEN-2017-227 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8336 | 26.8364 | 0.0028
GEN-2017-227 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8336 | 26.8364 | 0.0028
GEN-2017-227 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8156 | 2.8156 | 0
GEN-2017-227 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2017-227 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2017-227 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.0902 | 13.1075 | 0.0173
GEN-2017-227 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.576 | 11.5792 | 0.0032
GEN-2017-227 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.7879 | 10.8102 | 0.0223
GEN-2017-227 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.165 | 5.1692 | 0.0042
GEN-2017-227 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2837 | 7.2934 | 0.0097
GEN-2017-227 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.0431 | 13.0604 | 0.0173
GEN-2017-227 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.6686 | 16.6716 | 0.003
GEN-2017-227 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 8.967 | 8.9679 | 0.0009
GEN-2017-227 | 03 CENTRAL | 585420 | COWBOY_RIDGE | 345 | 6.8938 | 6.8943 | 0.0005
GEN-2017-227 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 10.8893 | 10.8907 | 0.0014
GEN-2017-227 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.9929 | 9.994 | 0.0011
GEN-2017-227 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.1776 | 10.18 | 0.0024
GEN-2017-227 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.3374 | 15.339 | 0.0016
GEN-2017-227 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8441 | 6.8493 | 0.0052
GEN-2017-227 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.313 | 10.3256 | 0.0126
GEN-2017-227 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 5.5324 | 5.533 | 0.0006
GEN-2017-227 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.274 | 8.2864 | 0.0124
GEN-2017-227 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.5733 | 8.577 | 0.0037
GEN-2017-227 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.9632 | 9.9682 | 0.005
GEN-2017-227 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.824 | 16.851 | 0.027
GEN-2017-227 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 28.4009 | 29.0807 | 0.6798
GEN-2017-227 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 21.2304 | 21.3626 | 0.1322
GEN-2017-227 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.108 | 31.9281 | 0.8201
GEN-2017-227 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.0139 | 9.0211 | 0.0072
GEN-2017-227 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.1148 | 9.1228 | 0.008
GEN-2017-227 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.5967 | 28.5995 | 0.0028
GEN-2017-227 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 10.9373 | 10.9398 | 0.0025
GEN-2017-227 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.7806 | 7.7818 | 0.0012
GEN-2017-117 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5787 | 10.5801 | 0.0014
GEN-2017-117 | 04 SOUTHEAST | 511433 | HINTON 4 | 138 | 5.94 | 5.9473 | 0.0073
GEN-2017-117 | 04 SOUTHEAST | 511489 | WTH_JCT4 | 138 | 5.2712 | 5.2746 | 0.0034
GEN-2017-117 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4159 | 10.4172 | 0.0013
GEN-2017-117 | 04 SOUTHEAST | 511540 | CAN_GAS4 | 138 | 9.2041 | 9.2248 | 0.0207
GEN-2017-117 | 04 SOUTHEAST | 511548 | REDROCKRD4 | 138 | 8.9694 | 8.9884 | 0.019
GEN-2017-117 | 04 SOUTHEAST | 511559 | DARLINGTNRD4 | 138 | 6.8135 | 6.8242 | 0.0107
GEN-2017-117 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.9421 | 6.9428 | 0.0007
GEN-2017-117 | 04 SOUTHEAST | 511581 | MAPLERD4 | 138 | 6.5537 | 6.5636 | 0.0099
GEN-2017-117 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7529 | 23.7553 | 0.0024
GEN-2017-117 | 04 SOUTHEAST | 514817 | SVCELRN2 | 69 | 6.5615 | 6.5639 | 0.0024
GEN-2017-117 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.5466 | 7.55 | 0.0034
GEN-2017-117 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.228 | 17.252 | 0.024
GEN-2017-117 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.6642 | 18.7141 | 0.0499
GEN-2017-117 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 15.7301 | 15.808 | 0.0779
GEN-2017-117 | 04 SOUTHEAST | 514823 | ROMNOSE4 | 138 | 6.0162 | 6.0219 | 0.0057
GEN-2017-117 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 37.5938 | 37.6002 | 0.0064
GEN-2017-117 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6122 | 27.6188 | 0.0066
GEN-2017-117 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3189 | 34.3238 | 0.0049
GEN-2017-117 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 30.9268 | 30.9327 | 0.0059
GEN-2017-117 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.594 | 29.6006 | 0.0066
GEN-2017-117 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.126 | 20.1299 | 0.0039
GEN-2017-117 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.6904 | 46.7216 | 0.0312
GEN-2017-117 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8451 | 36.8533 | 0.0082
GEN-2017-117 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 36.6116 | 36.6149 | 0.0033
GEN-2017-117 | 04 SOUTHEAST | 515314 | REDCORN4 | 138 | 8.542 | 8.5545 | 0.0125
GEN-2017-117 | 04 SOUTHEAST | 515460 | TALBEAR4 | 138 | 8.0749 | 8.0915 | 0.0166
GEN-2017-117 | 04 SOUTHEAST | 515472 | TLBEART4 | 138 | 9.1477 | 9.1682 | 0.0205
GEN-2017-117 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8783 | 34.8833 | 0.005
GEN-2017-117 | 04 SOUTHEAST | 515506 | OKRCHET2 | 69 | 3.7145 | 3.7157 | 0.0012
GEN-2017-117 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3368 | 18.3389 | 0.0021
GEN-2017-117 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 5.8159 | 5.8212 | 0.0053
GEN-2017-117 | 04 SOUTHEAST | 520401 | BAILEY4 | 138 | 10.0834 | 10.089 | 0.0056
GEN-2017-117 | 04 SOUTHEAST | 520412 | MUSTANG4 | 138 | 7.1044 | 7.1161 | 0.0117
GEN-2017-117 | 04 SOUTHEAST | 520501 | BRIDGCR4 | 138 | 8.2665 | 8.2718 | 0.0053
GEN-2017-117 | 04 SOUTHEAST | 520502 | CANA 4 | 138 | 10.0748 | 10.099 | 0.0242
GEN-2017-117 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 12.8282 | 12.8354 | 0.0072
GEN-2017-117 | 04 SOUTHEAST | 520530 | AMBERTP4 | 138 | 8.2813 | 8.2834 | 0.0021
GEN-2017-117 | 04 SOUTHEAST | 520533 | KGFSHSW4 | 138 | 8.6734 | 8.6786 | 0.0052
GEN-2017-117 | 04 SOUTHEAST | 520536 | WATNGSW4 | 138 | 7.0655 | 7.0705 | 0.005
GEN-2017-117 | 04 SOUTHEAST | 520552 | REDCNTP4 | 138 | 9.2131 | 9.2272 | 0.0141
GEN-2017-117 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 36.8687 | 36.8738 | 0.0051
GEN-2017-117 | 04 SOUTHEAST | 520839 | CALUMET4 | 138 | 8.5346 | 8.5458 | 0.0112
GEN-2017-117 | 04 SOUTHEAST | 520859 | COGAR 4 | 138 | 9.1902 | 9.2034 | 0.0132
GEN-2017-117 | 04 SOUTHEAST | 520865 | CONCHO 4 | 138 | 7.2024 | 7.2082 | 0.0058
GEN-2017-117 | 04 SOUTHEAST | 520893 | EL RENO4 | 138 | 14.4906 | 14.5905 | 0.0999
GEN-2017-117 | 04 SOUTHEAST | 520899 | SCOTTSW4 | 138 | 11.8674 | 11.9054 | 0.038
GEN-2017-117 | 04 SOUTHEAST | 520964 | OMEGA 4 | 138 | 6.0863 | 6.09 | 0.0037
GEN-2017-117 | 04 SOUTHEAST | 521005 | SARA RD4 | 138 | 7.1715 | 7.1821 | 0.0106
GEN-2017-117 | 04 SOUTHEAST | 521016 | OKEENE 4 | 138 | 7.1448 | 7.1479 | 0.0031
GEN-2017-117 | 04 SOUTHEAST | 521059 | SUNSHIN4 | 138 | 9.507 | 9.5143 | 0.0073
GEN-2017-117 | 04 SOUTHEAST | 521072 | TUTLETP4 | 138 | 7.3409 | 7.3443 | 0.0034
GEN-2017-117 | 04 SOUTHEAST | 521091 | WATONGA4 | 138 | 4.4722 | 4.4748 | 0.0026
GEN-2017-117 | 04 SOUTHEAST | 521123 | WMOORE 4 | 138 | 11.7579 | 11.7626 | 0.0047
GEN-2017-117 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1897 | 27.1936 | 0.0039
GEN-2017-117 | 04 SOUTHEAST | 588720 | GEN-2017-117 | 138 | 14.4906 | 14.5905 | 0.0999
GEN-2017-133 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.2375 | 8.2319 | -0.0056
GEN-2017-133 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 20.6873 | 20.6863 | -0.001
GEN-2017-133 | 04 SOUTHEAST | 300856 | 2LUTHER | 69 | 6.5228 | 6.5199 | -0.0029
GEN-2017-133 | 04 SOUTHEAST | 301372 | 4LUTHERD | 138 | 8.2271 | 8.2216 | -0.0055
GEN-2017-133 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 20.4842 | 20.483 | -0.0012
GEN-2017-133 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 17.7577 | 17.758 | 0.0003
GEN-2017-133 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 23.5322 | 23.5251 | -0.0071
GEN-2017-133 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.1886 | 10.1829 | -0.0057
GEN-2017-133 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.1736 | 9.1687 | -0.0049
GEN-2017-133 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 8.9038 | 8.9003 | -0.0035
GEN-2017-133 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 24.6857 | 24.671 | -0.0147
GEN-2017-133 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.0979 | 13.0883 | -0.0096
GEN-2017-133 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 12.57 | 12.5578 | -0.0122
GEN-2017-133 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 20.5223 | 20.5225 | 0.0002
GEN-2017-133 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.5954 | 20.5916 | -0.0038
GEN-2017-133 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 42.8423 | 42.8437 | 0.0014
GEN-2017-133 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3322 | 22.325 | -0.0072
GEN-2017-133 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 32.607 | 32.598 | -0.009
GEN-2017-133 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 25.4815 | 25.4809 | -0.0006
GEN-2017-133 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 18.8427 | 18.8401 | -0.0026
GEN-2017-133 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 19.7338 | 19.7308 | -0.003
GEN-2017-133 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 50.9047 | 50.9051 | 0.0004
GEN-2017-133 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 23.591 | 23.5905 | -0.0005
GEN-2017-133 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7829 | 31.7758 | -0.0071
GEN-2017-133 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 61.2656 | 61.2694 | 0.0038
GEN-2017-133 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 23.9112 | 23.9059 | -0.0053
GEN-2017-133 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 49.283 | 49.2749 | -0.0081
GEN-2017-133 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2916 | 29.2864 | -0.0052
GEN-2017-133 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 22.892 | 22.8924 | 0.0004
GEN-2017-133 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.4937 | 29.4868 | -0.0069
GEN-2017-133 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 29.0018 | 28.9966 | -0.0052
GEN-2017-133 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 24.9244 | 24.924 | -0.0004
GEN-2017-133 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 34.2202 | 34.2206 | 0.0004
GEN-2017-133 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 26.9864 | 26.987 | 0.0006
GEN-2017-133 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.0381 | 24.0314 | -0.0067
GEN-2017-133 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 29.9824 | 29.9822 | -0.0002
GEN-2017-133 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 17.784 | 17.7814 | -0.0026
GEN-2017-133 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.6954 | 22.6892 | -0.0062
GEN-2017-133 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.0915 | 33.0888 | -0.0027
GEN-2017-133 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 51.805 | 51.8057 | 0.0007
GEN-2017-133 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 23.3753 | 23.3747 | -0.0006
GEN-2017-133 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.3453 | 23.3416 | -0.0037
GEN-2017-133 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.0345 | 28.0306 | -0.0039
GEN-2017-133 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.664 | 11.6586 | -0.0054
GEN-2017-133 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.0789 | 19.0791 | 0.0002
GEN-2017-133 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.6266 | 9.6179 | -0.0087
GEN-2017-133 | 04 SOUTHEAST | 510877 | FIXCT4 | 138 | 7.9849 | 7.9815 | -0.0034
GEN-2017-133 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8813 | 6.8769 | -0.0044
GEN-2017-133 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.387 | 11.3845 | -0.0025
GEN-2017-133 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5694 | 3.5657 | -0.0037
GEN-2017-133 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 9.8907 | 9.8889 | -0.0018
GEN-2017-133 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0409 | 14.0275 | -0.0134
GEN-2017-133 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.5418 | 7.5345 | -0.0073
GEN-2017-133 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2953 | 13.2777 | -0.0176
GEN-2017-133 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 14.9131 | 14.8996 | -0.0135
GEN-2017-133 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.7997 | 13.7865 | -0.0132
GEN-2017-133 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.3193 | 13.311 | -0.0083
GEN-2017-133 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.419 | 8.4157 | -0.0033
GEN-2017-133 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.8115 | 9.8057 | -0.0058
GEN-2017-133 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5815 | 10.5801 | -0.0014
GEN-2017-133 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 16.9285 | 16.9275 | -0.001
GEN-2017-133 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4185 | 10.4172 | -0.0013
GEN-2017-133 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.5975 | 6.5969 | -0.0006
GEN-2017-133 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.4591 | 10.455 | -0.0041
GEN-2017-133 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.9438 | 6.9428 | -0.001
GEN-2017-133 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 22.9513 | 22.9513 | 0
GEN-2017-133 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.5767 | 11.5768 | 0.0001
GEN-2017-133 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.9078 | 19.9034 | -0.0044
GEN-2017-133 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 17.024 | 17.0202 | -0.0038
GEN-2017-133 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.4071 | 21.4024 | -0.0047
GEN-2017-133 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.9191 | 20.9135 | -0.0056
GEN-2017-133 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.2345 | 8.2308 | -0.0037
GEN-2017-133 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7546 | 23.7553 | 0.0007
GEN-2017-133 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.5567 | 32.5575 | 0.0008
GEN-2017-133 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3936 | 29.381 | -0.0126
GEN-2017-133 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9298 | 15.9196 | -0.0102
GEN-2017-133 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1713 | 11.1642 | -0.0071
GEN-2017-133 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.5512 | 7.55 | -0.0012
GEN-2017-133 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.2539 | 17.252 | -0.0019
GEN-2017-133 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.7164 | 18.7141 | -0.0023
GEN-2017-133 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 15.8099 | 15.808 | -0.0019
GEN-2017-133 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5431 | 18.5361 | -0.007
GEN-2017-133 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 27.4404 | 27.4391 | -0.0013
GEN-2017-133 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.5066 | 12.4993 | -0.0073
GEN-2017-133 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.2236 | 9.2171 | -0.0065
GEN-2017-133 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 14.8278 | 14.8223 | -0.0055
GEN-2017-133 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 26.8063 | 26.8057 | -0.0006
GEN-2017-133 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 27.91 | 27.9091 | -0.0009
GEN-2017-133 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.2332 | 21.2318 | -0.0014
GEN-2017-133 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 33.223 | 33.2269 | 0.0039
GEN-2017-133 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 30.5288 | 30.5292 | 0.0004
GEN-2017-133 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 34.1381 | 34.1397 | 0.0016
GEN-2017-133 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 37.5959 | 37.6002 | 0.0043
GEN-2017-133 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.7921 | 32.7917 | -0.0004
GEN-2017-133 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 22.6252 | 22.6228 | -0.0024
GEN-2017-133 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6193 | 27.6188 | -0.0005
GEN-2017-133 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.338 | 23.3345 | -0.0035
GEN-2017-133 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.0725 | 28.0702 | -0.0023
GEN-2017-133 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.9919 | 45.9997 | 0.0078
GEN-2017-133 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2995 | 34.3238 | 0.0243
GEN-2017-133 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1358 | 24.1374 | 0.0016
GEN-2017-133 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 21.4753 | 21.4786 | 0.0033
GEN-2017-133 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 30.9278 | 30.9327 | 0.0049
GEN-2017-133 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.5971 | 29.6006 | 0.0035
GEN-2017-133 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.1303 | 20.1299 | -0.0004
GEN-2017-133 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.7172 | 46.7216 | 0.0044
GEN-2017-133 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8408 | 36.8533 | 0.0125
GEN-2017-133 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 36.609 | 36.6149 | 0.0059
GEN-2017-133 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8446 | 20.8437 | -0.0009
GEN-2017-133 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.264 | 42.338 | 0.074
GEN-2017-133 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.1903 | 27.375 | 0.1847
GEN-2017-133 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.2692 | 26.4422 | 0.173
GEN-2017-133 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 11.4111 | 11.413 | 0.0019
GEN-2017-133 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4408 | 45.4476 | 0.0068
GEN-2017-133 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.6442 | 21.6438 | -0.0004
GEN-2017-133 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7392 | 42.7454 | 0.0062
GEN-2017-133 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0061 | 26.0139 | 0.0078
GEN-2017-133 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 12.0533 | 12.0553 | 0.002
GEN-2017-133 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 42.0317 | 42.0508 | 0.0191
GEN-2017-133 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.6818 | 34.6837 | 0.0019
GEN-2017-133 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 23.9763 | 23.976 | -0.0003
GEN-2017-133 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.0523 | 23.0521 | -0.0002
GEN-2017-133 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.9624 | 36.9658 | 0.0034
GEN-2017-133 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.7276 | 22.7277 | 0.0001
GEN-2017-133 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.2902 | 20.2908 | 0.0006
GEN-2017-133 | 04 SOUTHEAST | 514964 | NE10TH 4 | 138 | 18.4023 | 18.404 | 0.0017
GEN-2017-133 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 18.4912 | 18.4939 | 0.0027
GEN-2017-133 | 04 SOUTHEAST | 514973 | RENO 4 | 138 | 28.3532 | 28.3579 | 0.0047
GEN-2017-133 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 13.6751 | 13.6751 | 0
GEN-2017-133 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 14.0407 | 14.0411 | 0.0004
GEN-2017-133 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 30.6418 | 30.6445 | 0.0027
GEN-2017-133 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 15.6375 | 15.6378 | 0.0003
GEN-2017-133 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.2829 | 14.2828 | -0.0001
GEN-2017-133 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.4839 | 16.484 | 0.0001
GEN-2017-133 | 04 SOUTHEAST | 515004 | ROSEDAL2 | 69 | 4.5594 | 4.5586 | -0.0008
GEN-2017-133 | 04 SOUTHEAST | 515008 | KINZE 4 | 138 | 14.0799 | 14.0723 | -0.0076
GEN-2017-133 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.7794 | 40.7859 | 0.0065
GEN-2017-133 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4492 | 28.4632 | 0.014
GEN-2017-133 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 16.9215 | 16.9207 | -0.0008
GEN-2017-133 | 04 SOUTHEAST | 515053 | PEARSNT2 | 69 | 4.3105 | 4.3096 | -0.0009
GEN-2017-133 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 10.6689 | 10.6669 | -0.002
GEN-2017-133 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3291 | 20.3269 | -0.0022
GEN-2017-133 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.0842 | 14.0835 | -0.0007
GEN-2017-133 | 04 SOUTHEAST | 515073 | ERLSBOR2 | 69 | 8.2334 | 8.2305 | -0.0029
GEN-2017-133 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.1724 | 11.1713 | -0.0011
GEN-2017-133 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 13.9888 | 13.9878 | -0.001
GEN-2017-133 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.5636 | 9.5624 | -0.0012
GEN-2017-133 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 8.6741 | 8.6722 | -0.0019
GEN-2017-133 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.506 | 10.5045 | -0.0015
GEN-2017-133 | 04 SOUTHEAST | 515101 | PAULSVL2 | 69 | 5.812 | 5.8104 | -0.0016
GEN-2017-133 | 04 SOUTHEAST | 515113 | CHIGLEY2 | 69 | 6.9486 | 6.9462 | -0.0024
GEN-2017-133 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.2267 | 8.2244 | -0.0023
GEN-2017-133 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.1743 | 6.1717 | -0.0026
GEN-2017-133 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.0505 | 16.0452 | -0.0053
GEN-2017-133 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6218 | 11.6142 | -0.0076
GEN-2017-133 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.1519 | 11.1455 | -0.0064
GEN-2017-133 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.3132 | 11.3066 | -0.0066
GEN-2017-133 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 12.9501 | 12.9458 | -0.0043
GEN-2017-133 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.2918 | 6.2902 | -0.0016
GEN-2017-133 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 10.6625 | 10.6599 | -0.0026
GEN-2017-133 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.204 | 20.1906 | -0.0134
GEN-2017-133 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9648 | 11.9562 | -0.0086
GEN-2017-133 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.2927 | 9.287 | -0.0057
GEN-2017-133 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.3895 | 8.3852 | -0.0043
GEN-2017-133 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.388 | 13.3853 | -0.0027
GEN-2017-133 | 04 SOUTHEAST | 515177 | PARKLN 2 | 69 | 14.446 | 14.4423 | -0.0037
GEN-2017-133 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.5896 | 16.5864 | -0.0032
GEN-2017-133 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.2706 | 27.272 | 0.0014
GEN-2017-133 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 15.655 | 15.6503 | -0.0047
GEN-2017-133 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.2068 | 14.2022 | -0.0046
GEN-2017-133 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 9.758 | 9.7544 | -0.0036
GEN-2017-133 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.2673 | 21.2622 | -0.0051
GEN-2017-133 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2613 | 21.2592 | -0.0021
GEN-2017-133 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 13.9274 | 13.9265 | -0.0009
GEN-2017-133 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 23.4479 | 23.4275 | -0.0204
GEN-2017-133 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.3176 | 23.2972 | -0.0204
GEN-2017-133 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.146 | 10.1315 | -0.0145
GEN-2017-133 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.539 | 8.5315 | -0.0075
GEN-2017-133 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.3242 | 16.3106 | -0.0136
GEN-2017-133 | 04 SOUTHEAST | 515318 | SOTHADA4 | 138 | 11.5389 | 11.5357 | -0.0032
GEN-2017-133 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.4206 | 14.4148 | -0.0058
GEN-2017-133 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3548 | 22.3446 | -0.0102
GEN-2017-133 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 25.2341 | 25.2247 | -0.0094
GEN-2017-133 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.8477 | 10.843 | -0.0047
GEN-2017-133 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2259 | 18.2176 | -0.0083
GEN-2017-133 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.195 | 10.1886 | -0.0064
GEN-2017-133 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 15.0203 | 15.0175 | -0.0028
GEN-2017-133 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.6582 | 23.6589 | 0.0007
GEN-2017-133 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5372 | 12.5308 | -0.0064
GEN-2017-133 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.6811 | 20.6817 | 0.0006
GEN-2017-133 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 26.9093 | 26.9119 | 0.0026
GEN-2017-133 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2148 | 40.2784 | 0.0636
GEN-2017-133 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6081 | 21.6107 | 0.0026
GEN-2017-133 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 22.1486 | 22.1448 | -0.0038
GEN-2017-133 | 04 SOUTHEAST | 515467 | WHITESB4 | 138 | 15.9568 | 15.9515 | -0.0053
GEN-2017-133 | 04 SOUTHEAST | 515468 | FAIRFLD4 | 138 | 23.8665 | 23.864 | -0.0025
GEN-2017-133 | 04 SOUTHEAST | 515469 | HAFERSB4 | 138 | 24.1346 | 24.1327 | -0.0019
GEN-2017-133 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 24.4939 | 24.4931 | -0.0008
GEN-2017-133 | 04 SOUTHEAST | 515475 | PURCELL4 | 138 | 10.2166 | 10.2154 | -0.0012
GEN-2017-133 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.1951 | 14.1875 | -0.0076
GEN-2017-133 | 04 SOUTHEAST | 515480 | JONESSB4 | 138 | 29.3348 | 29.3406 | 0.0058
GEN-2017-133 | 04 SOUTHEAST | 515496 | KNAWATP2 | 69 | 4.4108 | 4.41 | -0.0008
GEN-2017-133 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8751 | 34.8833 | 0.0082
GEN-2017-133 | 04 SOUTHEAST | 515503 | LTRIVRT2 | 69 | 4.6867 | 4.6855 | -0.0012
GEN-2017-133 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.5162 | 13.5135 | -0.0027
GEN-2017-133 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7343 | 14.7334 | -0.0009
GEN-2017-133 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 14.558 | 14.5531 | -0.0049
GEN-2017-133 | 04 SOUTHEAST | 515570 | MAYSVLT4 | 138 | 5.9334 | 5.9317 | -0.0017
GEN-2017-133 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.9465 | 14.9364 | -0.0101
GEN-2017-133 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7086 | 8.7044 | -0.0042
GEN-2017-133 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.2529 | 14.2459 | -0.007
GEN-2017-133 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.5589 | 13.5526 | -0.0063
GEN-2017-133 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.2247 | 12.2222 | -0.0025
GEN-2017-133 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.3364 | 13.3343 | -0.0021
GEN-2017-133 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3404 | 18.3389 | -0.0015
GEN-2017-133 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3764 | 19.3737 | -0.0027
GEN-2017-133 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.9156 | 33.9154 | -0.0002
GEN-2017-133 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6809 | 14.6681 | -0.0128
GEN-2017-133 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.9607 | 18.9562 | -0.0045
GEN-2017-133 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.9561 | 18.9517 | -0.0044
GEN-2017-133 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 11.8301 | 11.825 | -0.0051
GEN-2017-133 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.5062 | 10.5052 | -0.001
GEN-2017-133 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.2786 | 14.2753 | -0.0033
GEN-2017-133 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 5.822 | 5.8212 | -0.0008
GEN-2017-133 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8663 | 39.8724 | 0.0061
GEN-2017-133 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.3724 | 7.3707 | -0.0017
GEN-2017-133 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.985 | 7.9804 | -0.0046
GEN-2017-133 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.7543 | 17.7518 | -0.0025
GEN-2017-133 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16.0005 | 15.9928 | -0.0077
GEN-2017-133 | 04 SOUTHEAST | 520540 | TWNLAKE4 | 138 | 10.1112 | 10.1072 | -0.004
GEN-2017-133 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3829 | 22.3812 | -0.0017
GEN-2017-133 | 04 SOUTHEAST | 520847 | TWNLKJT4 | 138 | 7.6166 | 7.6136 | -0.003
GEN-2017-133 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 29.89 | 29.8899 | -0.0001
GEN-2017-133 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.6899 | 22.6904 | 0.0005
GEN-2017-133 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 12.5995 | 12.5984 | -0.0011
GEN-2017-133 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.2345 | 8.2308 | -0.0037
GEN-2017-133 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.1112 | 10.1072 | -0.004
GEN-2017-133 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3069 | 11.2948 | -0.0121
GEN-2017-133 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1867 | 27.1936 | 0.0069
GEN-2017-133 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.575 | 19.5659 | -0.0091
GEN-2017-133 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.4731 | 9.4705 | -0.0026
GEN-2017-133 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.0925 | 8.0836 | -0.0089
GEN-2017-133 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5929 | 10.5911 | -0.0018
GEN-2017-133 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 8.0107 | 8.0069 | -0.0038
GEN-2017-133 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.9243 | 15.9213 | -0.003
GEN-2017-133 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.3713 | 16.3642 | -0.0071
GEN-2017-133 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.1573 | 10.1531 | -0.0042
GEN-2017-133 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.7654 | 8.7618 | -0.0036
GEN-2017-133 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 31.7829 | 31.7758 | -0.0071
GEN-2017-133 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 17.466 | 17.4606 | -0.0054
GEN-2017-133 | 04 SOUTHEAST | 588041 | G16133_765GS | 765 | 6.2075 | 6.2054 | -0.0021
GEN-2017-133 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 13.2358 | 13.2313 | -0.0045
GEN-2017-133 | 04 SOUTHEAST | 588834 | FWL-WND-SWYD | 345 | 11.3312 | 11.3287 | -0.0025
GEN-2017-133 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 11.3312 | 11.3287 | -0.0025
GEN-2017-133 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3312 | 11.3287 | -0.0025
GEN-2017-133 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 9.9721 | 9.9699 | -0.0022
GEN-2017-133 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.5289 | 10.5253 | -0.0036
GEN-2017-133 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.0281 | 6.2923 | 0.2642
GEN-2017-133 | 04 SOUTHEAST | 760368 | GEN-2017-213 | 345 | 16.7997 | 16.7965 | -0.0032
GEN-2017-133 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 4.5359 | 4.5353 | -0.0006
GEN-2017-133 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 4.4416 | 4.4411 | -0.0005
GEN-2017-133 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1582 | 4.1567 | -0.0015
GEN-2017-133 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.793 | 3.7918 | -0.0012
GEN-2017-133 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.9211 | 22.9216 | 0.0005
GEN-2017-133 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.9663 | 22.9668 | 0.0005
GEN-2017-133 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.089 | 12.0893 | 0.0003
GEN-2017-133 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9678 | 2.9648 | -0.003
GEN-2017-133 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.9503 | 6.9453 | -0.005
GEN-2017-133 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9866 | 11.9832 | -0.0034
GEN-2017-133 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0589 | 7.0577 | -0.0012
GEN-2017-133 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.6648 | 5.6641 | -0.0007
GEN-2017-133 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.316 | 6.3151 | -0.0009
GEN-2017-133 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 36.2911 | 36.2969 | 0.0058
GEN-2017-134 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.2387 | 8.2319 | -0.0068
GEN-2017-134 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 20.6871 | 20.6863 | -0.0008
GEN-2017-134 | 04 SOUTHEAST | 300856 | 2LUTHER | 69 | 6.5234 | 6.5199 | -0.0035
GEN-2017-134 | 04 SOUTHEAST | 301372 | 4LUTHERD | 138 | 8.2284 | 8.2216 | -0.0068
GEN-2017-134 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 20.4841 | 20.483 | -0.0011
GEN-2017-134 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 17.7576 | 17.758 | 0.0004
GEN-2017-134 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 23.534 | 23.5251 | -0.0089
GEN-2017-134 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.19 | 10.1829 | -0.0071
GEN-2017-134 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.1748 | 9.1687 | -0.0061
GEN-2017-134 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 8.9046 | 8.9003 | -0.0043
GEN-2017-134 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 24.6893 | 24.671 | -0.0183
GEN-2017-134 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.1002 | 13.0883 | -0.0119
GEN-2017-134 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 12.573 | 12.5578 | -0.0152
GEN-2017-134 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 20.5222 | 20.5225 | 0.0003
GEN-2017-134 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.5963 | 20.5916 | -0.0047
GEN-2017-134 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 42.8419 | 42.8437 | 0.0018
GEN-2017-134 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3338 | 22.325 | -0.0088
GEN-2017-134 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 32.6091 | 32.598 | -0.0111
GEN-2017-134 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 25.4817 | 25.4809 | -0.0008
GEN-2017-134 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 18.8433 | 18.8401 | -0.0032
GEN-2017-134 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 19.7345 | 19.7308 | -0.0037
GEN-2017-134 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 50.9046 | 50.9051 | 0.0005
GEN-2017-134 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 23.5911 | 23.5905 | -0.0006
GEN-2017-134 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7844 | 31.7758 | -0.0086
GEN-2017-134 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 61.2646 | 61.2694 | 0.0048
GEN-2017-134 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 23.9125 | 23.9059 | -0.0066
GEN-2017-134 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 49.2849 | 49.2749 | -0.01
GEN-2017-134 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2928 | 29.2864 | -0.0064
GEN-2017-134 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 22.8919 | 22.8924 | 0.0005
GEN-2017-134 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.4952 | 29.4868 | -0.0084
GEN-2017-134 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 29.003 | 28.9966 | -0.0064
GEN-2017-134 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 24.9245 | 24.924 | -0.0005
GEN-2017-134 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 34.2201 | 34.2206 | 0.0005
GEN-2017-134 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 26.9863 | 26.987 | 0.0007
GEN-2017-134 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.0397 | 24.0314 | -0.0083
GEN-2017-134 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 29.9825 | 29.9822 | -0.0003
GEN-2017-134 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 17.7847 | 17.7814 | -0.0033
GEN-2017-134 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.6968 | 22.6892 | -0.0076
GEN-2017-134 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.0921 | 33.0888 | -0.0033
GEN-2017-134 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 51.8048 | 51.8057 | 0.0009
GEN-2017-134 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 23.3754 | 23.3747 | -0.0007
GEN-2017-134 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.3462 | 23.3416 | -0.0046
GEN-2017-134 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.0354 | 28.0306 | -0.0048
GEN-2017-134 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.6654 | 11.6586 | -0.0068
GEN-2017-134 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.0788 | 19.0791 | 0.0003
GEN-2017-134 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.6288 | 9.6179 | -0.0109
GEN-2017-134 | 04 SOUTHEAST | 510877 | FIXCT4 | 138 | 7.9857 | 7.9815 | -0.0042
GEN-2017-134 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8824 | 6.8769 | -0.0055
GEN-2017-134 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.3875 | 11.3845 | -0.003
GEN-2017-134 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5703 | 3.5657 | -0.0046
GEN-2017-134 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 9.8911 | 9.8889 | -0.0022
GEN-2017-134 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0442 | 14.0275 | -0.0167
GEN-2017-134 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.5436 | 7.5345 | -0.0091
GEN-2017-134 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2996 | 13.2777 | -0.0219
GEN-2017-134 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 14.9164 | 14.8996 | -0.0168
GEN-2017-134 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.8029 | 13.7865 | -0.0164
GEN-2017-134 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.3214 | 13.311 | -0.0104
GEN-2017-134 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.4198 | 8.4157 | -0.0041
GEN-2017-134 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.8129 | 9.8057 | -0.0072
GEN-2017-134 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5818 | 10.5801 | -0.0017
GEN-2017-134 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 16.9287 | 16.9275 | -0.0012
GEN-2017-134 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4188 | 10.4172 | -0.0016
GEN-2017-134 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.5976 | 6.5969 | -0.0007
GEN-2017-134 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.4602 | 10.455 | -0.0052
GEN-2017-134 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.9441 | 6.9428 | -0.0013
GEN-2017-134 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 22.9507 | 22.9513 | 0.0006
GEN-2017-134 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.5766 | 11.5768 | 0.0002
GEN-2017-134 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.9087 | 19.9034 | -0.0053
GEN-2017-134 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 17.0248 | 17.0202 | -0.0046
GEN-2017-134 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.408 | 21.4024 | -0.0056
GEN-2017-134 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.9199 | 20.9135 | -0.0064
GEN-2017-134 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.2353 | 8.2308 | -0.0045
GEN-2017-134 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7542 | 23.7553 | 0.0011
GEN-2017-134 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.5565 | 32.5575 | 0.001
GEN-2017-134 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3961 | 29.381 | -0.0151
GEN-2017-134 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9323 | 15.9196 | -0.0127
GEN-2017-134 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.173 | 11.1642 | -0.0088
GEN-2017-134 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.5515 | 7.55 | -0.0015
GEN-2017-134 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.2543 | 17.252 | -0.0023
GEN-2017-134 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.7168 | 18.7141 | -0.0027
GEN-2017-134 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 15.8103 | 15.808 | -0.0023
GEN-2017-134 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5445 | 18.5361 | -0.0084
GEN-2017-134 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 27.4402 | 27.4391 | -0.0011
GEN-2017-134 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.5082 | 12.4993 | -0.0089
GEN-2017-134 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.2251 | 9.2171 | -0.008
GEN-2017-134 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 14.829 | 14.8223 | -0.0067
GEN-2017-134 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 26.8058 | 26.8057 | -0.0001
GEN-2017-134 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 27.9096 | 27.9091 | -0.0005
GEN-2017-134 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.2332 | 21.2318 | -0.0014
GEN-2017-134 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 33.2215 | 33.2269 | 0.0054
GEN-2017-134 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 30.5283 | 30.5292 | 0.0009
GEN-2017-134 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 34.1372 | 34.1397 | 0.0025
GEN-2017-134 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 37.5943 | 37.6002 | 0.0059
GEN-2017-134 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.7916 | 32.7917 | 0.0001
GEN-2017-134 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 22.6256 | 22.6228 | -0.0028
GEN-2017-134 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6192 | 27.6188 | -0.0004
GEN-2017-134 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.3385 | 23.3345 | -0.004
GEN-2017-134 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.0726 | 28.0702 | -0.0024
GEN-2017-134 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.9889 | 45.9997 | 0.0108
GEN-2017-134 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2922 | 34.3238 | 0.0316
GEN-2017-134 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1347 | 24.1374 | 0.0027
GEN-2017-134 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 21.4744 | 21.4786 | 0.0042
GEN-2017-134 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 30.9265 | 30.9327 | 0.0062
GEN-2017-134 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.596 | 29.6006 | 0.0046
GEN-2017-134 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.1303 | 20.1299 | -0.0004
GEN-2017-134 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.7156 | 46.7216 | 0.006
GEN-2017-134 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8369 | 36.8533 | 0.0164
GEN-2017-134 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 36.6074 | 36.6149 | 0.0075
GEN-2017-134 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8444 | 20.8437 | -0.0007
GEN-2017-134 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.2432 | 42.338 | 0.0948
GEN-2017-134 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.1409 | 27.375 | 0.2341
GEN-2017-134 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.2237 | 26.4422 | 0.2185
GEN-2017-134 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 11.4107 | 11.413 | 0.0023
GEN-2017-134 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4388 | 45.4476 | 0.0088
GEN-2017-134 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.6442 | 21.6438 | -0.0004
GEN-2017-134 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7373 | 42.7454 | 0.0081
GEN-2017-134 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0038 | 26.0139 | 0.0101
GEN-2017-134 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 12.0527 | 12.0553 | 0.0026
GEN-2017-134 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 42.0267 | 42.0508 | 0.0241
GEN-2017-134 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.6811 | 34.6837 | 0.0026
GEN-2017-134 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 23.9763 | 23.976 | -0.0003
GEN-2017-134 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.0523 | 23.0521 | -0.0002
GEN-2017-134 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.9614 | 36.9658 | 0.0044
GEN-2017-134 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.7275 | 22.7277 | 0.0002
GEN-2017-134 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.29 | 20.2908 | 0.0008
GEN-2017-134 | 04 SOUTHEAST | 514964 | NE10TH 4 | 138 | 18.4018 | 18.404 | 0.0022
GEN-2017-134 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 18.4904 | 18.4939 | 0.0035
GEN-2017-134 | 04 SOUTHEAST | 514973 | RENO 4 | 138 | 28.3518 | 28.3579 | 0.0061
GEN-2017-134 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 13.6751 | 13.6751 | 0
GEN-2017-134 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 14.0406 | 14.0411 | 0.0005
GEN-2017-134 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 30.641 | 30.6445 | 0.0035
GEN-2017-134 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 15.6374 | 15.6378 | 0.0004
GEN-2017-134 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.2829 | 14.2828 | -0.0001
GEN-2017-134 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.4838 | 16.484 | 0.0002
GEN-2017-134 | 04 SOUTHEAST | 515004 | ROSEDAL2 | 69 | 4.5596 | 4.5586 | -0.001
GEN-2017-134 | 04 SOUTHEAST | 515008 | KINZE 4 | 138 | 14.0818 | 14.0723 | -0.0095
GEN-2017-134 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.7777 | 40.7859 | 0.0082
GEN-2017-134 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4454 | 28.4632 | 0.0178
GEN-2017-134 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 16.9216 | 16.9207 | -0.0009
GEN-2017-134 | 04 SOUTHEAST | 515053 | PEARSNT2 | 69 | 4.3108 | 4.3096 | -0.0012
GEN-2017-134 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 10.6694 | 10.6669 | -0.0025
GEN-2017-134 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3295 | 20.3269 | -0.0026
GEN-2017-134 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.0844 | 14.0835 | -0.0009
GEN-2017-134 | 04 SOUTHEAST | 515073 | ERLSBOR2 | 69 | 8.2341 | 8.2305 | -0.0036
GEN-2017-134 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.1727 | 11.1713 | -0.0014
GEN-2017-134 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 13.989 | 13.9878 | -0.0012
GEN-2017-134 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.5638 | 9.5624 | -0.0014
GEN-2017-134 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 8.6746 | 8.6722 | -0.0024
GEN-2017-134 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.5064 | 10.5045 | -0.0019
GEN-2017-134 | 04 SOUTHEAST | 515101 | PAULSVL2 | 69 | 5.8123 | 5.8104 | -0.0019
GEN-2017-134 | 04 SOUTHEAST | 515113 | CHIGLEY2 | 69 | 6.9491 | 6.9462 | -0.0029
GEN-2017-134 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.2272 | 8.2244 | -0.0028
GEN-2017-134 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.1749 | 6.1717 | -0.0032
GEN-2017-134 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.0518 | 16.0452 | -0.0066
GEN-2017-134 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6236 | 11.6142 | -0.0094
GEN-2017-134 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.1535 | 11.1455 | -0.008
GEN-2017-134 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.3148 | 11.3066 | -0.0082
GEN-2017-134 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 12.9511 | 12.9458 | -0.0053
GEN-2017-134 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.2922 | 6.2902 | -0.002
GEN-2017-134 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 10.6631 | 10.6599 | -0.0032
GEN-2017-134 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.2073 | 20.1906 | -0.0167
GEN-2017-134 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9669 | 11.9562 | -0.0107
GEN-2017-134 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.2941 | 9.287 | -0.0071
GEN-2017-134 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.3905 | 8.3852 | -0.0053
GEN-2017-134 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.3886 | 13.3853 | -0.0033
GEN-2017-134 | 04 SOUTHEAST | 515177 | PARKLN 2 | 69 | 14.4468 | 14.4423 | -0.0045
GEN-2017-134 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.5904 | 16.5864 | -0.004
GEN-2017-134 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.2702 | 27.272 | 0.0018
GEN-2017-134 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 15.6561 | 15.6503 | -0.0058
GEN-2017-134 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.2079 | 14.2022 | -0.0057
GEN-2017-134 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 9.7589 | 9.7544 | -0.0045
GEN-2017-134 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.2685 | 21.2622 | -0.0063
GEN-2017-134 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2618 | 21.2592 | -0.0026
GEN-2017-134 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 13.9275 | 13.9265 | -0.001
GEN-2017-134 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 23.4528 | 23.4275 | -0.0253
GEN-2017-134 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.3226 | 23.2972 | -0.0254
GEN-2017-134 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.1496 | 10.1315 | -0.0181
GEN-2017-134 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.5408 | 8.5315 | -0.0093
GEN-2017-134 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.3275 | 16.3106 | -0.0169
GEN-2017-134 | 04 SOUTHEAST | 515318 | SOTHADA4 | 138 | 11.5397 | 11.5357 | -0.004
GEN-2017-134 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.4219 | 14.4148 | -0.0071
GEN-2017-134 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3573 | 22.3446 | -0.0127
GEN-2017-134 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 25.2364 | 25.2247 | -0.0117
GEN-2017-134 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.8487 | 10.843 | -0.0057
GEN-2017-134 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2278 | 18.2176 | -0.0102
GEN-2017-134 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1965 | 10.1886 | -0.0079
GEN-2017-134 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 15.021 | 15.0175 | -0.0035
GEN-2017-134 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.6578 | 23.6589 | 0.0011
GEN-2017-134 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5386 | 12.5308 | -0.0078
GEN-2017-134 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.6808 | 20.6817 | 0.0009
GEN-2017-134 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 26.9083 | 26.9119 | 0.0036
GEN-2017-134 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.1967 | 40.2784 | 0.0817
GEN-2017-134 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6068 | 21.6107 | 0.0039
GEN-2017-134 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 22.1491 | 22.1448 | -0.0043
GEN-2017-134 | 04 SOUTHEAST | 515467 | WHITESB4 | 138 | 15.9579 | 15.9515 | -0.0064
GEN-2017-134 | 04 SOUTHEAST | 515468 | FAIRFLD4 | 138 | 23.8667 | 23.864 | -0.0027
GEN-2017-134 | 04 SOUTHEAST | 515469 | HAFERSB4 | 138 | 24.1346 | 24.1327 | -0.0019
GEN-2017-134 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 24.494 | 24.4931 | -0.0009
GEN-2017-134 | 04 SOUTHEAST | 515475 | PURCELL4 | 138 | 10.2169 | 10.2154 | -0.0015
GEN-2017-134 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.1967 | 14.1875 | -0.0092
GEN-2017-134 | 04 SOUTHEAST | 515480 | JONESSB4 | 138 | 29.333 | 29.3406 | 0.0076
GEN-2017-134 | 04 SOUTHEAST | 515496 | KNAWATP2 | 69 | 4.411 | 4.41 | -0.001
GEN-2017-134 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8722 | 34.8833 | 0.0111
GEN-2017-134 | 04 SOUTHEAST | 515503 | LTRIVRT2 | 69 | 4.687 | 4.6855 | -0.0015
GEN-2017-134 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.5168 | 13.5135 | -0.0033
GEN-2017-134 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7344 | 14.7334 | -0.001
GEN-2017-134 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 14.5592 | 14.5531 | -0.0061
GEN-2017-134 | 04 SOUTHEAST | 515570 | MAYSVLT4 | 138 | 5.9338 | 5.9317 | -0.0021
GEN-2017-134 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.9488 | 14.9364 | -0.0124
GEN-2017-134 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7095 | 8.7044 | -0.0051
GEN-2017-134 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.2545 | 14.2459 | -0.0086
GEN-2017-134 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.5604 | 13.5526 | -0.0078
GEN-2017-134 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.2251 | 12.2222 | -0.0029
GEN-2017-134 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.3368 | 13.3343 | -0.0025
GEN-2017-134 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3405 | 18.3389 | -0.0016
GEN-2017-134 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3769 | 19.3737 | -0.0032
GEN-2017-134 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.9156 | 33.9154 | -0.0002
GEN-2017-134 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6841 | 14.6681 | -0.016
GEN-2017-134 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.9614 | 18.9562 | -0.0052
GEN-2017-134 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.9568 | 18.9517 | -0.0051
GEN-2017-134 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 11.8311 | 11.825 | -0.0061
GEN-2017-134 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.5064 | 10.5052 | -0.0012
GEN-2017-134 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.2794 | 14.2753 | -0.0041
GEN-2017-134 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 5.8222 | 5.8212 | -0.001
GEN-2017-134 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8647 | 39.8724 | 0.0077
GEN-2017-134 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.3728 | 7.3707 | -0.0021
GEN-2017-134 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.9862 | 7.9804 | -0.0058
GEN-2017-134 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.754 | 17.7518 | -0.0022
GEN-2017-134 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16.0024 | 15.9928 | -0.0096
GEN-2017-134 | 04 SOUTHEAST | 520540 | TWNLAKE4 | 138 | 10.112 | 10.1072 | -0.0048
GEN-2017-134 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3833 | 22.3812 | -0.0021
GEN-2017-134 | 04 SOUTHEAST | 520847 | TWNLKJT4 | 138 | 7.6172 | 7.6136 | -0.0036
GEN-2017-134 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 29.8898 | 29.8899 | 0.0001
GEN-2017-134 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.6898 | 22.6904 | 0.0006
GEN-2017-134 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 12.5997 | 12.5984 | -0.0013
GEN-2017-134 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.2353 | 8.2308 | -0.0045
GEN-2017-134 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.112 | 10.1072 | -0.0048
GEN-2017-134 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3099 | 11.2948 | -0.0151
GEN-2017-134 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1846 | 27.1936 | 0.009
GEN-2017-134 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5769 | 19.5659 | -0.011
GEN-2017-134 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.4737 | 9.4705 | -0.0032
GEN-2017-134 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.0946 | 8.0836 | -0.011
GEN-2017-134 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5933 | 10.5911 | -0.0022
GEN-2017-134 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 8.0115 | 8.0069 | -0.0046
GEN-2017-134 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.9249 | 15.9213 | -0.0036
GEN-2017-134 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.3728 | 16.3642 | -0.0086
GEN-2017-134 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.1582 | 10.1531 | -0.0051
GEN-2017-134 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.7661 | 8.7618 | -0.0043
GEN-2017-134 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 31.7844 | 31.7758 | -0.0086
GEN-2017-134 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 17.4672 | 17.4606 | -0.0066
GEN-2017-134 | 04 SOUTHEAST | 588041 | G16133_765GS | 765 | 6.208 | 6.2054 | -0.0026
GEN-2017-134 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 13.2369 | 13.2313 | -0.0056
GEN-2017-134 | 04 SOUTHEAST | 588834 | FWL-WND-SWYD | 345 | 11.3318 | 11.3287 | -0.0031
GEN-2017-134 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 11.3318 | 11.3287 | -0.0031
GEN-2017-134 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3318 | 11.3287 | -0.0031
GEN-2017-134 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 9.9726 | 9.9699 | -0.0027
GEN-2017-134 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.5298 | 10.5253 | -0.0045
GEN-2017-134 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 5.9621 | 6.2923 | 0.3302
GEN-2017-134 | 04 SOUTHEAST | 760368 | GEN-2017-213 | 345 | 16.8004 | 16.7965 | -0.0039
GEN-2017-134 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 4.536 | 4.5353 | -0.0007
GEN-2017-134 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 4.4417 | 4.4411 | -0.0006
GEN-2017-134 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1585 | 4.1567 | -0.0018
GEN-2017-134 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.7933 | 3.7918 | -0.0015
GEN-2017-134 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.9207 | 22.9216 | 0.0009
GEN-2017-134 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.966 | 22.9668 | 0.0008
GEN-2017-134 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.089 | 12.0893 | 0.0003
GEN-2017-134 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9686 | 2.9648 | -0.0038
GEN-2017-134 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.9515 | 6.9453 | -0.0062
GEN-2017-134 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9871 | 11.9832 | -0.0039
GEN-2017-134 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0591 | 7.0577 | -0.0014
GEN-2017-134 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.6649 | 5.6641 | -0.0008
GEN-2017-134 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3162 | 6.3151 | -0.0011
GEN-2017-134 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 36.2896 | 36.2969 | 0.0073
GEN-2017-137 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.2397 | 8.2319 | -0.0078
GEN-2017-137 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 20.6854 | 20.6863 | 0.0009
GEN-2017-137 | 04 SOUTHEAST | 300856 | 2LUTHER | 69 | 6.5239 | 6.5199 | -0.004
GEN-2017-137 | 04 SOUTHEAST | 301372 | 4LUTHERD | 138 | 8.2293 | 8.2216 | -0.0077
GEN-2017-137 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 20.4824 | 20.483 | 0.0006
GEN-2017-137 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 17.7576 | 17.758 | 0.0004
GEN-2017-137 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 23.5355 | 23.5251 | -0.0104
GEN-2017-137 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.1912 | 10.1829 | -0.0083
GEN-2017-137 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.176 | 9.1687 | -0.0073
GEN-2017-137 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 8.9054 | 8.9003 | -0.0051
GEN-2017-137 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 24.6925 | 24.671 | -0.0215
GEN-2017-137 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.1023 | 13.0883 | -0.014
GEN-2017-137 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 12.5757 | 12.5578 | -0.0179
GEN-2017-137 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 20.5222 | 20.5225 | 0.0003
GEN-2017-137 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.5971 | 20.5916 | -0.0055
GEN-2017-137 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 42.8414 | 42.8437 | 0.0023
GEN-2017-137 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3351 | 22.325 | -0.0101
GEN-2017-137 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 32.6108 | 32.598 | -0.0128
GEN-2017-137 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 25.4817 | 25.4809 | -0.0008
GEN-2017-137 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 18.8438 | 18.8401 | -0.0037
GEN-2017-137 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 19.7352 | 19.7308 | -0.0044
GEN-2017-137 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 50.9041 | 50.9051 | 0.001
GEN-2017-137 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 23.5911 | 23.5905 | -0.0006
GEN-2017-137 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7853 | 31.7758 | -0.0095
GEN-2017-137 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 61.2633 | 61.2694 | 0.0061
GEN-2017-137 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 23.9135 | 23.9059 | -0.0076
GEN-2017-137 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 49.2865 | 49.2749 | -0.0116
GEN-2017-137 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2937 | 29.2864 | -0.0073
GEN-2017-137 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 22.8918 | 22.8924 | 0.0006
GEN-2017-137 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.4961 | 29.4868 | -0.0093
GEN-2017-137 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 29.0039 | 28.9966 | -0.0073
GEN-2017-137 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 24.9246 | 24.924 | -0.0006
GEN-2017-137 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 34.2198 | 34.2206 | 0.0008
GEN-2017-137 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 26.9861 | 26.987 | 0.0009
GEN-2017-137 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.041 | 24.0314 | -0.0096
GEN-2017-137 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 29.9824 | 29.9822 | -0.0002
GEN-2017-137 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 17.7852 | 17.7814 | -0.0038
GEN-2017-137 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.6978 | 22.6892 | -0.0086
GEN-2017-137 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.0926 | 33.0888 | -0.0038
GEN-2017-137 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 51.8043 | 51.8057 | 0.0014
GEN-2017-137 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 23.3754 | 23.3747 | -0.0007
GEN-2017-137 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.3469 | 23.3416 | -0.0053
GEN-2017-137 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.0361 | 28.0306 | -0.0055
GEN-2017-137 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.6666 | 11.6586 | -0.008
GEN-2017-137 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.0787 | 19.0791 | 0.0004
GEN-2017-137 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.6307 | 9.6179 | -0.0128
GEN-2017-137 | 04 SOUTHEAST | 510877 | FIXCT4 | 138 | 7.9865 | 7.9815 | -0.005
GEN-2017-137 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8833 | 6.8769 | -0.0064
GEN-2017-137 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.388 | 11.3845 | -0.0035
GEN-2017-137 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5711 | 3.5657 | -0.0054
GEN-2017-137 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 9.8915 | 9.8889 | -0.0026
GEN-2017-137 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.047 | 14.0275 | -0.0195
GEN-2017-137 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.5452 | 7.5345 | -0.0107
GEN-2017-137 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.3034 | 13.2777 | -0.0257
GEN-2017-137 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 14.9193 | 14.8996 | -0.0197
GEN-2017-137 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.8057 | 13.7865 | -0.0192
GEN-2017-137 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.3231 | 13.311 | -0.0121
GEN-2017-137 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.4205 | 8.4157 | -0.0048
GEN-2017-137 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.8142 | 9.8057 | -0.0085
GEN-2017-137 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.582 | 10.5801 | -0.0019
GEN-2017-137 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 16.9288 | 16.9275 | -0.0013
GEN-2017-137 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.419 | 10.4172 | -0.0018
GEN-2017-137 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.5977 | 6.5969 | -0.0008
GEN-2017-137 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.461 | 10.455 | -0.006
GEN-2017-137 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.9442 | 6.9428 | -0.0014
GEN-2017-137 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 22.9479 | 22.9513 | 0.0034
GEN-2017-137 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.5765 | 11.5768 | 0.0003
GEN-2017-137 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.9093 | 19.9034 | -0.0059
GEN-2017-137 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 17.0253 | 17.0202 | -0.0051
GEN-2017-137 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.4087 | 21.4024 | -0.0063
GEN-2017-137 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.9203 | 20.9135 | -0.0068
GEN-2017-137 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.2359 | 8.2308 | -0.0051
GEN-2017-137 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7532 | 23.7553 | 0.0021
GEN-2017-137 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.5562 | 32.5575 | 0.0013
GEN-2017-137 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.398 | 29.381 | -0.017
GEN-2017-137 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9345 | 15.9196 | -0.0149
GEN-2017-137 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1745 | 11.1642 | -0.0103
GEN-2017-137 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.5517 | 7.55 | -0.0017
GEN-2017-137 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.2544 | 17.252 | -0.0024
GEN-2017-137 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.717 | 18.7141 | -0.0029
GEN-2017-137 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 15.8105 | 15.808 | -0.0025
GEN-2017-137 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5449 | 18.5361 | -0.0088
GEN-2017-137 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 27.4382 | 27.4391 | 0.0009
GEN-2017-137 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.5094 | 12.4993 | -0.0101
GEN-2017-137 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.2263 | 9.2171 | -0.0092
GEN-2017-137 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 14.8294 | 14.8223 | -0.0071
GEN-2017-137 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 26.8034 | 26.8057 | 0.0023
GEN-2017-137 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 27.9074 | 27.9091 | 0.0017
GEN-2017-137 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.2319 | 21.2318 | -0.0001
GEN-2017-137 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 33.2182 | 33.2269 | 0.0087
GEN-2017-137 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 30.5261 | 30.5292 | 0.0031
GEN-2017-137 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 34.1346 | 34.1397 | 0.0051
GEN-2017-137 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 37.5911 | 37.6002 | 0.0091
GEN-2017-137 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.7894 | 32.7917 | 0.0023
GEN-2017-137 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 22.6251 | 22.6228 | -0.0023
GEN-2017-137 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6182 | 27.6188 | 0.0006
GEN-2017-137 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.338 | 23.3345 | -0.0035
GEN-2017-137 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.0713 | 28.0702 | -0.0011
GEN-2017-137 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.9825 | 45.9997 | 0.0172
GEN-2017-137 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2803 | 34.3238 | 0.0435
GEN-2017-137 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1317 | 24.1374 | 0.0057
GEN-2017-137 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 21.473 | 21.4786 | 0.0056
GEN-2017-137 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 30.9245 | 30.9327 | 0.0082
GEN-2017-137 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.5944 | 29.6006 | 0.0062
GEN-2017-137 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.13 | 20.1299 | -0.0001
GEN-2017-137 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.7125 | 46.7216 | 0.0091
GEN-2017-137 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8303 | 36.8533 | 0.023
GEN-2017-137 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 36.6054 | 36.6149 | 0.0095
GEN-2017-137 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8426 | 20.8437 | 0.0011
GEN-2017-137 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.2122 | 42.338 | 0.1258
GEN-2017-137 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.0739 | 27.375 | 0.3011
GEN-2017-137 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.1643 | 26.4422 | 0.2779
GEN-2017-137 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 11.4102 | 11.413 | 0.0028
GEN-2017-137 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4359 | 45.4476 | 0.0117
GEN-2017-137 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.6439 | 21.6438 | -0.0001
GEN-2017-137 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7344 | 42.7454 | 0.011
GEN-2017-137 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0007 | 26.0139 | 0.0132
GEN-2017-137 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 12.0522 | 12.0553 | 0.0031
GEN-2017-137 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 42.0201 | 42.0508 | 0.0307
GEN-2017-137 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.6799 | 34.6837 | 0.0038
GEN-2017-137 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 23.9759 | 23.976 | 0.0001
GEN-2017-137 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.052 | 23.0521 | 0.0001
GEN-2017-137 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.9596 | 36.9658 | 0.0062
GEN-2017-137 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.7271 | 22.7277 | 0.0006
GEN-2017-137 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.2895 | 20.2908 | 0.0013
GEN-2017-137 | 04 SOUTHEAST | 514964 | NE10TH 4 | 138 | 18.401 | 18.404 | 0.003
GEN-2017-137 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 18.4894 | 18.4939 | 0.0045
GEN-2017-137 | 04 SOUTHEAST | 514973 | RENO 4 | 138 | 28.3498 | 28.3579 | 0.0081
GEN-2017-137 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 13.6749 | 13.6751 | 0.0002
GEN-2017-137 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 14.0403 | 14.0411 | 0.0008
GEN-2017-137 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 30.6397 | 30.6445 | 0.0048
GEN-2017-137 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 15.6371 | 15.6378 | 0.0007
GEN-2017-137 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.2827 | 14.2828 | 0.0001
GEN-2017-137 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.4835 | 16.484 | 0.0005
GEN-2017-137 | 04 SOUTHEAST | 515004 | ROSEDAL2 | 69 | 4.5597 | 4.5586 | -0.0011
GEN-2017-137 | 04 SOUTHEAST | 515008 | KINZE 4 | 138 | 14.0833 | 14.0723 | -0.011
GEN-2017-137 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.7755 | 40.7859 | 0.0104
GEN-2017-137 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4406 | 28.4632 | 0.0226
GEN-2017-137 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 16.9215 | 16.9207 | -0.0008
GEN-2017-137 | 04 SOUTHEAST | 515053 | PEARSNT2 | 69 | 4.3109 | 4.3096 | -0.0013
GEN-2017-137 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 10.6698 | 10.6669 | -0.0029
GEN-2017-137 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3298 | 20.3269 | -0.0029
GEN-2017-137 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.0844 | 14.0835 | -0.0009
GEN-2017-137 | 04 SOUTHEAST | 515073 | ERLSBOR2 | 69 | 8.2347 | 8.2305 | -0.0042
GEN-2017-137 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.1729 | 11.1713 | -0.0016
GEN-2017-137 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 13.9891 | 13.9878 | -0.0013
GEN-2017-137 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.564 | 9.5624 | -0.0016
GEN-2017-137 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 8.675 | 8.6722 | -0.0028
GEN-2017-137 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.5066 | 10.5045 | -0.0021
GEN-2017-137 | 04 SOUTHEAST | 515101 | PAULSVL2 | 69 | 5.8126 | 5.8104 | -0.0022
GEN-2017-137 | 04 SOUTHEAST | 515113 | CHIGLEY2 | 69 | 6.9496 | 6.9462 | -0.0034
GEN-2017-137 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.2277 | 8.2244 | -0.0033
GEN-2017-137 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.1755 | 6.1717 | -0.0038
GEN-2017-137 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.0529 | 16.0452 | -0.0077
GEN-2017-137 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6253 | 11.6142 | -0.0111
GEN-2017-137 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.1548 | 11.1455 | -0.0093
GEN-2017-137 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.3162 | 11.3066 | -0.0096
GEN-2017-137 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 12.952 | 12.9458 | -0.0062
GEN-2017-137 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.2925 | 6.2902 | -0.0023
GEN-2017-137 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 10.6637 | 10.6599 | -0.0038
GEN-2017-137 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.2102 | 20.1906 | -0.0196
GEN-2017-137 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9687 | 11.9562 | -0.0125
GEN-2017-137 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.2954 | 9.287 | -0.0084
GEN-2017-137 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.3915 | 8.3852 | -0.0063
GEN-2017-137 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.3891 | 13.3853 | -0.0038
GEN-2017-137 | 04 SOUTHEAST | 515177 | PARKLN 2 | 69 | 14.4476 | 14.4423 | -0.0053
GEN-2017-137 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.591 | 16.5864 | -0.0046
GEN-2017-137 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.2697 | 27.272 | 0.0023
GEN-2017-137 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 15.6571 | 15.6503 | -0.0068
GEN-2017-137 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.2088 | 14.2022 | -0.0066
GEN-2017-137 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 9.7597 | 9.7544 | -0.0053
GEN-2017-137 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.2695 | 21.2622 | -0.0073
GEN-2017-137 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2621 | 21.2592 | -0.0029
GEN-2017-137 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 13.9275 | 13.9265 | -0.001
GEN-2017-137 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 23.4572 | 23.4275 | -0.0297
GEN-2017-137 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.327 | 23.2972 | -0.0298
GEN-2017-137 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.1527 | 10.1315 | -0.0212
GEN-2017-137 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.5424 | 8.5315 | -0.0109
GEN-2017-137 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.3304 | 16.3106 | -0.0198
GEN-2017-137 | 04 SOUTHEAST | 515318 | SOTHADA4 | 138 | 11.5404 | 11.5357 | -0.0047
GEN-2017-137 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.4224 | 14.4148 | -0.0076
GEN-2017-137 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3594 | 22.3446 | -0.0148
GEN-2017-137 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 25.2384 | 25.2247 | -0.0137
GEN-2017-137 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.8495 | 10.843 | -0.0065
GEN-2017-137 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2292 | 18.2176 | -0.0116
GEN-2017-137 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1979 | 10.1886 | -0.0093
GEN-2017-137 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 15.0214 | 15.0175 | -0.0039
GEN-2017-137 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.6567 | 23.6589 | 0.0022
GEN-2017-137 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5398 | 12.5308 | -0.009
GEN-2017-137 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.6803 | 20.6817 | 0.0014
GEN-2017-137 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 26.906 | 26.9119 | 0.0059
GEN-2017-137 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.1696 | 40.2784 | 0.1088
GEN-2017-137 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6033 | 21.6107 | 0.0074
GEN-2017-137 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 22.1484 | 22.1448 | -0.0036
GEN-2017-137 | 04 SOUTHEAST | 515467 | WHITESB4 | 138 | 15.9582 | 15.9515 | -0.0067
GEN-2017-137 | 04 SOUTHEAST | 515468 | FAIRFLD4 | 138 | 23.8656 | 23.864 | -0.0016
GEN-2017-137 | 04 SOUTHEAST | 515469 | HAFERSB4 | 138 | 24.1331 | 24.1327 | -0.0004
GEN-2017-137 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 24.4941 | 24.4931 | -0.001
GEN-2017-137 | 04 SOUTHEAST | 515475 | PURCELL4 | 138 | 10.2171 | 10.2154 | -0.0017
GEN-2017-137 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.1981 | 14.1875 | -0.0106
GEN-2017-137 | 04 SOUTHEAST | 515480 | JONESSB4 | 138 | 29.3296 | 29.3406 | 0.011
GEN-2017-137 | 04 SOUTHEAST | 515496 | KNAWATP2 | 69 | 4.4112 | 4.41 | -0.0012
GEN-2017-137 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8667 | 34.8833 | 0.0166
GEN-2017-137 | 04 SOUTHEAST | 515503 | LTRIVRT2 | 69 | 4.6873 | 4.6855 | -0.0018
GEN-2017-137 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.5173 | 13.5135 | -0.0038
GEN-2017-137 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7342 | 14.7334 | -0.0008
GEN-2017-137 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 14.5603 | 14.5531 | -0.0072
GEN-2017-137 | 04 SOUTHEAST | 515570 | MAYSVLT4 | 138 | 5.9341 | 5.9317 | -0.0024
GEN-2017-137 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.9508 | 14.9364 | -0.0144
GEN-2017-137 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7103 | 8.7044 | -0.0059
GEN-2017-137 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.2558 | 14.2459 | -0.0099
GEN-2017-137 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.5617 | 13.5526 | -0.0091
GEN-2017-137 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.2253 | 12.2222 | -0.0031
GEN-2017-137 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.3368 | 13.3343 | -0.0025
GEN-2017-137 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3399 | 18.3389 | -0.001
GEN-2017-137 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3772 | 19.3737 | -0.0035
GEN-2017-137 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.9155 | 33.9154 | -0.0001
GEN-2017-137 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6869 | 14.6681 | -0.0188
GEN-2017-137 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.9616 | 18.9562 | -0.0054
GEN-2017-137 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.957 | 18.9517 | -0.0053
GEN-2017-137 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 11.832 | 11.825 | -0.007
GEN-2017-137 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.5064 | 10.5052 | -0.0012
GEN-2017-137 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.28 | 14.2753 | -0.0047
GEN-2017-137 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 5.8224 | 5.8212 | -0.0012
GEN-2017-137 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8626 | 39.8724 | 0.0098
GEN-2017-137 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.373 | 7.3707 | -0.0023
GEN-2017-137 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.9872 | 7.9804 | -0.0068
GEN-2017-137 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.7536 | 17.7518 | -0.0018
GEN-2017-137 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16.004 | 15.9928 | -0.0112
GEN-2017-137 | 04 SOUTHEAST | 520540 | TWNLAKE4 | 138 | 10.1127 | 10.1072 | -0.0055
GEN-2017-137 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3837 | 22.3812 | -0.0025
GEN-2017-137 | 04 SOUTHEAST | 520847 | TWNLKJT4 | 138 | 7.6178 | 7.6136 | -0.0042
GEN-2017-137 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 29.8892 | 29.8899 | 0.0007
GEN-2017-137 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.6897 | 22.6904 | 0.0007
GEN-2017-137 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 12.5997 | 12.5984 | -0.0013
GEN-2017-137 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.2359 | 8.2308 | -0.0051
GEN-2017-137 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.1127 | 10.1072 | -0.0055
GEN-2017-137 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3126 | 11.2948 | -0.0178
GEN-2017-137 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1816 | 27.1936 | 0.012
GEN-2017-137 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5785 | 19.5659 | -0.0126
GEN-2017-137 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.4743 | 9.4705 | -0.0038
GEN-2017-137 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.0965 | 8.0836 | -0.0129
GEN-2017-137 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5936 | 10.5911 | -0.0025
GEN-2017-137 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 8.0122 | 8.0069 | -0.0053
GEN-2017-137 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.9254 | 15.9213 | -0.0041
GEN-2017-137 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.3738 | 16.3642 | -0.0096
GEN-2017-137 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.1589 | 10.1531 | -0.0058
GEN-2017-137 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.7668 | 8.7618 | -0.005
GEN-2017-137 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 31.7853 | 31.7758 | -0.0095
GEN-2017-137 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 17.4682 | 17.4606 | -0.0076
GEN-2017-137 | 04 SOUTHEAST | 588041 | G16133_765GS | 765 | 6.2084 | 6.2054 | -0.003
GEN-2017-137 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 13.2379 | 13.2313 | -0.0066
GEN-2017-137 | 04 SOUTHEAST | 588834 | FWL-WND-SWYD | 345 | 11.3323 | 11.3287 | -0.0036
GEN-2017-137 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 11.3323 | 11.3287 | -0.0036
GEN-2017-137 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3323 | 11.3287 | -0.0036
GEN-2017-137 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 9.9731 | 9.9699 | -0.0032
GEN-2017-137 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.5305 | 10.5253 | -0.0052
GEN-2017-137 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 5.8737 | 6.2923 | 0.4186
GEN-2017-137 | 04 SOUTHEAST | 760368 | GEN-2017-213 | 345 | 16.8011 | 16.7965 | -0.0046
GEN-2017-137 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 4.5361 | 4.5353 | -0.0008
GEN-2017-137 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 4.4419 | 4.4411 | -0.0008
GEN-2017-137 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1589 | 4.1567 | -0.0022
GEN-2017-137 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.7936 | 3.7918 | -0.0018
GEN-2017-137 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.9198 | 22.9216 | 0.0018
GEN-2017-137 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.9651 | 22.9668 | 0.0017
GEN-2017-137 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.0889 | 12.0893 | 0.0004
GEN-2017-137 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9692 | 2.9648 | -0.0044
GEN-2017-137 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.9526 | 6.9453 | -0.0073
GEN-2017-137 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9875 | 11.9832 | -0.0043
GEN-2017-137 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0592 | 7.0577 | -0.0015
GEN-2017-137 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.665 | 5.6641 | -0.0009
GEN-2017-137 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3163 | 6.3151 | -0.0012
GEN-2017-137 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 36.2876 | 36.2969 | 0.0093
GEN-2017-140 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.2582 | 15.2482 | -0.01
GEN-2017-140 | 04 SOUTHEAST | 337811 | 8HAPPYVALY% | 500 | 24.8509 | 24.8493 | -0.0016
GEN-2017-140 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 17.7574 | 17.758 | 0.0006
GEN-2017-140 | 04 SOUTHEAST | 337912 | 5ANO% | 161 | 17.7701 | 17.7702 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 337922 | 8P.HILL% | 500 | 15.3621 | 15.3607 | -0.0014
GEN-2017-140 | 04 SOUTHEAST | 504010 | ELMSPRGS 5 | 161 | 18.7281 | 18.712 | -0.0161
GEN-2017-140 | 04 SOUTHEAST | 504011 | ELMSPG_1 2 | 69 | 5.5212 | 5.514 | -0.0072
GEN-2017-140 | 04 SOUTHEAST | 504013 | ELMSPG_2 2 | 69 | 7.6951 | 7.6854 | -0.0097
GEN-2017-140 | 04 SOUTHEAST | 504020 | FARMNGTN 5 | 161 | 12.5526 | 12.5413 | -0.0113
GEN-2017-140 | 04 SOUTHEAST | 504021 | FARM_1 2 | 69 | 7.0797 | 7.0715 | -0.0082
GEN-2017-140 | 04 SOUTHEAST | 504201 | GENTRY 5 | 161 | 26.8792 | 26.8853 | 0.0061
GEN-2017-140 | 04 SOUTHEAST | 504202 | SILOAMSP 5 | 161 | 19.6462 | 19.6422 | -0.004
GEN-2017-140 | 04 SOUTHEAST | 504274 | CARLEYRD 5 | 161 | 13.3268 | 13.3141 | -0.0127
GEN-2017-140 | 04 SOUTHEAST | 504275 | WEDINGTON5 | 161 | 11.8614 | 11.8508 | -0.0106
GEN-2017-140 | 04 SOUTHEAST | 506926 | DYESS 2 | 69 | 15.8242 | 15.8063 | -0.0179
GEN-2017-140 | 04 SOUTHEAST | 506927 | DYESS 5 | 161 | 17.5201 | 17.505 | -0.0151
GEN-2017-140 | 04 SOUTHEAST | 506931 | EROGERS5 | 161 | 15.0804 | 15.068 | -0.0124
GEN-2017-140 | 04 SOUTHEAST | 506934 | FLINTCR5 | 161 | 33.8926 | 33.9039 | 0.0113
GEN-2017-140 | 04 SOUTHEAST | 506935 | FLINTCR7 | 345 | 15.2904 | 15.2903 | -0.0001
GEN-2017-140 | 04 SOUTHEAST | 506938 | LOWELL 5 | 161 | 12.5 | 12.4876 | -0.0124
GEN-2017-140 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 23.5381 | 23.5251 | -0.013
GEN-2017-140 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.1949 | 10.1829 | -0.012
GEN-2017-140 | 04 SOUTHEAST | 506948 | SILOAM 5 | 161 | 22.0039 | 21.9997 | -0.0042
GEN-2017-140 | 04 SOUTHEAST | 506949 | SOSPRDL5 | 161 | 12.899 | 12.8865 | -0.0125
GEN-2017-140 | 04 SOUTHEAST | 506956 | FARMING5 | 161 | 12.422 | 12.4105 | -0.0115
GEN-2017-140 | 04 SOUTHEAST | 506957 | TONTITN5 | 161 | 23.0094 | 22.9917 | -0.0177
GEN-2017-140 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.1803 | 9.1687 | -0.0116
GEN-2017-140 | 04 SOUTHEAST | 506972 | LINCOLN2 | 69 | 4.7349 | 4.7305 | -0.0044
GEN-2017-140 | 04 SOUTHEAST | 506973 | SILOAM 2 | 69 | 11.3569 | 11.351 | -0.0059
GEN-2017-140 | 04 SOUTHEAST | 506978 | MATTISN5 | 161 | 22.5661 | 22.5484 | -0.0177
GEN-2017-140 | 04 SOUTHEAST | 506991 | BRUSHCRK_5 | 161 | 13.3339 | 13.3206 | -0.0133
GEN-2017-140 | 04 SOUTHEAST | 506992 | WEDINGTON | 161 | 16.3676 | 16.355 | -0.0126
GEN-2017-140 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.0952 | 13.0883 | -0.0069
GEN-2017-140 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 12.5666 | 12.5578 | -0.0088
GEN-2017-140 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.2805 | 12.2735 | -0.007
GEN-2017-140 | 04 SOUTHEAST | 509737 | BA101 S4 | 138 | 18.1631 | 18.1582 | -0.0049
GEN-2017-140 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.4323 | 20.5916 | 0.1593
GEN-2017-140 | 04 SOUTHEAST | 509747 | BA81---4 | 138 | 18.1891 | 18.1847 | -0.0044
GEN-2017-140 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 42.8276 | 42.8437 | 0.0161
GEN-2017-140 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3207 | 22.325 | 0.0043
GEN-2017-140 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 32.5961 | 32.598 | 0.0019
GEN-2017-140 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 25.4761 | 25.4809 | 0.0048
GEN-2017-140 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.0155 | 16.013 | -0.0025
GEN-2017-140 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 18.8448 | 18.8401 | -0.0047
GEN-2017-140 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 19.7358 | 19.7308 | -0.005
GEN-2017-140 | 04 SOUTHEAST | 509770 | LLAN WT4 | 138 | 24.3348 | 24.3287 | -0.0061
GEN-2017-140 | 04 SOUTHEAST | 509772 | FORD---4 | 138 | 18.3474 | 18.3441 | -0.0033
GEN-2017-140 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 50.8825 | 50.9051 | 0.0226
GEN-2017-140 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 23.5876 | 23.5905 | 0.0029
GEN-2017-140 | 04 SOUTHEAST | 509780 | MAYO--S4 | 138 | 21.3832 | 21.381 | -0.0022
GEN-2017-140 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7512 | 31.7758 | 0.0246
GEN-2017-140 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 61.2357 | 61.2694 | 0.0337
GEN-2017-140 | 04 SOUTHEAST | 509785 | BANNTAP4 | 138 | 18.7336 | 18.73 | -0.0036
GEN-2017-140 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 23.9141 | 23.9059 | -0.0082
GEN-2017-140 | 04 SOUTHEAST | 509790 | CATOOSA4 | 138 | 35.7043 | 35.7003 | -0.004
GEN-2017-140 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 27.1748 | 27.1688 | -0.006
GEN-2017-140 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 49.2503 | 49.2749 | 0.0246
GEN-2017-140 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2388 | 29.2864 | 0.0476
GEN-2017-140 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 22.8879 | 22.8924 | 0.0045
GEN-2017-140 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 34.889 | 34.8893 | 0.0003
GEN-2017-140 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.4667 | 29.4868 | 0.0201
GEN-2017-140 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 28.9509 | 28.9966 | 0.0457
GEN-2017-140 | 04 SOUTHEAST | 509845 | KIMCLRK4 | 138 | 22.3793 | 22.3815 | 0.0022
GEN-2017-140 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 24.9193 | 24.924 | 0.0047
GEN-2017-140 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 34.2111 | 34.2206 | 0.0095
GEN-2017-140 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 26.9808 | 26.987 | 0.0062
GEN-2017-140 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.0265 | 24.0314 | 0.0049
GEN-2017-140 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 29.9757 | 29.9822 | 0.0065
GEN-2017-140 | 04 SOUTHEAST | 509855 | 81GARN-4 | 138 | 17.765 | 17.7615 | -0.0035
GEN-2017-140 | 04 SOUTHEAST | 509861 | E41ST_E4 | 138 | 17.044 | 17.0402 | -0.0038
GEN-2017-140 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 17.7875 | 17.7814 | -0.0061
GEN-2017-140 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.6819 | 22.6892 | 0.0073
GEN-2017-140 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.0818 | 33.0888 | 0.007
GEN-2017-140 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 51.7822 | 51.8057 | 0.0235
GEN-2017-140 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 23.3707 | 23.3747 | 0.004
GEN-2017-140 | 04 SOUTHEAST | 509889 | E_121ST4 | 138 | 15.8775 | 15.8724 | -0.0051
GEN-2017-140 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.3466 | 23.3416 | -0.005
GEN-2017-140 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 34.8365 | 34.8369 | 0.0004
GEN-2017-140 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.0273 | 28.0306 | 0.0033
GEN-2017-140 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 10.9825 | 10.9769 | -0.0056
GEN-2017-140 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.6636 | 11.6586 | -0.005
GEN-2017-140 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.0712 | 19.0791 | 0.0079
GEN-2017-140 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.3858 | 11.3845 | -0.0013
GEN-2017-140 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 9.89 | 9.8889 | -0.0011
GEN-2017-140 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0355 | 14.0275 | -0.008
GEN-2017-140 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2901 | 13.2777 | -0.0124
GEN-2017-140 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 14.9092 | 14.8996 | -0.0096
GEN-2017-140 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.7943 | 13.7865 | -0.0078
GEN-2017-140 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.3163 | 13.311 | -0.0053
GEN-2017-140 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.416 | 8.4157 | -0.0003
GEN-2017-140 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.8098 | 9.8057 | -0.0041
GEN-2017-140 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.5972 | 6.5969 | -0.0003
GEN-2017-140 | 04 SOUTHEAST | 512642 | SILSPWW5 | 161 | 14.7001 | 14.6962 | -0.0039
GEN-2017-140 | 04 SOUTHEAST | 512643 | SILMCTY5 | 161 | 19.8469 | 19.8425 | -0.0044
GEN-2017-140 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.111 | 15.112 | 0.001
GEN-2017-140 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 16.7962 | 16.7956 | -0.0006
GEN-2017-140 | 04 SOUTHEAST | 512734 | FARML 4 | 138 | 8.386 | 8.3821 | -0.0039
GEN-2017-140 | 04 SOUTHEAST | 512751 | TONECE5 | 161 | 15.0736 | 15.0698 | -0.0038
GEN-2017-140 | 04 SOUTHEAST | 512820 | SILMCTY2 | 69 | 13.2969 | 13.2916 | -0.0053
GEN-2017-140 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 25.3323 | 25.3352 | 0.0029
GEN-2017-140 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 16.9067 | 16.9068 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 16.9067 | 16.9068 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.0408 | 20.0423 | 0.0015
GEN-2017-140 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7561 | 23.7553 | -0.0008
GEN-2017-140 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3814 | 29.381 | -0.0004
GEN-2017-140 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9253 | 15.9196 | -0.0057
GEN-2017-140 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1684 | 11.1642 | -0.0042
GEN-2017-140 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5366 | 18.5361 | -0.0005
GEN-2017-140 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.0014 | 45.9997 | -0.0017
GEN-2017-140 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3253 | 34.3238 | -0.0015
GEN-2017-140 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1385 | 24.1374 | -0.0011
GEN-2017-140 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8547 | 36.8533 | -0.0014
GEN-2017-140 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8438 | 20.8437 | -0.0001
GEN-2017-140 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.3382 | 42.338 | -0.0002
GEN-2017-140 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.3743 | 27.375 | 0.0007
GEN-2017-140 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.4412 | 26.4422 | 0.001
GEN-2017-140 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4475 | 45.4476 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7454 | 42.7454 | 0
GEN-2017-140 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0134 | 26.0139 | 0.0005
GEN-2017-140 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.6838 | 34.6837 | -0.0001
GEN-2017-140 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.0524 | 23.0521 | -0.0003
GEN-2017-140 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.2909 | 20.2908 | -0.0001
GEN-2017-140 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.4842 | 16.484 | -0.0002
GEN-2017-140 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.7846 | 40.7859 | 0.0013
GEN-2017-140 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4606 | 28.4632 | 0.0026
GEN-2017-140 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 10.6671 | 10.6669 | -0.0002
GEN-2017-140 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3267 | 20.3269 | 0.0002
GEN-2017-140 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 13.9877 | 13.9878 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.5629 | 9.5624 | -0.0005
GEN-2017-140 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 8.6732 | 8.6722 | -0.001
GEN-2017-140 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.5055 | 10.5045 | -0.001
GEN-2017-140 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.2257 | 8.2244 | -0.0013
GEN-2017-140 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.0482 | 16.0452 | -0.003
GEN-2017-140 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.2911 | 6.2902 | -0.0009
GEN-2017-140 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9613 | 11.9562 | -0.0051
GEN-2017-140 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.3868 | 13.3853 | -0.0015
GEN-2017-140 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.588 | 16.5864 | -0.0016
GEN-2017-140 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.1964 | 27.272 | 0.0756
GEN-2017-140 | 04 SOUTHEAST | 515227 | 5TRIBES2 | 69 | 12.8085 | 12.8061 | -0.0024
GEN-2017-140 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 15.6497 | 15.6503 | 0.0006
GEN-2017-140 | 04 SOUTHEAST | 515229 | AGENCY 2 | 69 | 13.1165 | 13.1138 | -0.0027
GEN-2017-140 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.2028 | 14.2022 | -0.0006
GEN-2017-140 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 9.7543 | 9.7544 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.2557 | 21.2622 | 0.0065
GEN-2017-140 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2276 | 21.2592 | 0.0316
GEN-2017-140 | 04 SOUTHEAST | 515249 | BEGGS 4 | 138 | 5.7134 | 5.7135 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 515250 | HANCOK-5 | 161 | 14.2948 | 14.2939 | -0.0009
GEN-2017-140 | 04 SOUTHEAST | 515251 | EUCLID 5 | 161 | 13.8792 | 13.8776 | -0.0016
GEN-2017-140 | 04 SOUTHEAST | 515299 | BEVYTAP5 | 161 | 20.724 | 20.7075 | -0.0165
GEN-2017-140 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 23.447 | 23.4275 | -0.0195
GEN-2017-140 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.3168 | 23.2972 | -0.0196
GEN-2017-140 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.1459 | 10.1315 | -0.0144
GEN-2017-140 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.5389 | 8.5315 | -0.0074
GEN-2017-140 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.3239 | 16.3106 | -0.0133
GEN-2017-140 | 04 SOUTHEAST | 515308 | 3RDST 5 | 161 | 15.7023 | 15.6901 | -0.0122
GEN-2017-140 | 04 SOUTHEAST | 515310 | QUANXTP5 | 161 | 17.8751 | 17.8603 | -0.0148
GEN-2017-140 | 04 SOUTHEAST | 515345 | COLONY 5 | 161 | 18.5871 | 18.5714 | -0.0157
GEN-2017-140 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1914 | 10.1886 | -0.0028
GEN-2017-140 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2787 | 40.2784 | -0.0003
GEN-2017-140 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6112 | 21.6107 | -0.0005
GEN-2017-140 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 24.4882 | 24.4931 | 0.0049
GEN-2017-140 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8855 | 34.8833 | -0.0022
GEN-2017-140 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.515 | 13.5135 | -0.0015
GEN-2017-140 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8712 | 39.8724 | 0.0012
GEN-2017-140 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.9831 | 7.9804 | -0.0027
GEN-2017-140 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3031 | 11.2948 | -0.0083
GEN-2017-140 | 04 SOUTHEAST | 532777 | G17-009-TAP | 345 | 11.5285 | 11.5225 | -0.006
GEN-2017-140 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.4372 | 17.4269 | -0.0103
GEN-2017-140 | 04 SOUTHEAST | 532937 | NEOSHO 5 | 161 | 22.3084 | 22.2969 | -0.0115
GEN-2017-140 | 04 SOUTHEAST | 533021 | NEOSHO 4 | 138 | 24.5009 | 24.4878 | -0.0131
GEN-2017-140 | 04 SOUTHEAST | 547484 | DEC392 5 | 161 | 15.2685 | 15.2683 | -0.0002
GEN-2017-140 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1935 | 27.1936 | 0.0001
GEN-2017-140 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5657 | 19.5659 | 0.0002
GEN-2017-140 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 31.7512 | 31.7758 | 0.0246
GEN-2017-140 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 17.4568 | 17.4606 | 0.0038
GEN-2017-140 | 04 SOUTHEAST | 588041 | G16133_765GS | 765 | 6.2051 | 6.2054 | 0.0003
GEN-2017-140 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 11.1718 | 11.1762 | 0.0044
GEN-2017-140 | 04 SOUTHEAST | 588834 | FWL-WND-SWYD | 345 | 11.3241 | 11.3287 | 0.0046
GEN-2017-140 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 11.3241 | 11.3287 | 0.0046
GEN-2017-140 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3241 | 11.3287 | 0.0046
GEN-2017-140 | 04 SOUTHEAST | 589140 | GEN-2017-076 | 161 | 20.9226 | 20.9097 | -0.0129
GEN-2017-140 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 9.9666 | 9.9699 | 0.0033
GEN-2017-140 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.2923 | 6.2923 | 0
GEN-2017-140 | 04 SOUTHEAST | 760368 | GEN-2017-213 | 345 | 16.6993 | 16.7965 | 0.0972
GEN-2017-140 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 4.327 | 4.5353 | 0.2083
GEN-2017-140 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 4.232 | 4.4411 | 0.2091
GEN-2017-140 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1576 | 4.1567 | -0.0009
GEN-2017-140 | 04 SOUTHEAST | 760921 | G17-209-TAP | 345 | 18.6007 | 18.5942 | -0.0065
GEN-2017-140 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.075 | 12.0893 | 0.0143
GEN-2017-140 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9667 | 2.9648 | -0.0019
GEN-2017-141 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.2633 | 15.2482 | -0.0151
GEN-2017-141 | 04 SOUTHEAST | 337811 | 8HAPPYVALY% | 500 | 24.8517 | 24.8493 | -0.0024
GEN-2017-141 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 17.7571 | 17.758 | 0.0009
GEN-2017-141 | 04 SOUTHEAST | 337912 | 5ANO% | 161 | 17.77 | 17.7702 | 0.0002
GEN-2017-141 | 04 SOUTHEAST | 337922 | 8P.HILL% | 500 | 15.3628 | 15.3607 | -0.0021
GEN-2017-141 | 04 SOUTHEAST | 504010 | ELMSPRGS 5 | 161 | 18.7343 | 18.712 | -0.0223
GEN-2017-141 | 04 SOUTHEAST | 504011 | ELMSPG_1 2 | 69 | 5.5242 | 5.514 | -0.0102
GEN-2017-141 | 04 SOUTHEAST | 504013 | ELMSPG_2 2 | 69 | 7.6993 | 7.6854 | -0.0139
GEN-2017-141 | 04 SOUTHEAST | 504020 | FARMNGTN 5 | 161 | 12.5571 | 12.5413 | -0.0158
GEN-2017-141 | 04 SOUTHEAST | 504021 | FARM_1 2 | 69 | 7.0832 | 7.0715 | -0.0117
GEN-2017-141 | 04 SOUTHEAST | 504201 | GENTRY 5 | 161 | 26.8758 | 26.8853 | 0.0095
GEN-2017-141 | 04 SOUTHEAST | 504202 | SILOAMSP 5 | 161 | 19.6471 | 19.6422 | -0.0049
GEN-2017-141 | 04 SOUTHEAST | 504274 | CARLEYRD 5 | 161 | 13.3319 | 13.3141 | -0.0178
GEN-2017-141 | 04 SOUTHEAST | 504275 | WEDINGTON5 | 161 | 11.8655 | 11.8508 | -0.0147
GEN-2017-141 | 04 SOUTHEAST | 506926 | DYESS 2 | 69 | 15.8318 | 15.8063 | -0.0255
GEN-2017-141 | 04 SOUTHEAST | 506927 | DYESS 5 | 161 | 17.5261 | 17.505 | -0.0211
GEN-2017-141 | 04 SOUTHEAST | 506931 | EROGERS5 | 161 | 15.0858 | 15.068 | -0.0178
GEN-2017-141 | 04 SOUTHEAST | 506934 | FLINTCR5 | 161 | 33.8866 | 33.9039 | 0.0173
GEN-2017-141 | 04 SOUTHEAST | 506935 | FLINTCR7 | 345 | 15.2902 | 15.2903 | 0.0001
GEN-2017-141 | 04 SOUTHEAST | 506938 | LOWELL 5 | 161 | 12.5053 | 12.4876 | -0.0177
GEN-2017-141 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 23.542 | 23.5251 | -0.0169
GEN-2017-141 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.1986 | 10.1829 | -0.0157
GEN-2017-141 | 04 SOUTHEAST | 506948 | SILOAM 5 | 161 | 22.0049 | 21.9997 | -0.0052
GEN-2017-141 | 04 SOUTHEAST | 506949 | SOSPRDL5 | 161 | 12.904 | 12.8865 | -0.0175
GEN-2017-141 | 04 SOUTHEAST | 506956 | FARMING5 | 161 | 12.4265 | 12.4105 | -0.016
GEN-2017-141 | 04 SOUTHEAST | 506957 | TONTITN5 | 161 | 23.0158 | 22.9917 | -0.0241
GEN-2017-141 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.1845 | 9.1687 | -0.0158
GEN-2017-141 | 04 SOUTHEAST | 506972 | LINCOLN2 | 69 | 4.7368 | 4.7305 | -0.0063
GEN-2017-141 | 04 SOUTHEAST | 506973 | SILOAM 2 | 69 | 11.3593 | 11.351 | -0.0083
GEN-2017-141 | 04 SOUTHEAST | 506978 | MATTISN5 | 161 | 22.5725 | 22.5484 | -0.0241
GEN-2017-141 | 04 SOUTHEAST | 506991 | BRUSHCRK_5 | 161 | 13.3396 | 13.3206 | -0.019
GEN-2017-141 | 04 SOUTHEAST | 506992 | WEDINGTON | 161 | 16.3722 | 16.355 | -0.0172
GEN-2017-141 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.0987 | 13.0883 | -0.0104
GEN-2017-141 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 12.571 | 12.5578 | -0.0132
GEN-2017-141 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.2826 | 12.2735 | -0.0091
GEN-2017-141 | 04 SOUTHEAST | 509737 | BA101 S4 | 138 | 18.1632 | 18.1582 | -0.005
GEN-2017-141 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.3325 | 20.5916 | 0.2591
GEN-2017-141 | 04 SOUTHEAST | 509747 | BA81---4 | 138 | 18.1891 | 18.1847 | -0.0044
GEN-2017-141 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 42.8186 | 42.8437 | 0.0251
GEN-2017-141 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3177 | 22.325 | 0.0073
GEN-2017-141 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 32.5943 | 32.598 | 0.0037
GEN-2017-141 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 25.4733 | 25.4809 | 0.0076
GEN-2017-141 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.0154 | 16.013 | -0.0024
GEN-2017-141 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 18.8448 | 18.8401 | -0.0047
GEN-2017-141 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 19.7357 | 19.7308 | -0.0049
GEN-2017-141 | 04 SOUTHEAST | 509770 | LLAN WT4 | 138 | 24.3364 | 24.3287 | -0.0077
GEN-2017-141 | 04 SOUTHEAST | 509772 | FORD---4 | 138 | 18.3474 | 18.3441 | -0.0033
GEN-2017-141 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 50.8695 | 50.9051 | 0.0356
GEN-2017-141 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 23.5852 | 23.5905 | 0.0053
GEN-2017-141 | 04 SOUTHEAST | 509780 | MAYO--S4 | 138 | 21.3826 | 21.381 | -0.0016
GEN-2017-141 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7353 | 31.7758 | 0.0405
GEN-2017-141 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 61.217 | 61.2694 | 0.0524
GEN-2017-141 | 04 SOUTHEAST | 509785 | BANNTAP4 | 138 | 18.7336 | 18.73 | -0.0036
GEN-2017-141 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 23.9151 | 23.9059 | -0.0092
GEN-2017-141 | 04 SOUTHEAST | 509790 | CATOOSA4 | 138 | 35.7046 | 35.7003 | -0.0043
GEN-2017-141 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 27.1763 | 27.1688 | -0.0075
GEN-2017-141 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 49.2273 | 49.2749 | 0.0476
GEN-2017-141 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.205 | 29.2864 | 0.0814
GEN-2017-141 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 22.8854 | 22.8924 | 0.007
GEN-2017-141 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 34.8881 | 34.8893 | 0.0012
GEN-2017-141 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.4535 | 29.4868 | 0.0333
GEN-2017-141 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 28.9183 | 28.9966 | 0.0783
GEN-2017-141 | 04 SOUTHEAST | 509845 | KIMCLRK4 | 138 | 22.3773 | 22.3815 | 0.0042
GEN-2017-141 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 24.9166 | 24.924 | 0.0074
GEN-2017-141 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 34.2055 | 34.2206 | 0.0151
GEN-2017-141 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 26.9773 | 26.987 | 0.0097
GEN-2017-141 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.0233 | 24.0314 | 0.0081
GEN-2017-141 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 29.9717 | 29.9822 | 0.0105
GEN-2017-141 | 04 SOUTHEAST | 509855 | 81GARN-4 | 138 | 17.7654 | 17.7615 | -0.0039
GEN-2017-141 | 04 SOUTHEAST | 509861 | E41ST_E4 | 138 | 17.0442 | 17.0402 | -0.004
GEN-2017-141 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 17.7882 | 17.7814 | -0.0068
GEN-2017-141 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.6767 | 22.6892 | 0.0125
GEN-2017-141 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.0774 | 33.0888 | 0.0114
GEN-2017-141 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 51.7687 | 51.8057 | 0.037
GEN-2017-141 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 23.3683 | 23.3747 | 0.0064
GEN-2017-141 | 04 SOUTHEAST | 509889 | E_121ST4 | 138 | 15.8783 | 15.8724 | -0.0059
GEN-2017-141 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.3457 | 23.3416 | -0.0041
GEN-2017-141 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 34.8356 | 34.8369 | 0.0013
GEN-2017-141 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.025 | 28.0306 | 0.0056
GEN-2017-141 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 10.9853 | 10.9769 | -0.0084
GEN-2017-141 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.6661 | 11.6586 | -0.0075
GEN-2017-141 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.0668 | 19.0791 | 0.0123
GEN-2017-141 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.3864 | 11.3845 | -0.0019
GEN-2017-141 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 9.8905 | 9.8889 | -0.0016
GEN-2017-141 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0394 | 14.0275 | -0.0119
GEN-2017-141 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2964 | 13.2777 | -0.0187
GEN-2017-141 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 14.914 | 14.8996 | -0.0144
GEN-2017-141 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.7982 | 13.7865 | -0.0117
GEN-2017-141 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.3189 | 13.311 | -0.0079
GEN-2017-141 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.4162 | 8.4157 | -0.0005
GEN-2017-141 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.8119 | 9.8057 | -0.0062
GEN-2017-141 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.5974 | 6.5969 | -0.0005
GEN-2017-141 | 04 SOUTHEAST | 512642 | SILSPWW5 | 161 | 14.7015 | 14.6962 | -0.0053
GEN-2017-141 | 04 SOUTHEAST | 512643 | SILMCTY5 | 161 | 19.8482 | 19.8425 | -0.0057
GEN-2017-141 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.1103 | 15.112 | 0.0017
GEN-2017-141 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 16.7963 | 16.7956 | -0.0007
GEN-2017-141 | 04 SOUTHEAST | 512734 | FARML 4 | 138 | 8.388 | 8.3821 | -0.0059
GEN-2017-141 | 04 SOUTHEAST | 512751 | TONECE5 | 161 | 15.0751 | 15.0698 | -0.0053
GEN-2017-141 | 04 SOUTHEAST | 512820 | SILMCTY2 | 69 | 13.2992 | 13.2916 | -0.0076
GEN-2017-141 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 25.3306 | 25.3352 | 0.0046
GEN-2017-141 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 16.9066 | 16.9068 | 0.0002
GEN-2017-141 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 16.9066 | 16.9068 | 0.0002
GEN-2017-141 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.0399 | 20.0423 | 0.0024
GEN-2017-141 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7565 | 23.7553 | -0.0012
GEN-2017-141 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3813 | 29.381 | -0.0003
GEN-2017-141 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9282 | 15.9196 | -0.0086
GEN-2017-141 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1705 | 11.1642 | -0.0063
GEN-2017-141 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5369 | 18.5361 | -0.0008
GEN-2017-141 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.0022 | 45.9997 | -0.0025
GEN-2017-141 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3261 | 34.3238 | -0.0023
GEN-2017-141 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1391 | 24.1374 | -0.0017
GEN-2017-141 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8553 | 36.8533 | -0.002
GEN-2017-141 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8438 | 20.8437 | -0.0001
GEN-2017-141 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.3382 | 42.338 | -0.0002
GEN-2017-141 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.3739 | 27.375 | 0.0011
GEN-2017-141 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.4406 | 26.4422 | 0.0016
GEN-2017-141 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4474 | 45.4476 | 0.0002
GEN-2017-141 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7453 | 42.7454 | 0.0001
GEN-2017-141 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0132 | 26.0139 | 0.0007
GEN-2017-141 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.6839 | 34.6837 | -0.0002
GEN-2017-141 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.0526 | 23.0521 | -0.0005
GEN-2017-141 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.291 | 20.2908 | -0.0002
GEN-2017-141 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.4843 | 16.484 | -0.0003
GEN-2017-141 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.7838 | 40.7859 | 0.0021
GEN-2017-141 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4591 | 28.4632 | 0.0041
GEN-2017-141 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 10.6671 | 10.6669 | -0.0002
GEN-2017-141 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3266 | 20.3269 | 0.0003
GEN-2017-141 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 13.9877 | 13.9878 | 0.0001
GEN-2017-141 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.5632 | 9.5624 | -0.0008
GEN-2017-141 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 8.6736 | 8.6722 | -0.0014
GEN-2017-141 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.506 | 10.5045 | -0.0015
GEN-2017-141 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.2263 | 8.2244 | -0.0019
GEN-2017-141 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.0498 | 16.0452 | -0.0046
GEN-2017-141 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.2916 | 6.2902 | -0.0014
GEN-2017-141 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.964 | 11.9562 | -0.0078
GEN-2017-141 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.3875 | 13.3853 | -0.0022
GEN-2017-141 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.5888 | 16.5864 | -0.0024
GEN-2017-141 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.1543 | 27.272 | 0.1177
GEN-2017-141 | 04 SOUTHEAST | 515227 | 5TRIBES2 | 69 | 12.8096 | 12.8061 | -0.0035
GEN-2017-141 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 15.6489 | 15.6503 | 0.0014
GEN-2017-141 | 04 SOUTHEAST | 515229 | AGENCY 2 | 69 | 13.1176 | 13.1138 | -0.0038
GEN-2017-141 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.2028 | 14.2022 | -0.0006
GEN-2017-141 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 9.754 | 9.7544 | 0.0004
GEN-2017-141 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.2516 | 21.2622 | 0.0106
GEN-2017-141 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2095 | 21.2592 | 0.0497
GEN-2017-141 | 04 SOUTHEAST | 515249 | BEGGS 4 | 138 | 5.7133 | 5.7135 | 0.0002
GEN-2017-141 | 04 SOUTHEAST | 515250 | HANCOK-5 | 161 | 14.2949 | 14.2939 | -0.001
GEN-2017-141 | 04 SOUTHEAST | 515251 | EUCLID 5 | 161 | 13.8796 | 13.8776 | -0.002
GEN-2017-141 | 04 SOUTHEAST | 515299 | BEVYTAP5 | 161 | 20.732 | 20.7075 | -0.0245
GEN-2017-141 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 23.4565 | 23.4275 | -0.029
GEN-2017-141 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.3263 | 23.2972 | -0.0291
GEN-2017-141 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.1529 | 10.1315 | -0.0214
GEN-2017-141 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.5424 | 8.5315 | -0.0109
GEN-2017-141 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.3303 | 16.3106 | -0.0197
GEN-2017-141 | 04 SOUTHEAST | 515308 | 3RDST 5 | 161 | 15.7083 | 15.6901 | -0.0182
GEN-2017-141 | 04 SOUTHEAST | 515310 | QUANXTP5 | 161 | 17.8823 | 17.8603 | -0.022
GEN-2017-141 | 04 SOUTHEAST | 515345 | COLONY 5 | 161 | 18.5947 | 18.5714 | -0.0233
GEN-2017-141 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1927 | 10.1886 | -0.0041
GEN-2017-141 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2788 | 40.2784 | -0.0004
GEN-2017-141 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6114 | 21.6107 | -0.0007
GEN-2017-141 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 24.4854 | 24.4931 | 0.0077
GEN-2017-141 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8865 | 34.8833 | -0.0032
GEN-2017-141 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.5157 | 13.5135 | -0.0022
GEN-2017-141 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8705 | 39.8724 | 0.0019
GEN-2017-141 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.9845 | 7.9804 | -0.0041
GEN-2017-141 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3074 | 11.2948 | -0.0126
GEN-2017-141 | 04 SOUTHEAST | 532777 | G17-009-TAP | 345 | 11.5316 | 11.5225 | -0.0091
GEN-2017-141 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.4425 | 17.4269 | -0.0156
GEN-2017-141 | 04 SOUTHEAST | 532937 | NEOSHO 5 | 161 | 22.3142 | 22.2969 | -0.0173
GEN-2017-141 | 04 SOUTHEAST | 533021 | NEOSHO 4 | 138 | 24.5075 | 24.4878 | -0.0197
GEN-2017-141 | 04 SOUTHEAST | 547484 | DEC392 5 | 161 | 15.2686 | 15.2683 | -0.0003
GEN-2017-141 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1934 | 27.1936 | 0.0002
GEN-2017-141 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5653 | 19.5659 | 0.0006
GEN-2017-141 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 31.7353 | 31.7758 | 0.0405
GEN-2017-141 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 17.4534 | 17.4606 | 0.0072
GEN-2017-141 | 04 SOUTHEAST | 588041 | G16133_765GS | 765 | 6.2044 | 6.2054 | 0.001
GEN-2017-141 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 11.1691 | 11.1762 | 0.0071
GEN-2017-141 | 04 SOUTHEAST | 588834 | FWL-WND-SWYD | 345 | 11.3213 | 11.3287 | 0.0074
GEN-2017-141 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 11.3213 | 11.3287 | 0.0074
GEN-2017-141 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3213 | 11.3287 | 0.0074
GEN-2017-141 | 04 SOUTHEAST | 589140 | GEN-2017-076 | 161 | 20.9268 | 20.9097 | -0.0171
GEN-2017-141 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 9.9646 | 9.9699 | 0.0053
GEN-2017-141 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.2923 | 6.2923 | 0
GEN-2017-141 | 04 SOUTHEAST | 760368 | GEN-2017-213 | 345 | 16.636 | 16.7965 | 0.1605
GEN-2017-141 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 4.2098 | 4.5353 | 0.3255
GEN-2017-141 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 4.1299 | 4.4411 | 0.3112
GEN-2017-141 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.158 | 4.1567 | -0.0013
GEN-2017-141 | 04 SOUTHEAST | 760921 | G17-209-TAP | 345 | 18.6041 | 18.5942 | -0.0099
GEN-2017-141 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.0671 | 12.0893 | 0.0222
GEN-2017-141 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9677 | 2.9648 | -0.0029
GEN-2017-146 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 7.3167 | 7.2671 | -0.0496
GEN-2017-146 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.6463 | 14.61 | -0.0363
GEN-2017-146 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1921 | 3.1865 | -0.0056
GEN-2017-146 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.4005 | 4.396 | -0.0045
GEN-2017-146 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.9574 | 6.9435 | -0.0139
GEN-2017-146 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.7439 | 9.7319 | -0.012
GEN-2017-146 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9609 | 8.9501 | -0.0108
GEN-2017-146 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2279 | 4.2217 | -0.0062
GEN-2017-146 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 20.2903 | 20.3107 | 0.0204
GEN-2017-146 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 7.4106 | 7.3999 | -0.0107
GEN-2017-146 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 25.9126 | 25.9565 | 0.0439
GEN-2017-146 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 25.9126 | 25.9565 | 0.0439
GEN-2017-146 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 25.9126 | 25.9565 | 0.0439
GEN-2017-146 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.2071 | 19.2181 | 0.011
GEN-2017-146 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 19.1804 | 19.2009 | 0.0205
GEN-2017-146 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 25.1382 | 25.1787 | 0.0405
GEN-2017-146 | 05 SOUTHWEST | 524243 | OUTPOST 3 | 115 | 9.4539 | 9.4592 | 0.0053
GEN-2017-146 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 9.3055 | 9.3115 | 0.006
GEN-2017-146 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 9.5733 | 9.6174 | 0.0441
GEN-2017-146 | 05 SOUTHWEST | 524276 | WILDOR_WND 6 | 230 | 4.9799 | 4.9878 | 0.0079
GEN-2017-146 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.6078 | 6.6247 | 0.0169
GEN-2017-146 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 4.0789 | 4.0715 | -0.0074
GEN-2017-146 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.2966 | 14.3126 | 0.016
GEN-2017-146 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.5452 | 16.5557 | 0.0105
GEN-2017-146 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.3882 | 13.4002 | 0.012
GEN-2017-146 | 05 SOUTHWEST | 524556 | LAPLATA 3 | 115 | 5.1734 | 5.2052 | 0.0318
GEN-2017-146 | 05 SOUTHWEST | 524560 | ARNOT 3 | 115 | 10.3524 | 10.3579 | 0.0055
GEN-2017-146 | 05 SOUTHWEST | 524567 | NE_HEREFORD3 | 115 | 9.5058 | 9.6124 | 0.1066
GEN-2017-146 | 05 SOUTHWEST | 524573 | NE_HEREFORD2 | 69 | 6.6008 | 6.6305 | 0.0297
GEN-2017-146 | 05 SOUTHWEST | 524575 | DS-#25+ 3 | 115 | 9.802 | 9.9081 | 0.1061
GEN-2017-146 | 05 SOUTHWEST | 524597 | PANDAHFD 3 | 115 | 8.5754 | 8.6501 | 0.0747
GEN-2017-146 | 05 SOUTHWEST | 524604 | HEREFRD_SB 2 | 69 | 4.6568 | 4.6715 | 0.0147
GEN-2017-146 | 05 SOUTHWEST | 524605 | HEREFRD_NB 2 | 69 | 4.6568 | 4.6715 | 0.0147
GEN-2017-146 | 05 SOUTHWEST | 524606 | HEREFORD 3 | 115 | 10.5349 | 10.6641 | 0.1292
GEN-2017-146 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.3065 | 11.4628 | 0.1563
GEN-2017-146 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.3082 | 11.4645 | 0.1563
GEN-2017-146 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 7.6824 | 7.891 | 0.2086
GEN-2017-146 | 05 SOUTHWEST | 524629 | DS-#6 3 | 115 | 7.0401 | 7.0908 | 0.0507
GEN-2017-146 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 11.608 | 11.7685 | 0.1605
GEN-2017-146 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.7294 | 4.7329 | 0.0035
GEN-2017-146 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.708 | 9.7291 | 0.0211
GEN-2017-146 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 9.0288 | 9.0368 | 0.008
GEN-2017-146 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 10.3073 | 10.3279 | 0.0206
GEN-2017-146 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.8705 | 8.8834 | 0.0129
GEN-2017-146 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.1854 | 10.1935 | 0.0081
GEN-2017-146 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.1403 | 6.1458 | 0.0055
GEN-2017-146 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 10.7212 | 10.7332 | 0.012
GEN-2017-146 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 9.4439 | 9.4504 | 0.0065
GEN-2017-146 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.3842 | 7.3913 | 0.0071
GEN-2017-146 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.7474 | 4.7478 | 0.0004
GEN-2017-146 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 10.3679 | 10.3767 | 0.0088
GEN-2017-146 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 8.8612 | 8.8723 | 0.0111
GEN-2017-146 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.2911 | 7.2951 | 0.004
GEN-2017-146 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 4.7908 | 4.7927 | 0.0019
GEN-2017-146 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.1005 | 5.1027 | 0.0022
GEN-2017-146 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 4.6737 | 4.6745 | 0.0008
GEN-2017-146 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.0014 | 5.0034 | 0.002
GEN-2017-146 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.5961 | 7.604 | 0.0079
GEN-2017-146 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 7.8506 | 7.8582 | 0.0076
GEN-2017-146 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.3714 | 7.3657 | -0.0057
GEN-2017-146 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.455 | -0.0074
GEN-2017-146 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4267 | 4.4198 | -0.0069
GEN-2017-146 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.6987 | 11.6874 | -0.0113
GEN-2017-146 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.1664 | 11.1549 | -0.0115
GEN-2017-146 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.259 | 10.2536 | -0.0054
GEN-2017-146 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4172 | 6.409 | -0.0082
GEN-2017-146 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2975 | 5.2909 | -0.0066
GEN-2017-146 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.2246 | 6.2173 | -0.0073
GEN-2017-146 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5793 | 2.5758 | -0.0035
GEN-2017-146 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.2567 | 3.2523 | -0.0044
GEN-2017-146 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.3591 | 6.352 | -0.0071
GEN-2017-146 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 8.072 | 8.0746 | 0.0026
GEN-2017-146 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 4.752 | 4.7476 | -0.0044
GEN-2017-146 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.365 | 7.361 | -0.004
GEN-2017-146 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.6587 | 5.6519 | -0.0068
GEN-2017-146 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 6.8258 | 6.8236 | -0.0022
GEN-2017-146 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 8.9331 | 8.9369 | 0.0038
GEN-2017-146 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.6062 | 6.5986 | -0.0076
GEN-2017-146 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.0115 | 10.0036 | -0.0079
GEN-2017-146 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.4631 | 14.4601 | -0.003
GEN-2017-146 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.5467 | 10.5488 | 0.0021
GEN-2017-146 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 14.6836 | 14.7044 | 0.0208
GEN-2017-146 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 21.9906 | 22.127 | 0.1364
GEN-2017-146 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 26.9079 | 27.0017 | 0.0938
GEN-2017-146 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 8.5592 | 8.5657 | 0.0065
GEN-2017-146 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 9.9579 | 9.9669 | 0.009
GEN-2017-146 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 10.4994 | 10.5095 | 0.0101
GEN-2017-146 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 10.4994 | 10.5095 | 0.0101
GEN-2017-146 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 3.011 | 3.0109 | -0.0001
GEN-2017-146 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1605 | 4.1606 | 0.0001
GEN-2017-146 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.9102 | 5.9107 | 0.0005
GEN-2017-146 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.2518 | 8.2553 | 0.0035
GEN-2017-146 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4046 | 5.4075 | 0.0029
GEN-2017-146 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9629 | 4.9631 | 0.0002
GEN-2017-146 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6255 | 4.6256 | 0.0001
GEN-2017-146 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.8304 | 5.8239 | -0.0065
GEN-2017-146 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.7123 | 6.7052 | -0.0071
GEN-2017-146 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6141 | 4.605 | -0.0091
GEN-2017-146 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9108 | 7.8955 | -0.0153
GEN-2017-146 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.7394 | 19.7064 | -0.033
GEN-2017-146 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9637 | 21.9248 | -0.0389
GEN-2017-146 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 12.6097 | 12.5696 | -0.0401
GEN-2017-146 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.7811 | 21.7426 | -0.0385
GEN-2017-146 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 12.4857 | 12.446 | -0.0397
GEN-2017-146 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.8286 | 11.8094 | -0.0192
GEN-2017-146 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.237 | 5.236 | -0.001
GEN-2017-146 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.5197 | 5.5192 | -0.0005
GEN-2017-146 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.8176 | 5.8169 | -0.0007
GEN-2017-146 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.0057 | 8.9953 | -0.0104
GEN-2017-146 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.7215 | 12.7108 | -0.0107
GEN-2017-146 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.4538 | 10.4443 | -0.0095
GEN-2017-146 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 18.2121 | 18.2089 | -0.0032
GEN-2017-146 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.7615 | 15.7633 | 0.0018
GEN-2017-146 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.9684 | 14.9624 | -0.006
GEN-2017-146 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.5697 | 11.5706 | 0.0009
GEN-2017-146 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 17.6957 | 17.6997 | 0.004
GEN-2017-146 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 7.1734 | 7.1719 | -0.0015
GEN-2017-146 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.5135 | 9.5116 | -0.0019
GEN-2017-146 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.9988 | 10.9969 | -0.0019
GEN-2017-146 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 10.998 | 10.9991 | 0.0011
GEN-2017-146 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.3267 | 10.3247 | -0.002
GEN-2017-146 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.4799 | 6.4781 | -0.0018
GEN-2017-146 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 9.6949 | 9.6946 | -0.0003
GEN-2017-146 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.741 | 10.7323 | -0.0087
GEN-2017-146 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.3182 | 9.3159 | -0.0023
GEN-2017-146 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2339 | 11.2259 | -0.008
GEN-2017-146 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 12.7679 | 12.764 | -0.0039
GEN-2017-146 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.3048 | 6.305 | 0.0002
GEN-2017-146 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.7962 | 10.7917 | -0.0045
GEN-2017-146 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 18.6238 | 18.6189 | -0.0049
GEN-2017-146 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 18.5263 | 18.5224 | -0.0039
GEN-2017-146 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.7182 | 9.7109 | -0.0073
GEN-2017-146 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 14.605 | 14.602 | -0.003
GEN-2017-146 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 10.9938 | 10.9919 | -0.0019
GEN-2017-146 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 15.8004 | 15.7983 | -0.0021
GEN-2017-146 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 9.3606 | 9.3605 | -0.0001
GEN-2017-146 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 9.1545 | 9.1543 | -0.0002
GEN-2017-146 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 10.3576 | 10.3578 | 0.0002
GEN-2017-146 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.1757 | 7.175 | -0.0007
GEN-2017-146 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 11.6961 | 11.6945 | -0.0016
GEN-2017-146 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 8.8612 | 8.8723 | 0.0111
GEN-2017-146 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 6.9747 | 7.3179 | 0.3432
GEN-2017-146 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.2572 | 7.5987 | 0.3415
GEN-2017-146 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 12.2859 | 12.3044 | 0.0185
GEN-2017-146 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 7.5434 | 7.5051 | -0.0383
GEN-2017-149 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 20.5183 | 20.5225 | 0.0042
GEN-2017-149 | 04 SOUTHEAST | 505600 | TUPELO 4 | 138 | 10.9865 | 10.9837 | -0.0028
GEN-2017-149 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 8.8025 | 8.7934 | -0.0091
GEN-2017-149 | 04 SOUTHEAST | 505604 | DENISON4 | 138 | 3.1579 | 3.1497 | -0.0082
GEN-2017-149 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.1909 | 10.1829 | -0.008
GEN-2017-149 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.0454 | 13.0343 | -0.0111
GEN-2017-149 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 24.0612 | 24.0649 | 0.0037
GEN-2017-149 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 8.9063 | 8.9003 | -0.006
GEN-2017-149 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 19.2888 | 19.268 | -0.0208
GEN-2017-149 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 23.7173 | 23.6925 | -0.0248
GEN-2017-149 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 24.6968 | 24.671 | -0.0258
GEN-2017-149 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.1041 | 13.0883 | -0.0158
GEN-2017-149 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 11.9772 | 11.9676 | -0.0096
GEN-2017-149 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 12.5785 | 12.5578 | -0.0207
GEN-2017-149 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 20.5183 | 20.5225 | 0.0042
GEN-2017-149 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 18.7101 | 18.7062 | -0.0039
GEN-2017-149 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.0695 | 15.0706 | 0.0011
GEN-2017-149 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.5966 | 20.5916 | -0.005
GEN-2017-149 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7812 | 31.7758 | -0.0054
GEN-2017-149 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.292 | 29.2864 | -0.0056
GEN-2017-149 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.6348 | 9.6179 | -0.0169
GEN-2017-149 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.5626 | 6.5488 | -0.0138
GEN-2017-149 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 4.9976 | 4.9868 | -0.0108
GEN-2017-149 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8857 | 6.8769 | -0.0088
GEN-2017-149 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.2296 | 7.2239 | -0.0057
GEN-2017-149 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.1937 | 5.1825 | -0.0112
GEN-2017-149 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5731 | 3.5657 | -0.0074
GEN-2017-149 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14 | 14.0275 | 0.0275
GEN-2017-149 | 04 SOUTHEAST | 510908 | MCALEST4 | 138 | 9.9393 | 9.9277 | -0.0116
GEN-2017-149 | 04 SOUTHEAST | 510909 | MCALESTIND 4 | 138 | 5.7233 | 5.7145 | -0.0088
GEN-2017-149 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.5501 | 7.5345 | -0.0156
GEN-2017-149 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2987 | 13.2777 | -0.021
GEN-2017-149 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 14.9222 | 14.8996 | -0.0226
GEN-2017-149 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.7608 | 13.7865 | 0.0257
GEN-2017-149 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.328 | 13.311 | -0.017
GEN-2017-149 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.4194 | 8.4157 | -0.0037
GEN-2017-149 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.8189 | 9.8057 | -0.0132
GEN-2017-149 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.1462 | 5.1387 | -0.0075
GEN-2017-149 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.134 | 25.1312 | -0.0028
GEN-2017-149 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.9039 | 13.906 | 0.0021
GEN-2017-149 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.5978 | 6.5969 | -0.0009
GEN-2017-149 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.4444 | 10.455 | 0.0106
GEN-2017-149 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.5866 | 6.5871 | 0.0005
GEN-2017-149 | 04 SOUTHEAST | 511979 | RSHSPR1_MPT1 | 345 | 5.8044 | 5.8016 | -0.0028
GEN-2017-149 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7532 | 23.7553 | 0.0021
GEN-2017-149 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.8665 | 15.9196 | 0.0531
GEN-2017-149 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.9269 | 11.1642 | 0.2373
GEN-2017-149 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.538 | 18.5361 | -0.0019
GEN-2017-149 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.0006 | 45.9997 | -0.0009
GEN-2017-149 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3237 | 34.3238 | 0.0001
GEN-2017-149 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1399 | 24.1374 | -0.0025
GEN-2017-149 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8517 | 36.8533 | 0.0016
GEN-2017-149 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8441 | 20.8437 | -0.0004
GEN-2017-149 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.336 | 42.338 | 0.002
GEN-2017-149 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.372 | 27.375 | 0.003
GEN-2017-149 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.4397 | 26.4422 | 0.0025
GEN-2017-149 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4417 | 45.4476 | 0.0059
GEN-2017-149 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7387 | 42.7454 | 0.0067
GEN-2017-149 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0038 | 26.0139 | 0.0101
GEN-2017-149 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.682 | 34.6837 | 0.0017
GEN-2017-149 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.0526 | 23.0521 | -0.0005
GEN-2017-149 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.2906 | 20.2908 | 0.0002
GEN-2017-149 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.4835 | 16.484 | 0.0005
GEN-2017-149 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.756 | 40.7859 | 0.0299
GEN-2017-149 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.433 | 28.4632 | 0.0302
GEN-2017-149 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 10.6696 | 10.6669 | -0.0027
GEN-2017-149 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3261 | 20.3269 | 0.0008
GEN-2017-149 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 13.989 | 13.9878 | -0.0012
GEN-2017-149 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.5677 | 9.5624 | -0.0053
GEN-2017-149 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 8.6826 | 8.6722 | -0.0104
GEN-2017-149 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.514 | 10.5045 | -0.0095
GEN-2017-149 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.2338 | 8.2244 | -0.0094
GEN-2017-149 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.182 | 6.1717 | -0.0103
GEN-2017-149 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.046 | 16.0452 | -0.0008
GEN-2017-149 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6169 | 11.6142 | -0.0027
GEN-2017-149 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.1459 | 11.1455 | -0.0004
GEN-2017-149 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.3056 | 11.3066 | 0.001
GEN-2017-149 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 12.953 | 12.9458 | -0.0072
GEN-2017-149 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.2989 | 6.2902 | -0.0087
GEN-2017-149 | 04 SOUTHEAST | 515128 | RATLIFF2 | 69 | 5.2598 | 5.245 | -0.0148
GEN-2017-149 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 7.2098 | 7.1966 | -0.0132
GEN-2017-149 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 9.8026 | 9.7877 | -0.0149
GEN-2017-149 | 04 SOUTHEAST | 515131 | FOX 4 | 138 | 7.6152 | 7.6006 | -0.0146
GEN-2017-149 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 10.665 | 10.6599 | -0.0051
GEN-2017-149 | 04 SOUTHEAST | 515134 | PRARPNT4 | 138 | 5.7098 | 5.6994 | -0.0104
GEN-2017-149 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.1572 | 20.1906 | 0.0334
GEN-2017-149 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.8775 | 11.9562 | 0.0787
GEN-2017-149 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.1527 | 13.1457 | -0.007
GEN-2017-149 | 04 SOUTHEAST | 515138 | CARTER 4 | 138 | 12.976 | 12.9687 | -0.0073
GEN-2017-149 | 04 SOUTHEAST | 515143 | WOLFCRK4 | 138 | 10.1513 | 10.136 | -0.0153
GEN-2017-149 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 14.2003 | 14.1964 | -0.0039
GEN-2017-149 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 8.4763 | 8.4633 | -0.013
GEN-2017-149 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 8.4744 | 8.4614 | -0.013
GEN-2017-149 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.2987 | 9.287 | -0.0117
GEN-2017-149 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 7.473 | 7.4605 | -0.0125
GEN-2017-149 | 04 SOUTHEAST | 515152 | BROWNTP4 | 138 | 8.631 | 8.6216 | -0.0094
GEN-2017-149 | 04 SOUTHEAST | 515155 | BODLE 4 | 138 | 6.5311 | 6.5204 | -0.0107
GEN-2017-149 | 04 SOUTHEAST | 515157 | BROWN 4 | 138 | 8.7591 | 8.75 | -0.0091
GEN-2017-149 | 04 SOUTHEAST | 515158 | MADLIND4 | 138 | 7.881 | 7.8671 | -0.0139
GEN-2017-149 | 04 SOUTHEAST | 515159 | COLBRTP4 | 138 | 6.5989 | 6.5883 | -0.0106
GEN-2017-149 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.5332 | 7.5183 | -0.0149
GEN-2017-149 | 04 SOUTHEAST | 515162 | FNDTION4 | 138 | 12.1918 | 12.1825 | -0.0093
GEN-2017-149 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 7.9891 | 7.9646 | -0.0245
GEN-2017-149 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.1892 | 12.179 | -0.0102
GEN-2017-149 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.1224 | 12.1135 | -0.0089
GEN-2017-149 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.3988 | 8.3852 | -0.0136
GEN-2017-149 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.3879 | 13.3853 | -0.0026
GEN-2017-149 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.5864 | 16.5864 | 0
GEN-2017-149 | 04 SOUTHEAST | 515196 | MILLCRK4 | 138 | 9.1353 | 9.1275 | -0.0078
GEN-2017-149 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.2655 | 27.272 | 0.0065
GEN-2017-149 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.267 | 21.2622 | -0.0048
GEN-2017-149 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2593 | 21.2592 | -0.0001
GEN-2017-149 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.3224 | 23.2972 | -0.0252
GEN-2017-149 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.1496 | 10.1315 | -0.0181
GEN-2017-149 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.5408 | 8.5315 | -0.0093
GEN-2017-149 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 12.9556 | 12.9479 | -0.0077
GEN-2017-149 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 12.78 | 12.7709 | -0.0091
GEN-2017-149 | 04 SOUTHEAST | 515420 | SCMMRCT2 | 69 | 9.1944 | 9.1675 | -0.0269
GEN-2017-149 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1918 | 10.1886 | -0.0032
GEN-2017-149 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2767 | 40.2784 | 0.0017
GEN-2017-149 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6099 | 21.6107 | 0.0008
GEN-2017-149 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.885 | 34.8833 | -0.0017
GEN-2017-149 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.5159 | 13.5135 | -0.0024
GEN-2017-149 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 14.5568 | 14.5531 | -0.0037
GEN-2017-149 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 10.0907 | 10.0758 | -0.0149
GEN-2017-149 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 5.8785 | 5.8639 | -0.0146
GEN-2017-149 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.187 | 11.1761 | -0.0109
GEN-2017-149 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.1099 | 10.0974 | -0.0125
GEN-2017-149 | 04 SOUTHEAST | 515944 | STRRDTP4 | 138 | 8.7259 | 8.7167 | -0.0092
GEN-2017-149 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8438 | 39.8724 | 0.0286
GEN-2017-149 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.8892 | 7.9804 | 0.0912
GEN-2017-149 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 10.6395 | 10.6433 | 0.0038
GEN-2017-149 | 04 SOUTHEAST | 520465 | REAGAN 4 | 138 | 4.2336 | 4.2201 | -0.0135
GEN-2017-149 | 04 SOUTHEAST | 520467 | ENOSJCT4 | 138 | 7.7424 | 7.7282 | -0.0142
GEN-2017-149 | 04 SOUTHEAST | 520488 | LEBANON4 | 138 | 6.0918 | 6.0771 | -0.0147
GEN-2017-149 | 04 SOUTHEAST | 520511 | ENVILLE4 | 138 | 6.5371 | 6.5224 | -0.0147
GEN-2017-149 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3661 | 22.3812 | 0.0151
GEN-2017-149 | 04 SOUTHEAST | 520901 | ENOS 4 | 138 | 4.9013 | 4.8871 | -0.0142
GEN-2017-149 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 10.7573 | 10.7604 | 0.0031
GEN-2017-149 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.6696 | 22.6904 | 0.0208
GEN-2017-149 | 04 SOUTHEAST | 520963 | KIERSEY4 | 138 | 5.6606 | 5.6499 | -0.0107
GEN-2017-149 | 04 SOUTHEAST | 520972 | LEBANTP4 | 138 | 6.9984 | 6.9835 | -0.0149
GEN-2017-149 | 04 SOUTHEAST | 520988 | MARIETA4 | 138 | 7.4397 | 7.4254 | -0.0143
GEN-2017-149 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 11.5443 | 11.5412 | -0.0031
GEN-2017-149 | 04 SOUTHEAST | 521049 | SCLMNJC4 | 138 | 7.3476 | 7.3373 | -0.0103
GEN-2017-149 | 04 SOUTHEAST | 521066 | TEXOMA 4 | 138 | 5.8074 | 5.7926 | -0.0148
GEN-2017-149 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 9.2056 | 9.1937 | -0.0119
GEN-2017-149 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 8.6785 | 8.6792 | 0.0007
GEN-2017-149 | 04 SOUTHEAST | 521122 | HOWE 4 | 138 | 11.1959 | 11.1963 | 0.0004
GEN-2017-149 | 04 SOUTHEAST | 521125 | CHEEK_4 | 138 | 8.8077 | 8.7912 | -0.0165
GEN-2017-149 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3096 | 11.2948 | -0.0148
GEN-2017-149 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1858 | 27.1936 | 0.0078
GEN-2017-149 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.0933 | 8.0836 | -0.0097
GEN-2017-149 | 04 SOUTHEAST | 563259 | GEN-2015-092 | 345 | 6.3834 | 6.3837 | 0.0003
GEN-2017-149 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 7.991 | 7.981 | -0.01
GEN-2017-149 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.9204 | 15.9213 | 0.0009
GEN-2017-149 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 13.238 | 13.2313 | -0.0067
GEN-2017-149 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 18.7457 | 18.76 | 0.0143
GEN-2017-149 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 10.0404 | 10.0256 | -0.0148
GEN-2017-149 | 04 SOUTHEAST | 588834 | FWL-WND-SWYD | 345 | 11.3301 | 11.3287 | -0.0014
GEN-2017-149 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 11.3301 | 11.3287 | -0.0014
GEN-2017-149 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3301 | 11.3287 | -0.0014
GEN-2017-149 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.0821 | 8.0724 | -0.0097
GEN-2017-149 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 9.9718 | 9.9699 | -0.0019
GEN-2017-149 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.2922 | 6.2923 | 0.0001
GEN-2017-149 | 04 SOUTHEAST | 760368 | GEN-2017-213 | 345 | 16.8007 | 16.7965 | -0.0042
GEN-2017-149 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 4.5361 | 4.5353 | -0.0008
GEN-2017-149 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.8047 | 4.1567 | 0.352
GEN-2017-149 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.505 | 3.7918 | 0.2868
GEN-2017-149 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.4134 | 11.4188 | 0.0054
GEN-2017-149 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.4134 | 11.4188 | 0.0054
GEN-2017-149 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.0881 | 12.0893 | 0.0012
GEN-2017-149 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9722 | 2.9648 | -0.0074
GEN-2017-149 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.935 | 6.9453 | 0.0103
GEN-2017-150 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.5961 | 20.5916 | -0.0045
GEN-2017-150 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.783 | 31.7758 | -0.0072
GEN-2017-150 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0449 | 14.0275 | -0.0174
GEN-2017-150 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.302 | 13.2777 | -0.0243
GEN-2017-150 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.8036 | 13.7865 | -0.0171
GEN-2017-150 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.0264 | 10.0261 | -0.0003
GEN-2017-150 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.0531 | 9.0513 | -0.0018
GEN-2017-150 | 04 SOUTHEAST | 511424 | T-CONCO4 | 138 | 6.903 | 6.9019 | -0.0011
GEN-2017-150 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.581 | 10.5801 | -0.0009
GEN-2017-150 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.4265 | 18.4204 | -0.0061
GEN-2017-150 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 11.7639 | 11.7591 | -0.0048
GEN-2017-150 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 8.0177 | 8.018 | 0.0003
GEN-2017-150 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.1429 | 5.1387 | -0.0042
GEN-2017-150 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.5658 | 16.5612 | -0.0046
GEN-2017-150 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.1339 | 25.1312 | -0.0027
GEN-2017-150 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.9028 | 13.906 | 0.0032
GEN-2017-150 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.5664 | 12.5614 | -0.005
GEN-2017-150 | 04 SOUTHEAST | 511476 | S.W.S.-2 | 69 | 4.3095 | 4.3096 | 0.0001
GEN-2017-150 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.9178 | 34.9339 | 0.0161
GEN-2017-150 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 11.5652 | 11.564 | -0.0012
GEN-2017-150 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.2604 | 10.258 | -0.0024
GEN-2017-150 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 7.3482 | 7.3446 | -0.0036
GEN-2017-150 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 21.9638 | 21.9595 | -0.0043
GEN-2017-150 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4182 | 10.4172 | -0.001
GEN-2017-150 | 04 SOUTHEAST | 511540 | CAN_GAS4 | 138 | 9.2257 | 9.2248 | -0.0009
GEN-2017-150 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 8.6897 | 8.6849 | -0.0048
GEN-2017-150 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.5479 | 10.543 | -0.0049
GEN-2017-150 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 11.5287 | 11.5228 | -0.0059
GEN-2017-150 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.185 | 10.1828 | -0.0022
GEN-2017-150 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.1286 | 5.1244 | -0.0042
GEN-2017-150 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.4596 | 10.455 | -0.0046
GEN-2017-150 | 04 SOUTHEAST | 511575 | LEONARD4 | 138 | 10.2666 | 10.2655 | -0.0011
GEN-2017-150 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.9439 | 6.9428 | -0.0011
GEN-2017-150 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.4058 | 21.4024 | -0.0034
GEN-2017-150 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.9174 | 20.9135 | -0.0039
GEN-2017-150 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.3962 | 23.7553 | 0.3591
GEN-2017-150 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3955 | 29.381 | -0.0145
GEN-2017-150 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1743 | 11.1642 | -0.0101
GEN-2017-150 | 04 SOUTHEAST | 514817 | SVCELRN2 | 69 | 6.5638 | 6.5639 | 0.0001
GEN-2017-150 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.5498 | 7.55 | 0.0002
GEN-2017-150 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.2501 | 17.252 | 0.0019
GEN-2017-150 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.7117 | 18.7141 | 0.0024
GEN-2017-150 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 15.8072 | 15.808 | 0.0008
GEN-2017-150 | 04 SOUTHEAST | 514823 | ROMNOSE4 | 138 | 6.0223 | 6.0219 | -0.0004
GEN-2017-150 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5369 | 18.5361 | -0.0008
GEN-2017-150 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 27.4322 | 27.4391 | 0.0069
GEN-2017-150 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 27.9018 | 27.9091 | 0.0073
GEN-2017-150 | 04 SOUTHEAST | 514849 | LAKESID4 | 138 | 25.3871 | 25.3942 | 0.0071
GEN-2017-150 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 30.5194 | 30.5292 | 0.0098
GEN-2017-150 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 34.1256 | 34.1397 | 0.0141
GEN-2017-150 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 37.5807 | 37.6002 | 0.0195
GEN-2017-150 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.7794 | 32.7917 | 0.0123
GEN-2017-150 | 04 SOUTHEAST | 514861 | MUSTANG4 | 138 | 39.9489 | 39.9735 | 0.0246
GEN-2017-150 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 22.6181 | 22.6228 | 0.0047
GEN-2017-150 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6088 | 27.6188 | 0.01
GEN-2017-150 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.3301 | 23.3345 | 0.0044
GEN-2017-150 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.0626 | 28.0702 | 0.0076
GEN-2017-150 | 04 SOUTHEAST | 514876 | SW134TP4 | 138 | 30.0537 | 30.0708 | 0.0171
GEN-2017-150 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.9705 | 45.9997 | 0.0292
GEN-2017-150 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2675 | 34.3238 | 0.0563
GEN-2017-150 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1217 | 24.1374 | 0.0157
GEN-2017-150 | 04 SOUTHEAST | 514887 | WESTMOR4 | 138 | 28.7157 | 28.7306 | 0.0149
GEN-2017-150 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 30.9178 | 30.9327 | 0.0149
GEN-2017-150 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.5869 | 29.6006 | 0.0137
GEN-2017-150 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.1235 | 20.1299 | 0.0064
GEN-2017-150 | 04 SOUTHEAST | 514896 | MORGAN 4 | 138 | 34.2932 | 34.3115 | 0.0183
GEN-2017-150 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.6757 | 46.7216 | 0.0459
GEN-2017-150 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.7152 | 36.8533 | 0.1381
GEN-2017-150 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 36.586 | 36.6149 | 0.0289
GEN-2017-150 | 04 SOUTHEAST | 514904 | WESTHSE4 | 138 | 19.4503 | 19.4553 | 0.005
GEN-2017-150 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8423 | 20.8437 | 0.0014
GEN-2017-150 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.3234 | 42.338 | 0.0146
GEN-2017-150 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.3597 | 27.375 | 0.0153
GEN-2017-150 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.4294 | 26.4422 | 0.0128
GEN-2017-150 | 04 SOUTHEAST | 514928 | SOGATE 4 | 138 | 27.0397 | 27.0537 | 0.014
GEN-2017-150 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.3973 | 45.4476 | 0.0503
GEN-2017-150 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.6384 | 21.6438 | 0.0054
GEN-2017-150 | 04 SOUTHEAST | 514932 | MLENIUM4 | 138 | 20.7675 | 20.773 | 0.0055
GEN-2017-150 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7041 | 42.7454 | 0.0413
GEN-2017-150 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 25.9596 | 26.0139 | 0.0543
GEN-2017-150 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.6634 | 34.6837 | 0.0203
GEN-2017-150 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 23.969 | 23.976 | 0.007
GEN-2017-150 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.0455 | 23.0521 | 0.0066
GEN-2017-150 | 04 SOUTHEAST | 514952 | STUBMAN4 | 138 | 25.2427 | 25.2528 | 0.0101
GEN-2017-150 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.9388 | 36.9658 | 0.027
GEN-2017-150 | 04 SOUTHEAST | 514954 | INDNHIL4 | 138 | 29.0644 | 29.079 | 0.0146
GEN-2017-150 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.7196 | 22.7277 | 0.0081
GEN-2017-150 | 04 SOUTHEAST | 514958 | BOYD 4 | 138 | 20.9378 | 20.9434 | 0.0056
GEN-2017-150 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.2853 | 20.2908 | 0.0055
GEN-2017-150 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 30.6249 | 30.6445 | 0.0196
GEN-2017-150 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 15.6354 | 15.6378 | 0.0024
GEN-2017-150 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.281 | 14.2828 | 0.0018
GEN-2017-150 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.4811 | 16.484 | 0.0029
GEN-2017-150 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.7734 | 40.7859 | 0.0125
GEN-2017-150 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4371 | 28.4632 | 0.0261
GEN-2017-150 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3302 | 20.3269 | -0.0033
GEN-2017-150 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.5065 | 10.5045 | -0.002
GEN-2017-150 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.2707 | 27.272 | 0.0013
GEN-2017-150 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2615 | 21.2592 | -0.0023
GEN-2017-150 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.1501 | 10.1315 | -0.0186
GEN-2017-150 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3546 | 22.3446 | -0.01
GEN-2017-150 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 25.236 | 25.2247 | -0.0113
GEN-2017-150 | 04 SOUTHEAST | 515380 | INDIANH4 | 138 | 28.8689 | 28.8833 | 0.0144
GEN-2017-150 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2213 | 18.2176 | -0.0037
GEN-2017-150 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1969 | 10.1886 | -0.0083
GEN-2017-150 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.3028 | 23.6589 | 0.3561
GEN-2017-150 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5357 | 12.5308 | -0.0049
GEN-2017-150 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.676 | 20.6817 | 0.0057
GEN-2017-150 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.5233 | 7.5184 | -0.0049
GEN-2017-150 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2651 | 40.2784 | 0.0133
GEN-2017-150 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6065 | 21.6107 | 0.0042
GEN-2017-150 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 22.1412 | 22.1448 | 0.0036
GEN-2017-150 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.1966 | 14.1875 | -0.0091
GEN-2017-150 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8136 | 34.8833 | 0.0697
GEN-2017-150 | 04 SOUTHEAST | 515506 | OKRCHET2 | 69 | 3.7161 | 3.7157 | -0.0004
GEN-2017-150 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.5166 | 13.5135 | -0.0031
GEN-2017-150 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.6113 | 14.7334 | 0.1221
GEN-2017-150 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7083 | 8.7044 | -0.0039
GEN-2017-150 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.2507 | 14.2459 | -0.0048
GEN-2017-150 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.56 | 13.5526 | -0.0074
GEN-2017-150 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.2171 | 12.2222 | 0.0051
GEN-2017-150 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.3265 | 13.3343 | 0.0078
GEN-2017-150 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3178 | 18.3389 | 0.0211
GEN-2017-150 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.2985 | 19.3737 | 0.0752
GEN-2017-150 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.8914 | 33.9154 | 0.024
GEN-2017-150 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6865 | 14.6681 | -0.0184
GEN-2017-150 | 04 SOUTHEAST | 515864 | CMTRYRD4 | 138 | 6.7427 | 6.7416 | -0.0011
GEN-2017-150 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.9546 | 18.9562 | 0.0016
GEN-2017-150 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.9501 | 18.9517 | 0.0016
GEN-2017-150 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.4507 | 10.5052 | 0.0545
GEN-2017-150 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.2783 | 14.2753 | -0.003
GEN-2017-150 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 5.8218 | 5.8212 | -0.0006
GEN-2017-150 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8606 | 39.8724 | 0.0118
GEN-2017-150 | 04 SOUTHEAST | 515980 | MNCWND57 | 345 | 7.6865 | 7.7119 | 0.0254
GEN-2017-150 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.3726 | 7.3707 | -0.0019
GEN-2017-150 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.753 | 17.7518 | -0.0012
GEN-2017-150 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16.0019 | 15.9928 | -0.0091
GEN-2017-150 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 26.2194 | 26.2297 | 0.0103
GEN-2017-150 | 04 SOUTHEAST | 520440 | HARPER2 | 69 | 13.9106 | 13.9112 | 0.0006
GEN-2017-150 | 04 SOUTHEAST | 520473 | CKSHATP4 | 138 | 11.1669 | 11.166 | -0.0009
GEN-2017-150 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 12.8351 | 12.8354 | 0.0003
GEN-2017-150 | 04 SOUTHEAST | 520512 | BC SW 4 | 138 | 6.4543 | 6.4542 | -0.0001
GEN-2017-150 | 04 SOUTHEAST | 520513 | BCV SW 4 | 138 | 5.8846 | 5.8844 | -0.0002
GEN-2017-150 | 04 SOUTHEAST | 520514 | BCVI_HVB | 138 | 7.5576 | 7.5575 | -0.0001
GEN-2017-150 | 04 SOUTHEAST | 520530 | AMBERTP4 | 138 | 8.2847 | 8.2834 | -0.0013
GEN-2017-150 | 04 SOUTHEAST | 520547 | SEQOYAH4 | 138 | 20.5671 | 20.5734 | 0.0063
GEN-2017-150 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 14.6817 | 14.6824 | 0.0007
GEN-2017-150 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 36.8522 | 36.8738 | 0.0216
GEN-2017-150 | 04 SOUTHEAST | 520827 | BINGERJ4 | 138 | 7.9685 | 7.9683 | -0.0002
GEN-2017-150 | 04 SOUTHEAST | 520838 | CADDO 2 | 69 | 11.4811 | 11.4815 | 0.0004
GEN-2017-150 | 04 SOUTHEAST | 520859 | COGAR 4 | 138 | 9.2043 | 9.2034 | -0.0009
GEN-2017-150 | 04 SOUTHEAST | 520893 | EL RENO4 | 138 | 14.5902 | 14.5905 | 0.0003
GEN-2017-150 | 04 SOUTHEAST | 520912 | FLETCH-4 | 138 | 7.2283 | 7.2262 | -0.0021
GEN-2017-150 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 29.8787 | 29.8899 | 0.0112
GEN-2017-150 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 18.7649 | 18.769 | 0.0041
GEN-2017-150 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.2447 | 11.2453 | 0.0006
GEN-2017-150 | 04 SOUTHEAST | 521024 | PARADSE4 | 138 | 6.001 | 6.0007 | -0.0003
GEN-2017-150 | 04 SOUTHEAST | 521027 | PINERTP2 | 69 | 4.9226 | 4.9222 | -0.0004
GEN-2017-150 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.1875 | 8.1872 | -0.0003
GEN-2017-150 | 04 SOUTHEAST | 521072 | TUTLETP4 | 138 | 7.3452 | 7.3443 | -0.0009
GEN-2017-150 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.2705 | 9.2707 | 0.0002
GEN-2017-150 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.7981 | 30.8113 | 0.0132
GEN-2017-150 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 7.5778 | 7.5778 | 0
GEN-2017-150 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 6.3779 | 6.3777 | -0.0002
GEN-2017-150 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1095 | 27.1936 | 0.0841
GEN-2017-150 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.4704 | 9.4705 | 0.0001
GEN-2017-150 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5741 | 10.5911 | 0.017
GEN-2017-150 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.0482 | 9.048 | -0.0002
GEN-2017-150 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 10.9572 | 10.969 | 0.0118
GEN-2017-150 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.889 | 15.9213 | 0.0323
GEN-2017-150 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.441 | 11.454 | 0.013
GEN-2017-150 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.8443 | 11.8442 | -0.0001
GEN-2017-150 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.3699 | 16.3642 | -0.0057
GEN-2017-150 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.1568 | 10.1531 | -0.0037
GEN-2017-150 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.6681 | 3.6648 | -0.0033
GEN-2017-150 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3319 | 11.3287 | -0.0032
GEN-2017-150 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.5303 | 10.5253 | -0.005
GEN-2017-150 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.2918 | 6.2923 | 0.0005
GEN-2017-150 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.4206 | 11.4188 | -0.0018
GEN-2017-150 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.4206 | 11.4188 | -0.0018
GEN-2017-150 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.5614 | 22.9216 | 0.3602
GEN-2017-150 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.6067 | 22.9668 | 0.3601
GEN-2017-150 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.089 | 12.0893 | 0.0003
GEN-2017-150 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9689 | 2.9648 | -0.0041
GEN-2017-150 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.518 | 7.5147 | -0.0033
GEN-2017-150 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9865 | 11.9832 | -0.0033
GEN-2017-150 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0575 | 7.0577 | 0.0002
GEN-2017-150 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.664 | 5.6641 | 0.0001
GEN-2017-150 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.315 | 6.3151 | 0.0001
GEN-2017-150 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 36.2685 | 36.2969 | 0.0284
GEN-2017-151 | 05 SOUTHWEST | 511422 | FLETCHR4 | 138 | 7.9104 | 7.9027 | -0.0077
GEN-2017-151 | 05 SOUTHWEST | 511423 | FLE TAP4 | 138 | 8.6418 | 8.6334 | -0.0084
GEN-2017-151 | 05 SOUTHWEST | 511431 | LWS S4 | 138 | 10.9941 | 10.9754 | -0.0187
GEN-2017-151 | 05 SOUTHWEST | 511436 | COMANC-2 | 69 | 9.6952 | 9.6956 | 0.0004
GEN-2017-151 | 05 SOUTHWEST | 511437 | COMANC-4 | 138 | 17.9379 | 17.9399 | 0.002
GEN-2017-151 | 05 SOUTHWEST | 511439 | LWSTAP 4 | 138 | 11.4608 | 11.4413 | -0.0195
GEN-2017-151 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 5.2739 | 5.193 | -0.0809
GEN-2017-151 | 05 SOUTHWEST | 511466 | L.E.S.-2 | 69 | 16.2698 | 16.2493 | -0.0205
GEN-2017-151 | 05 SOUTHWEST | 511467 | L.E.S.-4 | 138 | 24.1599 | 24.1097 | -0.0502
GEN-2017-151 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 12.5289 | 12.4489 | -0.08
GEN-2017-151 | 05 SOUTHWEST | 511469 | LGORE-N2 | 69 | 8.0443 | 8.0341 | -0.0102
GEN-2017-151 | 05 SOUTHWEST | 511470 | LGORE-S2 | 69 | 7.0035 | 6.9944 | -0.0091
GEN-2017-151 | 05 SOUTHWEST | 511474 | SHERID4 | 138 | 12.2279 | 12.2053 | -0.0226
GEN-2017-151 | 05 SOUTHWEST | 511486 | ELGINJT4 | 138 | 10.0414 | 10.0299 | -0.0115
GEN-2017-151 | 05 SOUTHWEST | 511487 | ELGINJT2 | 69 | 8.6176 | 8.608 | -0.0096
GEN-2017-151 | 05 SOUTHWEST | 511488 | 112GORE4 | 138 | 12.5977 | 12.5783 | -0.0194
GEN-2017-151 | 05 SOUTHWEST | 511494 | COMMTAP4 | 138 | 21.1837 | 21.1479 | -0.0358
GEN-2017-151 | 05 SOUTHWEST | 511512 | RPPAPER4 | 138 | 11.8745 | 11.8553 | -0.0192
GEN-2017-151 | 05 SOUTHWEST | 511537 | ARTVLTP4 | 138 | 11.6189 | 11.5984 | -0.0205
GEN-2017-151 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 10.291 | 10.1899 | -0.1011
GEN-2017-151 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 11.2739 | 11.1684 | -0.1055
GEN-2017-151 | 05 SOUTHWEST | 511563 | ELSWORTH 4 | 138 | 9.9708 | 9.9597 | -0.0111
GEN-2017-151 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 5.2589 | 5.1782 | -0.0807
GEN-2017-151 | 05 SOUTHWEST | 511568 | TERRYRD7 | 345 | 9.0446 | 8.9922 | -0.0524
GEN-2017-151 | 05 SOUTHWEST | 511571 | RUSHSPR7 | 345 | 5.4933 | 5.4613 | -0.032
GEN-2017-151 | 05 SOUTHWEST | 511979 | RSHSPR1_MPT1 | 345 | 5.35 | 5.3188 | -0.0312
GEN-2017-151 | 05 SOUTHWEST | 514801 | MINCO 7 | 345 | 20.798 | 20.7514 | -0.0466
GEN-2017-151 | 05 SOUTHWEST | 515136 | SUNNYSD7 | 345 | 10.1887 | 10.1481 | -0.0406
GEN-2017-151 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 19.9583 | 19.8651 | -0.0932
GEN-2017-151 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 24.3395 | 24.2585 | -0.081
GEN-2017-151 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 17.2045 | 17.1423 | -0.0622
GEN-2017-151 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 7.3611 | 7.2671 | -0.094
GEN-2017-151 | 05 SOUTHWEST | 515599 | G07621119-20 | 345 | 12.0689 | 12.0119 | -0.057
GEN-2017-151 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 17.085 | 17.018 | -0.067
GEN-2017-151 | 05 SOUTHWEST | 515802 | GRACMNT4 | 138 | 32.7103 | 32.6879 | -0.0224
GEN-2017-151 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 14.2133 | 14.1587 | -0.0546
GEN-2017-151 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 12.0944 | 12.0373 | -0.0571
GEN-2017-151 | 05 SOUTHWEST | 516106 | BOBCAT 7 | 345 | 15.7766 | 15.6999 | -0.0767
GEN-2017-151 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 20.3417 | 20.3107 | -0.031
GEN-2017-151 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 25.1712 | 25.1787 | 0.0075
GEN-2017-151 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.3147 | 14.3126 | -0.0021
GEN-2017-151 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.563 | 16.5557 | -0.0073
GEN-2017-151 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.4058 | 13.4002 | -0.0056
GEN-2017-151 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.1469 | 6.1458 | -0.0011
GEN-2017-151 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.3919 | 7.3913 | -0.0006
GEN-2017-151 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 10.3784 | 10.3767 | -0.0017
GEN-2017-151 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 8.8723 | 8.8723 | 0
GEN-2017-151 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.7162 | 11.6874 | -0.0288
GEN-2017-151 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.1825 | 11.1549 | -0.0276
GEN-2017-151 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.2701 | 10.2536 | -0.0165
GEN-2017-151 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.366 | 6.352 | -0.014
GEN-2017-151 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.3756 | 7.361 | -0.0146
GEN-2017-151 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.616 | 6.5986 | -0.0174
GEN-2017-151 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.0245 | 10.0036 | -0.0209
GEN-2017-151 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.4926 | 14.4601 | -0.0325
GEN-2017-151 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.5697 | 10.5488 | -0.0209
GEN-2017-151 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 14.7164 | 14.7044 | -0.012
GEN-2017-151 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 22.1238 | 22.127 | 0.0032
GEN-2017-151 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 26.9744 | 27.0017 | 0.0273
GEN-2017-151 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 8.5631 | 8.5657 | 0.0026
GEN-2017-151 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 10.5059 | 10.5095 | 0.0036
GEN-2017-151 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 10.5059 | 10.5095 | 0.0036
GEN-2017-151 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.2577 | 8.2553 | -0.0024
GEN-2017-151 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4077 | 5.4075 | -0.0002
GEN-2017-151 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.045 | 3.0406 | -0.0044
GEN-2017-151 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4884 | 2.4845 | -0.0039
GEN-2017-151 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.8341 | 5.8239 | -0.0102
GEN-2017-151 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4756 | 5.4659 | -0.0097
GEN-2017-151 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.7143 | 6.7052 | -0.0091
GEN-2017-151 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.8688 | 5.8635 | -0.0053
GEN-2017-151 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.611 | 4.605 | -0.006
GEN-2017-151 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9027 | 7.8955 | -0.0072
GEN-2017-151 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.6643 | 19.7064 | 0.0421
GEN-2017-151 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.6931 | 21.9248 | 0.2317
GEN-2017-151 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 12.3237 | 12.5696 | 0.2459
GEN-2017-151 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.5155 | 21.7426 | 0.2271
GEN-2017-151 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 12.2057 | 12.446 | 0.2403
GEN-2017-151 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5779 | 2.5739 | -0.004
GEN-2017-151 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3534 | 3.3486 | -0.0048
GEN-2017-151 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.245 | 5.2419 | -0.0031
GEN-2017-151 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.7717 | 11.8094 | 0.0377
GEN-2017-151 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.9952 | 8.9953 | 0.0001
GEN-2017-151 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9864 | 10.9894 | 0.003
GEN-2017-151 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3692 | 9.3697 | 0.0005
GEN-2017-151 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.6973 | 2.695 | -0.0023
GEN-2017-151 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.7047 | 12.7108 | 0.0061
GEN-2017-151 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.428 | 10.4443 | 0.0163
GEN-2017-151 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.3366 | 11.3399 | 0.0033
GEN-2017-151 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.3691 | 10.3715 | 0.0024
GEN-2017-151 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 18.1879 | 18.2089 | 0.021
GEN-2017-151 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.7291 | 15.7633 | 0.0342
GEN-2017-151 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 8.3183 | 8.3171 | -0.0012
GEN-2017-151 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.9498 | 14.9624 | 0.0126
GEN-2017-151 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.5523 | 11.5706 | 0.0183
GEN-2017-151 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 17.6562 | 17.6997 | 0.0435
GEN-2017-151 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 10.9945 | 10.9991 | 0.0046
GEN-2017-151 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 9.6922 | 9.6946 | 0.0024
GEN-2017-151 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2235 | 11.2259 | 0.0024
GEN-2017-151 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 12.7444 | 12.764 | 0.0196
GEN-2017-151 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.1257 | 7.1286 | 0.0029
GEN-2017-151 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.2999 | 6.305 | 0.0051
GEN-2017-151 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.9497 | 4.9528 | 0.0031
GEN-2017-151 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 14.2206 | 14.2238 | 0.0032
GEN-2017-151 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0916 | 6.0903 | -0.0013
GEN-2017-151 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.23 | 10.2287 | -0.0013
GEN-2017-151 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 18.6177 | 18.6189 | 0.0012
GEN-2017-151 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 18.5124 | 18.5224 | 0.01
GEN-2017-151 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.7055 | 9.7109 | 0.0054
GEN-2017-151 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 14.5978 | 14.602 | 0.0042
GEN-2017-151 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 14.4695 | 14.4735 | 0.004
GEN-2017-151 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 14.2497 | 14.2534 | 0.0037
GEN-2017-151 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.2081 | 13.2071 | -0.001
GEN-2017-151 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 10.9909 | 10.9919 | 0.001
GEN-2017-151 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6074 | 13.6067 | -0.0007
GEN-2017-151 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 23.7427 | 23.745 | 0.0023
GEN-2017-151 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 15.7944 | 15.7983 | 0.0039
GEN-2017-151 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 15.7944 | 15.7983 | 0.0039
GEN-2017-151 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9981 | 7.9972 | -0.0009
GEN-2017-151 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 7.9126 | 7.9124 | -0.0002
GEN-2017-151 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 9.359 | 9.3605 | 0.0015
GEN-2017-151 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 9.1529 | 9.1543 | 0.0014
GEN-2017-151 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 10.3556 | 10.3578 | 0.0022
GEN-2017-151 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.1747 | 7.175 | 0.0003
GEN-2017-151 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.4248 | 17.4296 | 0.0048
GEN-2017-151 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 31.5218 | 31.5246 | 0.0028
GEN-2017-151 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.2715 | 19.2782 | 0.0067
GEN-2017-151 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 11.6918 | 11.6945 | 0.0027
GEN-2017-151 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.7107 | 8.7109 | 0.0002
GEN-2017-151 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 16.9768 | 16.976 | -0.0008
GEN-2017-151 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.7447 | 5.7439 | -0.0008
GEN-2017-151 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.8663 | 13.8643 | -0.002
GEN-2017-151 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.7224 | 8.7226 | 0.0002
GEN-2017-151 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.592 | 6.5913 | -0.0007
GEN-2017-151 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0781 | 6.0785 | 0.0004
GEN-2017-151 | 05 SOUTHWEST | 529304 | OMDUNCN4 | 138 | 6.5085 | 6.4935 | -0.015
GEN-2017-151 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 9.1624 | 9.1012 | -0.0612
GEN-2017-151 | 05 SOUTHWEST | 563269 | GEN-2015-093 | 345 | 9.6231 | 9.5842 | -0.0389
GEN-2017-151 | 05 SOUTHWEST | 587740 | GEN-2016-091 | 345 | 9.7594 | 9.7141 | -0.0453
GEN-2017-151 | 05 SOUTHWEST | 587744 | G16-091-TAP | 345 | 13.8653 | 13.8018 | -0.0635
GEN-2017-151 | 05 SOUTHWEST | 587770 | GEN-2016-095 | 345 | 10.0903 | 10.0435 | -0.0468
GEN-2017-151 | 05 SOUTHWEST | 587794 | G16-097-TAP | 138 | 10.8522 | 10.8473 | -0.0049
GEN-2017-151 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 3.9501 | 3.8982 | -0.0519
GEN-2017-151 | 05 SOUTHWEST | 590001 | OKLEHV24 | 138 | 5.0489 | 5.0489 | 0
GEN-2017-151 | 05 SOUTHWEST | 590003 | OKLEHV14 | 138 | 5.1608 | 5.1608 | 0
GEN-2017-151 | 05 SOUTHWEST | 599891 | OKLAUN 7 | 345 | 4.262 | 4.262 | 0
GEN-2017-151 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 8.8723 | 8.8723 | 0
GEN-2017-151 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 10.2738 | 10.1722 | -0.1016
GEN-2017-151 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.6141 | 7.5987 | -0.0154
GEN-2017-151 | 05 SOUTHWEST | 760938 | G17-171-TAP | 345 | 10.1993 | 10.1393 | -0.06
GEN-2017-151 | 05 SOUTHWEST | 760939 | GEN-2017-171 | 345 | 10.1993 | 10.1393 | -0.06
GEN-2017-151 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 12.2991 | 12.3044 | 0.0053
GEN-2017-151 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 7.187 | 7.5051 | 0.3181
GEN-2017-151 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 5.276 | 5.6326 | 0.3566
GEN-2017-158 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 5.2589 | 5.193 | -0.0659
GEN-2017-158 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 12.5119 | 12.4489 | -0.063
GEN-2017-158 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 10.2855 | 10.1899 | -0.0956
GEN-2017-158 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 5.2438 | 5.1782 | -0.0656
GEN-2017-158 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 19.9584 | 19.8651 | -0.0933
GEN-2017-158 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 7.3533 | 7.2671 | -0.0862
GEN-2017-158 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.6627 | 14.61 | -0.0527
GEN-2017-158 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1959 | 3.1865 | -0.0094
GEN-2017-158 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.4033 | 4.396 | -0.0073
GEN-2017-158 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.9663 | 6.9435 | -0.0228
GEN-2017-158 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.754 | 9.7319 | -0.0221
GEN-2017-158 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9743 | 8.9501 | -0.0242
GEN-2017-158 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.1636 | 7.1597 | -0.0039
GEN-2017-158 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.7009 | 5.6583 | -0.0426
GEN-2017-158 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2332 | 4.2217 | -0.0115
GEN-2017-158 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 20.3457 | 20.3107 | -0.035
GEN-2017-158 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 7.4223 | 7.3999 | -0.0224
GEN-2017-158 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 25.9458 | 25.9565 | 0.0107
GEN-2017-158 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 25.9458 | 25.9565 | 0.0107
GEN-2017-158 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 25.9458 | 25.9565 | 0.0107
GEN-2017-158 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.2232 | 19.2181 | -0.0051
GEN-2017-158 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 19.212 | 19.2009 | -0.0111
GEN-2017-158 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 29.5803 | 29.5881 | 0.0078
GEN-2017-158 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 25.1686 | 25.1787 | 0.0101
GEN-2017-158 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 9.3264 | 9.3115 | -0.0149
GEN-2017-158 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 9.6407 | 9.6174 | -0.0233
GEN-2017-158 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.6401 | 6.6247 | -0.0154
GEN-2017-158 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 4.0843 | 4.0715 | -0.0128
GEN-2017-158 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 20.5685 | 20.5561 | -0.0124
GEN-2017-158 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.3141 | 14.3126 | -0.0015
GEN-2017-158 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.1681 | 15.1591 | -0.009
GEN-2017-158 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.4946 | 13.4878 | -0.0068
GEN-2017-158 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 14.788 | 14.7795 | -0.0085
GEN-2017-158 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.5644 | 16.5557 | -0.0087
GEN-2017-158 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.4055 | 13.4002 | -0.0053
GEN-2017-158 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.7757 | 2.7753 | -0.0004
GEN-2017-158 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 3.1109 | 3.1107 | -0.0002
GEN-2017-158 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.5303 | 2.5302 | -0.0001
GEN-2017-158 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.3626 | 6.3582 | -0.0044
GEN-2017-158 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.4936 | 11.4628 | -0.0308
GEN-2017-158 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.4953 | 11.4645 | -0.0308
GEN-2017-158 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 7.91 | 7.891 | -0.019
GEN-2017-158 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 11.7996 | 11.7685 | -0.0311
GEN-2017-158 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 4.6984 | 4.6873 | -0.0111
GEN-2017-158 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 5.5209 | 5.5166 | -0.0043
GEN-2017-158 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.7418 | 4.7329 | -0.0089
GEN-2017-158 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.7439 | 9.7291 | -0.0148
GEN-2017-158 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 9.0529 | 9.0368 | -0.0161
GEN-2017-158 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 10.3422 | 10.3279 | -0.0143
GEN-2017-158 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.8943 | 8.8834 | -0.0109
GEN-2017-158 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 10.692 | 10.7046 | 0.0126
GEN-2017-158 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.1809 | 10.1935 | 0.0126
GEN-2017-158 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.1341 | 6.1458 | 0.0117
GEN-2017-158 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.6175 | 8.6244 | 0.0069
GEN-2017-158 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.3068 | 7.3115 | 0.0047
GEN-2017-158 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.5902 | 6.5935 | 0.0033
GEN-2017-158 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4681 | 2.466 | -0.0021
GEN-2017-158 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 5.8914 | 5.8937 | 0.0023
GEN-2017-158 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.3725 | 6.3759 | 0.0034
GEN-2017-158 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 9.8039 | 9.8136 | 0.0097
GEN-2017-158 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.8105 | 6.8141 | 0.0036
GEN-2017-158 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4392 | 4.4365 | -0.0027
GEN-2017-158 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 10.7204 | 10.7332 | 0.0128
GEN-2017-158 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 8.8991 | 8.9071 | 0.008
GEN-2017-158 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.1759 | 10.1869 | 0.011
GEN-2017-158 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1549 | 2.153 | -0.0019
GEN-2017-158 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 7.6932 | 7.6986 | 0.0054
GEN-2017-158 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 9.4382 | 9.4504 | 0.0122
GEN-2017-158 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.3735 | 7.3913 | 0.0178
GEN-2017-158 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.7482 | 4.7478 | -0.0004
GEN-2017-158 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.5527 | 4.552 | -0.0007
GEN-2017-158 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 10.3596 | 10.3767 | 0.0171
GEN-2017-158 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 8.839 | 8.8723 | 0.0333
GEN-2017-158 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.4258 | 7.4271 | 0.0013
GEN-2017-158 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.2889 | 7.2951 | 0.0062
GEN-2017-158 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.4258 | 7.4271 | 0.0013
GEN-2017-158 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.4911 | 5.4905 | -0.0006
GEN-2017-158 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.0002 | 6.0034 | 0.0032
GEN-2017-158 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7065 | 5.7061 | -0.0004
GEN-2017-158 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.6481 | 5.6507 | 0.0026
GEN-2017-158 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.5695 | 5.5719 | 0.0024
GEN-2017-158 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 4.7934 | 4.7927 | -0.0007
GEN-2017-158 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.1031 | 5.1027 | -0.0004
GEN-2017-158 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 4.6769 | 4.6745 | -0.0024
GEN-2017-158 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.004 | 5.0034 | -0.0006
GEN-2017-158 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.6121 | 7.604 | -0.0081
GEN-2017-158 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 7.8643 | 7.8582 | -0.0061
GEN-2017-158 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.386 | 7.3657 | -0.0203
GEN-2017-158 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.476 | 6.455 | -0.021
GEN-2017-158 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4361 | 4.4198 | -0.0163
GEN-2017-158 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.7237 | 11.6874 | -0.0363
GEN-2017-158 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.1898 | 11.1549 | -0.0349
GEN-2017-158 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.2782 | 10.2536 | -0.0246
GEN-2017-158 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4297 | 6.409 | -0.0207
GEN-2017-158 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.3064 | 5.2909 | -0.0155
GEN-2017-158 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.2347 | 6.2173 | -0.0174
GEN-2017-158 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5837 | 2.5758 | -0.0079
GEN-2017-158 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.2617 | 3.2523 | -0.0094
GEN-2017-158 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.3682 | 6.352 | -0.0162
GEN-2017-158 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.2043 | 2.1992 | -0.0051
GEN-2017-158 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 8.0789 | 8.0746 | -0.0043
GEN-2017-158 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 4.7597 | 4.7476 | -0.0121
GEN-2017-158 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.3764 | 7.361 | -0.0154
GEN-2017-158 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.668 | 5.6519 | -0.0161
GEN-2017-158 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 6.8352 | 6.8236 | -0.0116
GEN-2017-158 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 8.9404 | 8.9369 | -0.0035
GEN-2017-158 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.6169 | 6.5986 | -0.0183
GEN-2017-158 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.0265 | 10.0036 | -0.0229
GEN-2017-158 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.4972 | 14.4601 | -0.0371
GEN-2017-158 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.5714 | 10.5488 | -0.0226
GEN-2017-158 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 14.6859 | 14.7044 | 0.0185
GEN-2017-158 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 21.9074 | 22.127 | 0.2196
GEN-2017-158 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 26.4262 | 27.0017 | 0.5755
GEN-2017-158 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 8.5222 | 8.5657 | 0.0435
GEN-2017-158 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 9.9085 | 9.9669 | 0.0584
GEN-2017-158 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 10.4442 | 10.5095 | 0.0653
GEN-2017-158 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 10.4442 | 10.5095 | 0.0653
GEN-2017-158 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3855 | 2.3858 | 0.0003
GEN-2017-158 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 3.0103 | 3.0109 | 0.0006
GEN-2017-158 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1591 | 4.1606 | 0.0015
GEN-2017-158 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.9072 | 5.9107 | 0.0035
GEN-2017-158 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.2413 | 8.2553 | 0.014
GEN-2017-158 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.3942 | 5.4075 | 0.0133
GEN-2017-158 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9609 | 4.9631 | 0.0022
GEN-2017-158 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1435 | 4.145 | 0.0015
GEN-2017-158 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6237 | 4.6256 | 0.0019
GEN-2017-158 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4552 | 3.4561 | 0.0009
GEN-2017-158 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.2331 | 2.227 | -0.0061
GEN-2017-158 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0488 | 3.0406 | -0.0082
GEN-2017-158 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4915 | 2.4845 | -0.007
GEN-2017-158 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4634 | 2.4565 | -0.0069
GEN-2017-158 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.8366 | 5.8239 | -0.0127
GEN-2017-158 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4773 | 5.4659 | -0.0114
GEN-2017-158 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.7181 | 6.7052 | -0.0129
GEN-2017-158 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.5951 | 2.5892 | -0.0059
GEN-2017-158 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 5.8705 | 5.8626 | -0.0079
GEN-2017-158 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.8714 | 5.8635 | -0.0079
GEN-2017-158 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.3649 | 4.3553 | -0.0096
GEN-2017-158 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6172 | 4.605 | -0.0122
GEN-2017-158 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9158 | 7.8955 | -0.0203
GEN-2017-158 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.7466 | 19.7064 | -0.0402
GEN-2017-158 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9571 | 21.9248 | -0.0323
GEN-2017-158 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 12.631 | 12.5696 | -0.0614
GEN-2017-158 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.7748 | 21.7426 | -0.0322
GEN-2017-158 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 12.5068 | 12.446 | -0.0608
GEN-2017-158 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5811 | 2.5739 | -0.0072
GEN-2017-158 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.289 | 2.2826 | -0.0064
GEN-2017-158 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3578 | 3.3486 | -0.0092
GEN-2017-158 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.69 | 2.6826 | -0.0074
GEN-2017-158 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 5.2255 | 5.2198 | -0.0057
GEN-2017-158 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.2476 | 5.2419 | -0.0057
GEN-2017-158 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.8296 | 11.8094 | -0.0202
GEN-2017-158 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.3578 | 4.3562 | -0.0016
GEN-2017-158 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.2375 | 5.236 | -0.0015
GEN-2017-158 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.5192 | 5.5192 | 0
GEN-2017-158 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.8175 | 5.8169 | -0.0006
GEN-2017-158 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.3018 | 2.3006 | -0.0012
GEN-2017-158 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.3552 | 4.3537 | -0.0015
GEN-2017-158 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.0086 | 8.9953 | -0.0133
GEN-2017-158 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 11.0024 | 10.9894 | -0.013
GEN-2017-158 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.2003 | 2.1971 | -0.0032
GEN-2017-158 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3829 | 9.3697 | -0.0132
GEN-2017-158 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.6989 | 2.695 | -0.0039
GEN-2017-158 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.7239 | 12.7108 | -0.0131
GEN-2017-158 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.4539 | 10.4443 | -0.0096
GEN-2017-158 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.3521 | 11.3399 | -0.0122
GEN-2017-158 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 8.8991 | 8.8888 | -0.0103
GEN-2017-158 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.2648 | 2.2615 | -0.0033
GEN-2017-158 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.3812 | 10.3715 | -0.0097
GEN-2017-158 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 9.8032 | 9.7949 | -0.0083
GEN-2017-158 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.6897 | 10.6844 | -0.0053
GEN-2017-158 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.2587 | 4.257 | -0.0017
GEN-2017-158 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 18.2106 | 18.2089 | -0.0017
GEN-2017-158 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.7576 | 15.7633 | 0.0057
GEN-2017-158 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 5.9146 | 5.9105 | -0.0041
GEN-2017-158 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 8.3226 | 8.3171 | -0.0055
GEN-2017-158 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.969 | 14.9624 | -0.0066
GEN-2017-158 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.568 | 11.5706 | 0.0026
GEN-2017-158 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.508 | 5.5041 | -0.0039
GEN-2017-158 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 17.6908 | 17.6997 | 0.0089
GEN-2017-158 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 7.1751 | 7.1719 | -0.0032
GEN-2017-158 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.5154 | 9.5116 | -0.0038
GEN-2017-158 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 11.0006 | 10.9969 | -0.0037
GEN-2017-158 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 10.9961 | 10.9991 | 0.003
GEN-2017-158 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.3287 | 10.3247 | -0.004
GEN-2017-158 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.482 | 6.4781 | -0.0039
GEN-2017-158 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 9.6944 | 9.6946 | 0.0002
GEN-2017-158 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.744 | 10.7323 | -0.0117
GEN-2017-158 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.9044 | 10.8926 | -0.0118
GEN-2017-158 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.3205 | 9.3159 | -0.0046
GEN-2017-158 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2372 | 11.2259 | -0.0113
GEN-2017-158 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 12.7659 | 12.764 | -0.0019
GEN-2017-158 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.467 | 2.4651 | -0.0019
GEN-2017-158 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.3718 | 9.3697 | -0.0021
GEN-2017-158 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 6.1165 | 6.1158 | -0.0007
GEN-2017-158 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.1288 | 7.1286 | -0.0002
GEN-2017-158 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.3042 | 6.305 | 0.0008
GEN-2017-158 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.9524 | 4.9528 | 0.0004
GEN-2017-158 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 2.8876 | 2.8873 | -0.0003
GEN-2017-158 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.7998 | 10.7917 | -0.0081
GEN-2017-158 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 14.2246 | 14.2238 | -0.0008
GEN-2017-158 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0952 | 6.0903 | -0.0049
GEN-2017-158 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.2332 | 10.2287 | -0.0045
GEN-2017-158 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 18.624 | 18.6189 | -0.0051
GEN-2017-158 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 18.5207 | 18.5224 | 0.0017
GEN-2017-158 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.7189 | 9.7109 | -0.008
GEN-2017-158 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 8.2422 | 8.2384 | -0.0038
GEN-2017-158 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 14.603 | 14.602 | -0.001
GEN-2017-158 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 14.4746 | 14.4735 | -0.0011
GEN-2017-158 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 14.2543 | 14.2534 | -0.0009
GEN-2017-158 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.7055 | 13.7017 | -0.0038
GEN-2017-158 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.2094 | 13.2071 | -0.0023
GEN-2017-158 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 10.9928 | 10.9919 | -0.0009
GEN-2017-158 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2567 | 12.2543 | -0.0024
GEN-2017-158 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6106 | 13.6067 | -0.0039
GEN-2017-158 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8712 | 10.8676 | -0.0036
GEN-2017-158 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.5888 | 16.5855 | -0.0033
GEN-2017-158 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.2313 | 22.2293 | -0.002
GEN-2017-158 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.2313 | 22.2293 | -0.002
GEN-2017-158 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 23.7464 | 23.745 | -0.0014
GEN-2017-158 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 15.7982 | 15.7983 | 0.0001
GEN-2017-158 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 15.7982 | 15.7983 | 0.0001
GEN-2017-158 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.0002 | 7.9972 | -0.003
GEN-2017-158 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.2038 | 9.2008 | -0.003
GEN-2017-158 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.0133 | 14.0105 | -0.0028
GEN-2017-158 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 7.9141 | 7.9124 | -0.0017
GEN-2017-158 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 6.6386 | 6.6374 | -0.0012
GEN-2017-158 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.2301 | 4.2294 | -0.0007
GEN-2017-158 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 9.3523 | 9.3605 | 0.0082
GEN-2017-158 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 9.3523 | 9.3605 | 0.0082
GEN-2017-158 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 9.3523 | 9.3605 | 0.0082
GEN-2017-158 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.1387 | 8.144 | 0.0053
GEN-2017-158 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 9.1464 | 9.1543 | 0.0079
GEN-2017-158 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 10.3462 | 10.3578 | 0.0116
GEN-2017-158 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 8.1387 | 8.144 | 0.0053
GEN-2017-158 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 8.1387 | 8.144 | 0.0053
GEN-2017-158 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.7977 | 11.7975 | -0.0002
GEN-2017-158 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.7977 | 11.7975 | -0.0002
GEN-2017-158 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.2851 | 9.2865 | 0.0014
GEN-2017-158 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.1739 | 7.175 | 0.0011
GEN-2017-158 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.4226 | 17.4296 | 0.007
GEN-2017-158 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.4226 | 17.4296 | 0.007
GEN-2017-158 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 31.5187 | 31.5246 | 0.0059
GEN-2017-158 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.2689 | 19.2782 | 0.0093
GEN-2017-158 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 11.6901 | 11.6945 | 0.0044
GEN-2017-158 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.7094 | 8.7109 | 0.0015
GEN-2017-158 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 16.9756 | 16.976 | 0.0004
GEN-2017-158 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.7444 | 5.7439 | -0.0005
GEN-2017-158 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.8658 | 13.8643 | -0.0015
GEN-2017-158 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.7214 | 8.7226 | 0.0012
GEN-2017-158 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3481 | 6.3481 | 0
GEN-2017-158 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5915 | 6.5913 | -0.0002
GEN-2017-158 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.0068 | 9.0053 | -0.0015
GEN-2017-158 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0778 | 6.0785 | 0.0007
GEN-2017-158 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.633 | 3.6307 | -0.0023
GEN-2017-158 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.2094 | 13.2071 | -0.0023
GEN-2017-158 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 3.941 | 3.8982 | -0.0428
GEN-2017-158 | 05 SOUTHWEST | 599950 | LAMAR7 | 345 | 2.4031 | 2.3967 | -0.0064
GEN-2017-158 | 05 SOUTHWEST | 599951 | LAMAR 6 | 345 | 57.7912 | 57.7912 | 0
GEN-2017-158 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 8.839 | 8.8723 | 0.0333
GEN-2017-158 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.2851 | 9.2865 | 0.0014
GEN-2017-158 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 10.2682 | 10.1722 | -0.096
GEN-2017-158 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.3308 | 7.3179 | -0.0129
GEN-2017-158 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.6118 | 7.5987 | -0.0131
GEN-2017-158 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 12.8932 | 12.8918 | -0.0014
GEN-2017-158 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 11.7335 | 12.3044 | 0.5709
GEN-2017-158 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 7.5713 | 7.5051 | -0.0662
GEN-2017-158 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 5.6783 | 5.6326 | -0.0457
GEN-2017-164 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 22.6348 | 22.6286 | -0.0062
GEN-2017-164 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3296 | 22.325 | -0.0046
GEN-2017-164 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 32.6052 | 32.598 | -0.0072
GEN-2017-164 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7785 | 31.7758 | -0.0027
GEN-2017-164 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 25.9884 | 25.9854 | -0.003
GEN-2017-164 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.2292 | 19.2264 | -0.0028
GEN-2017-164 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.2813 | 15.2773 | -0.004
GEN-2017-164 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.0375 | 24.0314 | -0.0061
GEN-2017-164 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.6921 | 22.6892 | -0.0029
GEN-2017-164 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.0901 | 33.0888 | -0.0013
GEN-2017-164 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 34.8449 | 34.8369 | -0.008
GEN-2017-164 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.0779 | 19.0791 | 0.0012
GEN-2017-164 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5808 | 10.5801 | -0.0007
GEN-2017-164 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.1183 | 15.112 | -0.0063
GEN-2017-164 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 15.7193 | 15.7128 | -0.0065
GEN-2017-164 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 16.8046 | 16.7956 | -0.009
GEN-2017-164 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.0438 | 20.0423 | -0.0015
GEN-2017-164 | 04 SOUTHEAST | 514642 | BRCKWND4 | 138 | 8.5913 | 8.5963 | 0.005
GEN-2017-164 | 04 SOUTHEAST | 514701 | BUNCHCK4 | 138 | 6.7543 | 6.7544 | 0.0001
GEN-2017-164 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 20.9193 | 20.9242 | 0.0049
GEN-2017-164 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.132 | 4.1315 | -0.0005
GEN-2017-164 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 11.8675 | 11.8685 | 0.001
GEN-2017-164 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.5253 | 11.5263 | 0.001
GEN-2017-164 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.57 | 11.5768 | 0.0068
GEN-2017-164 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.8632 | 19.9034 | 0.0402
GEN-2017-164 | 04 SOUTHEAST | 514710 | WAUKOMI4 | 138 | 11.0884 | 11.0963 | 0.0079
GEN-2017-164 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 16.9947 | 17.0202 | 0.0255
GEN-2017-164 | 04 SOUTHEAST | 514712 | FAIRMON4 | 138 | 15.2812 | 15.3017 | 0.0205
GEN-2017-164 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 9.3376 | 9.3389 | 0.0013
GEN-2017-164 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.3536 | 21.4024 | 0.0488
GEN-2017-164 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.4946 | 20.9135 | 0.4189
GEN-2017-164 | 04 SOUTHEAST | 514718 | VANCE 2 | 69 | 7.1907 | 7.1923 | 0.0016
GEN-2017-164 | 04 SOUTHEAST | 514721 | IMO 2 | 69 | 12.418 | 12.4233 | 0.0053
GEN-2017-164 | 04 SOUTHEAST | 514722 | CLEVETP2 | 69 | 12.2005 | 12.2057 | 0.0052
GEN-2017-164 | 04 SOUTHEAST | 514727 | ENID 2 | 69 | 11.2506 | 11.2551 | 0.0045
GEN-2017-164 | 04 SOUTHEAST | 514730 | SO4TH 2 | 69 | 14.4056 | 14.4132 | 0.0076
GEN-2017-164 | 04 SOUTHEAST | 514731 | SO4TH 4 | 138 | 16.6121 | 16.636 | 0.0239
GEN-2017-164 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.2265 | 8.2308 | 0.0043
GEN-2017-164 | 04 SOUTHEAST | 514734 | GLENWD 4 | 138 | 10.8673 | 10.8763 | 0.009
GEN-2017-164 | 04 SOUTHEAST | 514743 | OSAGE 4 | 138 | 17.178 | 17.1769 | -0.0011
GEN-2017-164 | 04 SOUTHEAST | 514774 | HENESEY4 | 138 | 9.9662 | 9.9699 | 0.0037
GEN-2017-164 | 04 SOUTHEAST | 514789 | MENOTAP4 | 138 | 7.2477 | 7.2512 | 0.0035
GEN-2017-164 | 04 SOUTHEAST | 514790 | IMO 4 | 138 | 12.6319 | 12.6443 | 0.0124
GEN-2017-164 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 20.9617 | 20.9664 | 0.0047
GEN-2017-164 | 04 SOUTHEAST | 514799 | SNRPMP 4 | 138 | 11.5098 | 11.5109 | 0.0011
GEN-2017-164 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7511 | 23.7553 | 0.0042
GEN-2017-164 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.5437 | 32.5575 | 0.0138
GEN-2017-164 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3377 | 29.381 | 0.0433
GEN-2017-164 | 04 SOUTHEAST | 514815 | BRECKNR4 | 138 | 15.1586 | 15.1777 | 0.0191
GEN-2017-164 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.252 | 17.252 | 0
GEN-2017-164 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.7141 | 18.7141 | 0
GEN-2017-164 | 04 SOUTHEAST | 514825 | KAYWIND7 | 345 | 13.1604 | 13.149 | -0.0114
GEN-2017-164 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5328 | 18.5361 | 0.0033
GEN-2017-164 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 27.4358 | 27.4391 | 0.0033
GEN-2017-164 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.499 | 12.4993 | 0.0003
GEN-2017-164 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.2184 | 9.2171 | -0.0013
GEN-2017-164 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 14.8214 | 14.8223 | 0.0009
GEN-2017-164 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.7865 | 32.7917 | 0.0052
GEN-2017-164 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.616 | 27.6188 | 0.0028
GEN-2017-164 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.3328 | 23.3345 | 0.0017
GEN-2017-164 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.0668 | 28.0702 | 0.0034
GEN-2017-164 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.9854 | 45.9997 | 0.0143
GEN-2017-164 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2914 | 34.3238 | 0.0324
GEN-2017-164 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1244 | 24.1374 | 0.013
GEN-2017-164 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.5967 | 29.6006 | 0.0039
GEN-2017-164 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.1291 | 20.1299 | 0.0008
GEN-2017-164 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.7098 | 46.7216 | 0.0118
GEN-2017-164 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8177 | 36.8533 | 0.0356
GEN-2017-164 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8434 | 20.8437 | 0.0003
GEN-2017-164 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.3291 | 42.338 | 0.0089
GEN-2017-164 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.3668 | 27.375 | 0.0082
GEN-2017-164 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.4354 | 26.4422 | 0.0068
GEN-2017-164 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4424 | 45.4476 | 0.0052
GEN-2017-164 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0085 | 26.0139 | 0.0054
GEN-2017-164 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 14.2306 | 14.2303 | -0.0003
GEN-2017-164 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.3483 | 14.3465 | -0.0018
GEN-2017-164 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4592 | 28.4632 | 0.004
GEN-2017-164 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.4137 | 14.4148 | 0.0011
GEN-2017-164 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3516 | 22.3446 | -0.007
GEN-2017-164 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 25.2337 | 25.2247 | -0.009
GEN-2017-164 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.8421 | 10.843 | 0.0009
GEN-2017-164 | 04 SOUTHEAST | 515383 | ENIDINT4 | 138 | 14.1045 | 14.1208 | 0.0163
GEN-2017-164 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2198 | 18.2176 | -0.0022
GEN-2017-164 | 04 SOUTHEAST | 515412 | DMNCRKT4 | 138 | 14.099 | 14.0996 | 0.0006
GEN-2017-164 | 04 SOUTHEAST | 515426 | RDRUNNR4 | 138 | 8.7499 | 8.7492 | -0.0007
GEN-2017-164 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.6546 | 23.6589 | 0.0043
GEN-2017-164 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.2581 | 14.2578 | -0.0003
GEN-2017-164 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5342 | 12.5308 | -0.0034
GEN-2017-164 | 04 SOUTHEAST | 515456 | CHSTNTT2 | 69 | 11.9059 | 11.9108 | 0.0049
GEN-2017-164 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2703 | 40.2784 | 0.0081
GEN-2017-164 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6089 | 21.6107 | 0.0018
GEN-2017-164 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.102 | 14.1875 | 0.0855
GEN-2017-164 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 14.0826 | 14.1678 | 0.0852
GEN-2017-164 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.827 | 34.8833 | 0.0563
GEN-2017-164 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.8343 | 12.8527 | 0.0184
GEN-2017-164 | 04 SOUTHEAST | 515544 | RENFROW4 | 138 | 14.3663 | 14.3612 | -0.0051
GEN-2017-164 | 04 SOUTHEAST | 515546 | GRANTCO4 | 138 | 6.5189 | 6.5132 | -0.0057
GEN-2017-164 | 04 SOUTHEAST | 515547 | GRANTCO2 | 69 | 7.5445 | 7.5382 | -0.0063
GEN-2017-164 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7327 | 14.7334 | 0.0007
GEN-2017-164 | 04 SOUTHEAST | 515569 | MDFRDTP4 | 138 | 11.6012 | 11.5957 | -0.0055
GEN-2017-164 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.945 | 14.9364 | -0.0086
GEN-2017-164 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7071 | 8.7044 | -0.0027
GEN-2017-164 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.2492 | 14.2459 | -0.0033
GEN-2017-164 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.5579 | 13.5526 | -0.0053
GEN-2017-164 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.2216 | 12.2222 | 0.0006
GEN-2017-164 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.333 | 13.3343 | 0.0013
GEN-2017-164 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3343 | 18.3389 | 0.0046
GEN-2017-164 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 13.198 | 13.1865 | -0.0115
GEN-2017-164 | 04 SOUTHEAST | 515641 | PLNSMEN4 | 138 | 15.1263 | 15.1462 | 0.0199
GEN-2017-164 | 04 SOUTHEAST | 515646 | GRNTWD 7 | 345 | 11.2585 | 11.2695 | 0.011
GEN-2017-164 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 12.092 | 12.0835 | -0.0085
GEN-2017-164 | 04 SOUTHEAST | 515694 | ARMFTWD4 | 138 | 11.5394 | 11.5462 | 0.0068
GEN-2017-164 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3746 | 19.3737 | -0.0009
GEN-2017-164 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6812 | 14.6681 | -0.0131
GEN-2017-164 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.8285 | 18.9562 | 0.1277
GEN-2017-164 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.8241 | 18.9517 | 0.1276
GEN-2017-164 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 11.8238 | 11.825 | 0.0012
GEN-2017-164 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.2774 | 14.2753 | -0.0021
GEN-2017-164 | 04 SOUTHEAST | 515978 | OTOETAP4 | 138 | 16.692 | 16.6949 | 0.0029
GEN-2017-164 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.3365 | 7.3707 | 0.0342
GEN-2017-164 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.6151 | 17.7518 | 0.1367
GEN-2017-164 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.553 | 17.6889 | 0.1359
GEN-2017-164 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 11.694 | 11.6857 | -0.0083
GEN-2017-164 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16 | 15.9928 | -0.0072
GEN-2017-164 | 04 SOUTHEAST | 520409 | WFEC_RNFRO4 | 138 | 10.6361 | 10.6286 | -0.0075
GEN-2017-164 | 04 SOUTHEAST | 520434 | WAKTASW4 | 138 | 6.284 | 6.2774 | -0.0066
GEN-2017-164 | 04 SOUTHEAST | 520461 | GARBER 4 | 138 | 4.6698 | 4.6698 | 0
GEN-2017-164 | 04 SOUTHEAST | 520535 | BULFTTP4 | 138 | 9.2797 | 9.2825 | 0.0028
GEN-2017-164 | 04 SOUTHEAST | 520882 | DOVERSW4 | 138 | 10.8772 | 10.8807 | 0.0035
GEN-2017-164 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.2265 | 8.2308 | 0.0043
GEN-2017-164 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.1063 | 10.1072 | 0.0009
GEN-2017-164 | 04 SOUTHEAST | 521100 | WARREN 4 | 138 | 6.5655 | 6.5659 | 0.0004
GEN-2017-164 | 04 SOUTHEAST | 522397 | MEDFORD4 | 138 | 7.6045 | 7.5987 | -0.0058
GEN-2017-164 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 14.9155 | 14.9069 | -0.0086
GEN-2017-164 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 10.741 | 10.7276 | -0.0134
GEN-2017-164 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 20.0435 | 20.0223 | -0.0212
GEN-2017-164 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 18.5242 | 18.5082 | -0.016
GEN-2017-164 | 04 SOUTHEAST | 532792 | FR2EAST7 | 345 | 6.1807 | 6.1722 | -0.0085
GEN-2017-164 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.3269 | 23.3041 | -0.0228
GEN-2017-164 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.3802 | 13.3641 | -0.0161
GEN-2017-164 | 04 SOUTHEAST | 532803 | EXPEDITION7 | 345 | 9.906 | 9.8967 | -0.0093
GEN-2017-164 | 04 SOUTHEAST | 532984 | SUMNER 4 | 138 | 11.7048 | 11.6934 | -0.0114
GEN-2017-164 | 04 SOUTHEAST | 533036 | CLEARWT4 | 138 | 13.8798 | 13.8548 | -0.025
GEN-2017-164 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 28.9921 | 28.9605 | -0.0316
GEN-2017-164 | 04 SOUTHEAST | 533047 | GILL 4 | 138 | 21.2619 | 21.2316 | -0.0303
GEN-2017-164 | 04 SOUTHEAST | 533075 | VIOLA 4 | 138 | 23.4765 | 23.4388 | -0.0377
GEN-2017-164 | 04 SOUTHEAST | 539008 | MILAN_GOAB | 138 | 11.6363 | 11.613 | -0.0233
GEN-2017-164 | 04 SOUTHEAST | 539009 | CONWAY | 138 | 11.1417 | 11.1193 | -0.0224
GEN-2017-164 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.187 | 27.1936 | 0.0066
GEN-2017-164 | 04 SOUTHEAST | 560053 | G15-052T | 345 | 13.18 | 13.1639 | -0.0161
GEN-2017-164 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5594 | 19.5659 | 0.0065
GEN-2017-164 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 32.6052 | 32.598 | -0.0072
GEN-2017-164 | 04 SOUTHEAST | 562476 | G14-001-TAP | 345 | 9.874 | 9.8648 | -0.0092
GEN-2017-164 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 19.3668 | 19.3731 | 0.0063
GEN-2017-164 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 8.0067 | 8.0069 | 0.0002
GEN-2017-164 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.359 | 16.3642 | 0.0052
GEN-2017-164 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.153 | 10.1531 | 0.0001
GEN-2017-164 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.7622 | 8.7618 | -0.0004
GEN-2017-164 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 6.8098 | 6.8385 | 0.0287
GEN-2017-164 | 04 SOUTHEAST | 588360 | GEN-2016-153 | 345 | 7.3834 | 7.3726 | -0.0108
GEN-2017-164 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.5279 | 10.5253 | -0.0026
GEN-2017-164 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.292 | 6.2923 | 0.0003
GEN-2017-164 | 04 SOUTHEAST | 760809 | GEN-2017-203 | 345 | 9.1229 | 9.1266 | 0.0037
GEN-2017-164 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.963 | 22.9668 | 0.0038
GEN-2017-164 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.5556 | 11.9832 | 0.4276
GEN-2017-164 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.0607 | 8.2581 | 0.1974
GEN-2017-164 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0574 | 7.0577 | 0.0003
GEN-2017-164 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.664 | 5.6641 | 0.0001
GEN-2017-164 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3149 | 6.3151 | 0.0002
GEN-2017-171 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0343 | 14.0275 | -0.0068
GEN-2017-171 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2923 | 13.2777 | -0.0146
GEN-2017-171 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.7932 | 13.7865 | -0.0067
GEN-2017-171 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.2522 | 8.2581 | 0.0059
GEN-2017-171 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.0443 | 9.0513 | 0.007
GEN-2017-171 | 04 SOUTHEAST | 511428 | LG-YEAR4 | 138 | 12.1057 | 12.1266 | 0.0209
GEN-2017-171 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.2571 | 11.2758 | 0.0187
GEN-2017-171 | 04 SOUTHEAST | 511436 | COMANC-2 | 69 | 9.7262 | 9.7305 | 0.0043
GEN-2017-171 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.3682 | 18.4204 | 0.0522
GEN-2017-171 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 11.7386 | 11.7591 | 0.0205
GEN-2017-171 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 4.7913 | 4.7925 | 0.0012
GEN-2017-171 | 04 SOUTHEAST | 511453 | DUNCAN-4 | 138 | 6.5328 | 6.5309 | -0.0019
GEN-2017-171 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.1343 | 5.1387 | 0.0044
GEN-2017-171 | 04 SOUTHEAST | 511461 | FT.SILL2 | 69 | 6.0736 | 6.0759 | 0.0023
GEN-2017-171 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.5419 | 16.5612 | 0.0193
GEN-2017-171 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.0131 | 25.1312 | 0.1181
GEN-2017-171 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.7491 | 13.906 | 0.1569
GEN-2017-171 | 04 SOUTHEAST | 511469 | LGORE-N2 | 69 | 8.1601 | 8.1644 | 0.0043
GEN-2017-171 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 7.0899 | 7.0932 | 0.0033
GEN-2017-171 | 04 SOUTHEAST | 511471 | LWS-NTP4 | 138 | 11.8468 | 11.8681 | 0.0213
GEN-2017-171 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 5.9635 | 5.9656 | 0.0021
GEN-2017-171 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.5359 | 12.5614 | 0.0255
GEN-2017-171 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.9107 | 34.9339 | 0.0232
GEN-2017-171 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.2478 | 10.258 | 0.0102
GEN-2017-171 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 8.7568 | 8.7608 | 0.004
GEN-2017-171 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 12.9069 | 12.9308 | 0.0239
GEN-2017-171 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 21.8741 | 21.9595 | 0.0854
GEN-2017-171 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.6464 | 4.6477 | 0.0013
GEN-2017-171 | 04 SOUTHEAST | 511509 | 53CACHE4 | 138 | 11.8845 | 11.9063 | 0.0218
GEN-2017-171 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 12.492 | 12.5141 | 0.0221
GEN-2017-171 | 04 SOUTHEAST | 511512 | RPPAPER4 | 138 | 12.1626 | 12.1841 | 0.0215
GEN-2017-171 | 04 SOUTHEAST | 511524 | L-DISTP2 | 69 | 8.9715 | 8.9749 | 0.0034
GEN-2017-171 | 04 SOUTHEAST | 511537 | ARTVLTP4 | 138 | 11.9038 | 11.9258 | 0.022
GEN-2017-171 | 04 SOUTHEAST | 511538 | ARTVILL4 | 138 | 8.6117 | 8.6226 | 0.0109
GEN-2017-171 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.543 | 10.543 | 0
GEN-2017-171 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.1729 | 10.1828 | 0.0099
GEN-2017-171 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.12 | 5.1244 | 0.0044
GEN-2017-171 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.3293 | 10.455 | 0.1257
GEN-2017-171 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.5442 | 6.5871 | 0.0429
GEN-2017-171 | 04 SOUTHEAST | 511979 | RSHSPR1_MPT1 | 345 | 5.7657 | 5.8016 | 0.0359
GEN-2017-171 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7372 | 23.7553 | 0.0181
GEN-2017-171 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9221 | 15.9196 | -0.0025
GEN-2017-171 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1585 | 11.1642 | 0.0057
GEN-2017-171 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8454 | 36.8533 | 0.0079
GEN-2017-171 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4567 | 28.4632 | 0.0065
GEN-2017-171 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.619 | 11.6142 | -0.0048
GEN-2017-171 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.3099 | 11.3066 | -0.0033
GEN-2017-171 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 7.1988 | 7.1966 | -0.0022
GEN-2017-171 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 9.7898 | 9.7877 | -0.0021
GEN-2017-171 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.1777 | 20.1906 | 0.0129
GEN-2017-171 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9293 | 11.9562 | 0.0269
GEN-2017-171 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.1458 | 13.1457 | -0.0001
GEN-2017-171 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 14.1942 | 14.1964 | 0.0022
GEN-2017-171 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.2911 | 9.287 | -0.0041
GEN-2017-171 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.5217 | 7.5183 | -0.0034
GEN-2017-171 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 7.9688 | 7.9646 | -0.0042
GEN-2017-171 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.1808 | 12.179 | -0.0018
GEN-2017-171 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.115 | 12.1135 | -0.0015
GEN-2017-171 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 12.9483 | 12.9479 | -0.0004
GEN-2017-171 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 12.7704 | 12.7709 | 0.0005
GEN-2017-171 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1927 | 10.1886 | -0.0041
GEN-2017-171 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.6409 | 23.6589 | 0.018
GEN-2017-171 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.5187 | 7.5184 | -0.0003
GEN-2017-171 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7275 | 14.7334 | 0.0059
GEN-2017-171 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 10.0779 | 10.0758 | -0.0021
GEN-2017-171 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 5.8665 | 5.8639 | -0.0026
GEN-2017-171 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3259 | 19.3737 | 0.0478
GEN-2017-171 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.8924 | 33.9154 | 0.023
GEN-2017-171 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.9797 | 7.9804 | 0.0007
GEN-2017-171 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3801 | 22.3812 | 0.0011
GEN-2017-171 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 36.8536 | 36.8738 | 0.0202
GEN-2017-171 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.794 | 30.8113 | 0.0173
GEN-2017-171 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3055 | 11.2948 | -0.0107
GEN-2017-171 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 21.893 | 21.8906 | -0.0024
GEN-2017-171 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 12.5212 | 12.5184 | -0.0028
GEN-2017-171 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 12.3983 | 12.3955 | -0.0028
GEN-2017-171 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 9.3223 | 9.3209 | -0.0014
GEN-2017-171 | 04 SOUTHEAST | 529304 | OMDUNCN4 | 138 | 6.7431 | 6.7425 | -0.0006
GEN-2017-171 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1866 | 27.1936 | 0.007
GEN-2017-171 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.468 | 9.4705 | 0.0025
GEN-2017-171 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.089 | 8.0836 | -0.0054
GEN-2017-171 | 04 SOUTHEAST | 563259 | GEN-2015-092 | 345 | 6.3437 | 6.3837 | 0.04
GEN-2017-171 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5782 | 10.5911 | 0.0129
GEN-2017-171 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.0457 | 9.048 | 0.0023
GEN-2017-171 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 7.9864 | 7.981 | -0.0054
GEN-2017-171 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 10.9412 | 10.969 | 0.0278
GEN-2017-171 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.8596 | 15.9213 | 0.0617
GEN-2017-171 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.4238 | 11.454 | 0.0302
GEN-2017-171 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.661 | 9.6651 | 0.0041
GEN-2017-171 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.8379 | 11.8442 | 0.0063
GEN-2017-171 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 10.0276 | 10.0256 | -0.002
GEN-2017-171 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.6643 | 3.6648 | 0.0005
GEN-2017-171 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.0778 | 8.0724 | -0.0054
GEN-2017-171 | 04 SOUTHEAST | 590001 | OKLEHV24 | 138 | 5.0489 | 5.0489 | 0
GEN-2017-171 | 04 SOUTHEAST | 590003 | OKLEHV14 | 138 | 5.1608 | 5.1608 | 0
GEN-2017-171 | 04 SOUTHEAST | 599891 | OKLAUN 7 | 345 | 4.262 | 4.262 | 0
GEN-2017-171 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1572 | 4.1567 | -0.0005
GEN-2017-171 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.7922 | 3.7918 | -0.0004
GEN-2017-171 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.1961 | 11.4188 | 0.2227
GEN-2017-171 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.1961 | 11.4188 | 0.2227
GEN-2017-171 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.95 | 22.9668 | 0.0168
GEN-2017-171 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9672 | 2.9648 | -0.0024
GEN-2017-171 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.94 | 6.9453 | 0.0053
GEN-2017-171 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.5186 | 7.5147 | -0.0039
GEN-2017-171 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.6367 | 5.6337 | -0.003
GEN-2017-172 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0299 | 14.0275 | -0.0024
GEN-2017-172 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2827 | 13.2777 | -0.005
GEN-2017-172 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.7888 | 13.7865 | -0.0023
GEN-2017-172 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.2561 | 8.2581 | 0.002
GEN-2017-172 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.049 | 9.0513 | 0.0023
GEN-2017-172 | 04 SOUTHEAST | 511428 | LG-YEAR4 | 138 | 12.1196 | 12.1266 | 0.007
GEN-2017-172 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.2695 | 11.2758 | 0.0063
GEN-2017-172 | 04 SOUTHEAST | 511436 | COMANC-2 | 69 | 9.729 | 9.7305 | 0.0015
GEN-2017-172 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.4028 | 18.4204 | 0.0176
GEN-2017-172 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 11.7522 | 11.7591 | 0.0069
GEN-2017-172 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 4.7921 | 4.7925 | 0.0004
GEN-2017-172 | 04 SOUTHEAST | 511453 | DUNCAN-4 | 138 | 6.5316 | 6.5309 | -0.0007
GEN-2017-172 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.1372 | 5.1387 | 0.0015
GEN-2017-172 | 04 SOUTHEAST | 511461 | FT.SILL2 | 69 | 6.0752 | 6.0759 | 0.0007
GEN-2017-172 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.5547 | 16.5612 | 0.0065
GEN-2017-172 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.0913 | 25.1312 | 0.0399
GEN-2017-172 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.8526 | 13.906 | 0.0534
GEN-2017-172 | 04 SOUTHEAST | 511469 | LGORE-N2 | 69 | 8.1629 | 8.1644 | 0.0015
GEN-2017-172 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 7.0921 | 7.0932 | 0.0011
GEN-2017-172 | 04 SOUTHEAST | 511471 | LWS-NTP4 | 138 | 11.861 | 11.8681 | 0.0071
GEN-2017-172 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 5.9649 | 5.9656 | 0.0007
GEN-2017-172 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.5528 | 12.5614 | 0.0086
GEN-2017-172 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.926 | 34.9339 | 0.0079
GEN-2017-172 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.2546 | 10.258 | 0.0034
GEN-2017-172 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 8.7595 | 8.7608 | 0.0013
GEN-2017-172 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 12.9228 | 12.9308 | 0.008
GEN-2017-172 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 21.9306 | 21.9595 | 0.0289
GEN-2017-172 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.6473 | 4.6477 | 0.0004
GEN-2017-172 | 04 SOUTHEAST | 511509 | 53CACHE4 | 138 | 11.899 | 11.9063 | 0.0073
GEN-2017-172 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 12.5067 | 12.5141 | 0.0074
GEN-2017-172 | 04 SOUTHEAST | 511512 | RPPAPER4 | 138 | 12.1769 | 12.1841 | 0.0072
GEN-2017-172 | 04 SOUTHEAST | 511524 | L-DISTP2 | 69 | 8.9738 | 8.9749 | 0.0011
GEN-2017-172 | 04 SOUTHEAST | 511537 | ARTVLTP4 | 138 | 11.9184 | 11.9258 | 0.0074
GEN-2017-172 | 04 SOUTHEAST | 511538 | ARTVILL4 | 138 | 8.6189 | 8.6226 | 0.0037
GEN-2017-172 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.543 | 10.543 | 0
GEN-2017-172 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.1795 | 10.1828 | 0.0033
GEN-2017-172 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.1229 | 5.1244 | 0.0015
GEN-2017-172 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.4121 | 10.455 | 0.0429
GEN-2017-172 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.5725 | 6.5871 | 0.0146
GEN-2017-172 | 04 SOUTHEAST | 511979 | RSHSPR1_MPT1 | 345 | 5.7894 | 5.8016 | 0.0122
GEN-2017-172 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7493 | 23.7553 | 0.006
GEN-2017-172 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9205 | 15.9196 | -0.0009
GEN-2017-172 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1624 | 11.1642 | 0.0018
GEN-2017-172 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8508 | 36.8533 | 0.0025
GEN-2017-172 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.461 | 28.4632 | 0.0022
GEN-2017-172 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6159 | 11.6142 | -0.0017
GEN-2017-172 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.3078 | 11.3066 | -0.0012
GEN-2017-172 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 7.1974 | 7.1966 | -0.0008
GEN-2017-172 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 9.7885 | 9.7877 | -0.0008
GEN-2017-172 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.1864 | 20.1906 | 0.0042
GEN-2017-172 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9472 | 11.9562 | 0.009
GEN-2017-172 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.1458 | 13.1457 | -0.0001
GEN-2017-172 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 14.1958 | 14.1964 | 0.0006
GEN-2017-172 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.2884 | 9.287 | -0.0014
GEN-2017-172 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.5195 | 7.5183 | -0.0012
GEN-2017-172 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 7.9661 | 7.9646 | -0.0015
GEN-2017-172 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.1797 | 12.179 | -0.0007
GEN-2017-172 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.1141 | 12.1135 | -0.0006
GEN-2017-172 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 12.9482 | 12.9479 | -0.0003
GEN-2017-172 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 12.7708 | 12.7709 | 0.0001
GEN-2017-172 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.19 | 10.1886 | -0.0014
GEN-2017-172 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.6529 | 23.6589 | 0.006
GEN-2017-172 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.5185 | 7.5184 | -0.0001
GEN-2017-172 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7315 | 14.7334 | 0.0019
GEN-2017-172 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 10.0766 | 10.0758 | -0.0008
GEN-2017-172 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 5.8648 | 5.8639 | -0.0009
GEN-2017-172 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3576 | 19.3737 | 0.0161
GEN-2017-172 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.9077 | 33.9154 | 0.0077
GEN-2017-172 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.9802 | 7.9804 | 0.0002
GEN-2017-172 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3808 | 22.3812 | 0.0004
GEN-2017-172 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 36.867 | 36.8738 | 0.0068
GEN-2017-172 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.8055 | 30.8113 | 0.0058
GEN-2017-172 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.2984 | 11.2948 | -0.0036
GEN-2017-172 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 21.8914 | 21.8906 | -0.0008
GEN-2017-172 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 12.5194 | 12.5184 | -0.001
GEN-2017-172 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 12.3965 | 12.3955 | -0.001
GEN-2017-172 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 9.3214 | 9.3209 | -0.0005
GEN-2017-172 | 04 SOUTHEAST | 529304 | OMDUNCN4 | 138 | 6.7427 | 6.7425 | -0.0002
GEN-2017-172 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1913 | 27.1936 | 0.0023
GEN-2017-172 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.4697 | 9.4705 | 0.0008
GEN-2017-172 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.0855 | 8.0836 | -0.0019
GEN-2017-172 | 04 SOUTHEAST | 563259 | GEN-2015-092 | 345 | 6.3701 | 6.3837 | 0.0136
GEN-2017-172 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5868 | 10.5911 | 0.0043
GEN-2017-172 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.0472 | 9.048 | 0.0008
GEN-2017-172 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 7.9829 | 7.981 | -0.0019
GEN-2017-172 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 10.9597 | 10.969 | 0.0093
GEN-2017-172 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.9005 | 15.9213 | 0.0208
GEN-2017-172 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.4438 | 11.454 | 0.0102
GEN-2017-172 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.6637 | 9.6651 | 0.0014
GEN-2017-172 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.8421 | 11.8442 | 0.0021
GEN-2017-172 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 10.0263 | 10.0256 | -0.0007
GEN-2017-172 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.6646 | 3.6648 | 0.0002
GEN-2017-172 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.0743 | 8.0724 | -0.0019
GEN-2017-172 | 04 SOUTHEAST | 590001 | OKLEHV24 | 138 | 5.0489 | 5.0489 | 0
GEN-2017-172 | 04 SOUTHEAST | 590003 | OKLEHV14 | 138 | 5.1608 | 5.1608 | 0
GEN-2017-172 | 04 SOUTHEAST | 599891 | OKLAUN 7 | 345 | 4.262 | 4.262 | 0
GEN-2017-172 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1569 | 4.1567 | -0.0002
GEN-2017-172 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.7919 | 3.7918 | -0.0001
GEN-2017-172 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.3424 | 11.4188 | 0.0764
GEN-2017-172 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.3424 | 11.4188 | 0.0764
GEN-2017-172 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.9613 | 22.9668 | 0.0055
GEN-2017-172 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9656 | 2.9648 | -0.0008
GEN-2017-172 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.9436 | 6.9453 | 0.0017
GEN-2017-172 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.516 | 7.5147 | -0.0013
GEN-2017-172 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.6347 | 5.6337 | -0.001
GEN-2017-173 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0299 | 14.0275 | -0.0024
GEN-2017-173 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2827 | 13.2777 | -0.005
GEN-2017-173 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.7889 | 13.7865 | -0.0024
GEN-2017-173 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.2562 | 8.2581 | 0.0019
GEN-2017-173 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.0491 | 9.0513 | 0.0022
GEN-2017-173 | 04 SOUTHEAST | 511428 | LG-YEAR4 | 138 | 12.1198 | 12.1266 | 0.0068
GEN-2017-173 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.2697 | 11.2758 | 0.0061
GEN-2017-173 | 04 SOUTHEAST | 511436 | COMANC-2 | 69 | 9.729 | 9.7305 | 0.0015
GEN-2017-173 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.4033 | 18.4204 | 0.0171
GEN-2017-173 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 11.7524 | 11.7591 | 0.0067
GEN-2017-173 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 4.7922 | 4.7925 | 0.0003
GEN-2017-173 | 04 SOUTHEAST | 511453 | DUNCAN-4 | 138 | 6.5317 | 6.5309 | -0.0008
GEN-2017-173 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.1374 | 5.1387 | 0.0013
GEN-2017-173 | 04 SOUTHEAST | 511461 | FT.SILL2 | 69 | 6.0752 | 6.0759 | 0.0007
GEN-2017-173 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.5549 | 16.5612 | 0.0063
GEN-2017-173 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.0921 | 25.1312 | 0.0391
GEN-2017-173 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.8535 | 13.906 | 0.0525
GEN-2017-173 | 04 SOUTHEAST | 511469 | LGORE-N2 | 69 | 8.163 | 8.1644 | 0.0014
GEN-2017-173 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 7.0922 | 7.0932 | 0.001
GEN-2017-173 | 04 SOUTHEAST | 511471 | LWS-NTP4 | 138 | 11.8612 | 11.8681 | 0.0069
GEN-2017-173 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 5.9649 | 5.9656 | 0.0007
GEN-2017-173 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.553 | 12.5614 | 0.0084
GEN-2017-173 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.9261 | 34.9339 | 0.0078
GEN-2017-173 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.2547 | 10.258 | 0.0033
GEN-2017-173 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 8.7596 | 8.7608 | 0.0012
GEN-2017-173 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 12.923 | 12.9308 | 0.0078
GEN-2017-173 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 21.9312 | 21.9595 | 0.0283
GEN-2017-173 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.6474 | 4.6477 | 0.0003
GEN-2017-173 | 04 SOUTHEAST | 511509 | 53CACHE4 | 138 | 11.8992 | 11.9063 | 0.0071
GEN-2017-173 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 12.5069 | 12.5141 | 0.0072
GEN-2017-173 | 04 SOUTHEAST | 511512 | RPPAPER4 | 138 | 12.1771 | 12.1841 | 0.007
GEN-2017-173 | 04 SOUTHEAST | 511524 | L-DISTP2 | 69 | 8.9738 | 8.9749 | 0.0011
GEN-2017-173 | 04 SOUTHEAST | 511537 | ARTVLTP4 | 138 | 11.9186 | 11.9258 | 0.0072
GEN-2017-173 | 04 SOUTHEAST | 511538 | ARTVILL4 | 138 | 8.6191 | 8.6226 | 0.0035
GEN-2017-173 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.543 | 10.543 | 0
GEN-2017-173 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.1796 | 10.1828 | 0.0032
GEN-2017-173 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.123 | 5.1244 | 0.0014
GEN-2017-173 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.4129 | 10.455 | 0.0421
GEN-2017-173 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.5728 | 6.5871 | 0.0143
GEN-2017-173 | 04 SOUTHEAST | 511979 | RSHSPR1_MPT1 | 345 | 5.7897 | 5.8016 | 0.0119
GEN-2017-173 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7495 | 23.7553 | 0.0058
GEN-2017-173 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.9206 | 15.9196 | -0.001
GEN-2017-173 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1625 | 11.1642 | 0.0017
GEN-2017-173 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8509 | 36.8533 | 0.0024
GEN-2017-173 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.461 | 28.4632 | 0.0022
GEN-2017-173 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6159 | 11.6142 | -0.0017
GEN-2017-173 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.3078 | 11.3066 | -0.0012
GEN-2017-173 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 7.1974 | 7.1966 | -0.0008
GEN-2017-173 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 9.7885 | 9.7877 | -0.0008
GEN-2017-173 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.1866 | 20.1906 | 0.004
GEN-2017-173 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9475 | 11.9562 | 0.0087
GEN-2017-173 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.1459 | 13.1457 | -0.0002
GEN-2017-173 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 14.196 | 14.1964 | 0.0004
GEN-2017-173 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.2885 | 9.287 | -0.0015
GEN-2017-173 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.5196 | 7.5183 | -0.0013
GEN-2017-173 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 7.9661 | 7.9646 | -0.0015
GEN-2017-173 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.1798 | 12.179 | -0.0008
GEN-2017-173 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.1142 | 12.1135 | -0.0007
GEN-2017-173 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 12.9483 | 12.9479 | -0.0004
GEN-2017-173 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 12.7709 | 12.7709 | 0
GEN-2017-173 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.19 | 10.1886 | -0.0014
GEN-2017-173 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.653 | 23.6589 | 0.0059
GEN-2017-173 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.5185 | 7.5184 | -0.0001
GEN-2017-173 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7315 | 14.7334 | 0.0019
GEN-2017-173 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 10.0767 | 10.0758 | -0.0009
GEN-2017-173 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 5.8649 | 5.8639 | -0.001
GEN-2017-173 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3579 | 19.3737 | 0.0158
GEN-2017-173 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.9078 | 33.9154 | 0.0076
GEN-2017-173 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.9803 | 7.9804 | 0.0001
GEN-2017-173 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3808 | 22.3812 | 0.0004
GEN-2017-173 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 36.8671 | 36.8738 | 0.0067
GEN-2017-173 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.8056 | 30.8113 | 0.0057
GEN-2017-173 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.2984 | 11.2948 | -0.0036
GEN-2017-173 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 21.8914 | 21.8906 | -0.0008
GEN-2017-173 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 12.5194 | 12.5184 | -0.001
GEN-2017-173 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 12.3965 | 12.3955 | -0.001
GEN-2017-173 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 9.3214 | 9.3209 | -0.0005
GEN-2017-173 | 04 SOUTHEAST | 529304 | OMDUNCN4 | 138 | 6.7428 | 6.7425 | -0.0003
GEN-2017-173 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1913 | 27.1936 | 0.0023
GEN-2017-173 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.4698 | 9.4705 | 0.0007
GEN-2017-173 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.0856 | 8.0836 | -0.002
GEN-2017-173 | 04 SOUTHEAST | 563259 | GEN-2015-092 | 345 | 6.3704 | 6.3837 | 0.0133
GEN-2017-173 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5869 | 10.5911 | 0.0042
GEN-2017-173 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.0473 | 9.048 | 0.0007
GEN-2017-173 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 7.983 | 7.981 | -0.002
GEN-2017-173 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 10.9599 | 10.969 | 0.0091
GEN-2017-173 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.9009 | 15.9213 | 0.0204
GEN-2017-173 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.4441 | 11.454 | 0.0099
GEN-2017-173 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.6638 | 9.6651 | 0.0013
GEN-2017-173 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.8422 | 11.8442 | 0.002
GEN-2017-173 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 10.0264 | 10.0256 | -0.0008
GEN-2017-173 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.6647 | 3.6648 | 0.0001
GEN-2017-173 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.0744 | 8.0724 | -0.002
GEN-2017-173 | 04 SOUTHEAST | 590001 | OKLEHV24 | 138 | 5.0489 | 5.0489 | 0
GEN-2017-173 | 04 SOUTHEAST | 590003 | OKLEHV14 | 138 | 5.1608 | 5.1608 | 0
GEN-2017-173 | 04 SOUTHEAST | 599891 | OKLAUN 7 | 345 | 4.262 | 4.262 | 0
GEN-2017-173 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1569 | 4.1567 | -0.0002
GEN-2017-173 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.7919 | 3.7918 | -0.0001
GEN-2017-173 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.3437 | 11.4188 | 0.0751
GEN-2017-173 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.3437 | 11.4188 | 0.0751
GEN-2017-173 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.9614 | 22.9668 | 0.0054
GEN-2017-173 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9656 | 2.9648 | -0.0008
GEN-2017-173 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.9437 | 6.9453 | 0.0016
GEN-2017-173 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.5161 | 7.5147 | -0.0014
GEN-2017-173 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.6348 | 5.6337 | -0.0011
GEN-2017-178 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 22.6303 | 22.6286 | -0.0017
GEN-2017-178 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3266 | 22.325 | -0.0016
GEN-2017-178 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 32.6001 | 32.598 | -0.0021
GEN-2017-178 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7766 | 31.7758 | -0.0008
GEN-2017-178 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 25.9863 | 25.9854 | -0.0009
GEN-2017-178 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.2272 | 19.2264 | -0.0008
GEN-2017-178 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.2783 | 15.2773 | -0.001
GEN-2017-178 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.0332 | 24.0314 | -0.0018
GEN-2017-178 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.6902 | 22.6892 | -0.001
GEN-2017-178 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.0893 | 33.0888 | -0.0005
GEN-2017-178 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 34.839 | 34.8369 | -0.0021
GEN-2017-178 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.0789 | 19.0791 | 0.0002
GEN-2017-178 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5805 | 10.5801 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.1141 | 15.112 | -0.0021
GEN-2017-178 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 15.7145 | 15.7128 | -0.0017
GEN-2017-178 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 16.7981 | 16.7956 | -0.0025
GEN-2017-178 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.0427 | 20.0423 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 514642 | BRCKWND4 | 138 | 8.5969 | 8.5963 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 514701 | BUNCHCK4 | 138 | 6.7553 | 6.7544 | -0.0009
GEN-2017-178 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 20.9235 | 20.9242 | 0.0007
GEN-2017-178 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.1316 | 4.1315 | -0.0001
GEN-2017-178 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 11.8685 | 11.8685 | 0
GEN-2017-178 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.5263 | 11.5263 | 0
GEN-2017-178 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.5756 | 11.5768 | 0.0012
GEN-2017-178 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.9013 | 19.9034 | 0.0021
GEN-2017-178 | 04 SOUTHEAST | 514710 | WAUKOMI4 | 138 | 11.0969 | 11.0963 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 17.0195 | 17.0202 | 0.0007
GEN-2017-178 | 04 SOUTHEAST | 514712 | FAIRMON4 | 138 | 15.3015 | 15.3017 | 0.0002
GEN-2017-178 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 9.3387 | 9.3389 | 0.0002
GEN-2017-178 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.3993 | 21.4024 | 0.0031
GEN-2017-178 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.8546 | 20.9135 | 0.0589
GEN-2017-178 | 04 SOUTHEAST | 514718 | VANCE 2 | 69 | 7.1935 | 7.1923 | -0.0012
GEN-2017-178 | 04 SOUTHEAST | 514721 | IMO 2 | 69 | 12.4248 | 12.4233 | -0.0015
GEN-2017-178 | 04 SOUTHEAST | 514722 | CLEVETP2 | 69 | 12.2072 | 12.2057 | -0.0015
GEN-2017-178 | 04 SOUTHEAST | 514727 | ENID 2 | 69 | 11.2566 | 11.2551 | -0.0015
GEN-2017-178 | 04 SOUTHEAST | 514730 | SO4TH 2 | 69 | 14.4148 | 14.4132 | -0.0016
GEN-2017-178 | 04 SOUTHEAST | 514731 | SO4TH 4 | 138 | 16.6353 | 16.636 | 0.0007
GEN-2017-178 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.2316 | 8.2308 | -0.0008
GEN-2017-178 | 04 SOUTHEAST | 514734 | GLENWD 4 | 138 | 10.8769 | 10.8763 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 514743 | OSAGE 4 | 138 | 17.1778 | 17.1769 | -0.0009
GEN-2017-178 | 04 SOUTHEAST | 514774 | HENESEY4 | 138 | 9.9703 | 9.9699 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 514789 | MENOTAP4 | 138 | 7.2517 | 7.2512 | -0.0005
GEN-2017-178 | 04 SOUTHEAST | 514790 | IMO 4 | 138 | 12.6446 | 12.6443 | -0.0003
GEN-2017-178 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 20.9657 | 20.9664 | 0.0007
GEN-2017-178 | 04 SOUTHEAST | 514799 | SNRPMP 4 | 138 | 11.5108 | 11.5109 | 0.0001
GEN-2017-178 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.7556 | 23.7553 | -0.0003
GEN-2017-178 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.5551 | 32.5575 | 0.0024
GEN-2017-178 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3765 | 29.381 | 0.0045
GEN-2017-178 | 04 SOUTHEAST | 514815 | BRECKNR4 | 138 | 15.1774 | 15.1777 | 0.0003
GEN-2017-178 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.2527 | 17.252 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.7148 | 18.7141 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 514825 | KAYWIND7 | 345 | 13.1521 | 13.149 | -0.0031
GEN-2017-178 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5366 | 18.5361 | -0.0005
GEN-2017-178 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 27.4396 | 27.4391 | -0.0005
GEN-2017-178 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.4999 | 12.4993 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.2178 | 9.2171 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 14.8228 | 14.8223 | -0.0005
GEN-2017-178 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.7924 | 32.7917 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6194 | 27.6188 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.3354 | 23.3345 | -0.0009
GEN-2017-178 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.071 | 28.0702 | -0.0008
GEN-2017-178 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.9998 | 45.9997 | -0.0001
GEN-2017-178 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3209 | 34.3238 | 0.0029
GEN-2017-178 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1371 | 24.1374 | 0.0003
GEN-2017-178 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.6003 | 29.6006 | 0.0003
GEN-2017-178 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.1303 | 20.1299 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.7215 | 46.7216 | 0.0001
GEN-2017-178 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8502 | 36.8533 | 0.0031
GEN-2017-178 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8439 | 20.8437 | -0.0002
GEN-2017-178 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.3371 | 42.338 | 0.0009
GEN-2017-178 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.3737 | 27.375 | 0.0013
GEN-2017-178 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.4411 | 26.4422 | 0.0011
GEN-2017-178 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.4473 | 45.4476 | 0.0003
GEN-2017-178 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.0135 | 26.0139 | 0.0004
GEN-2017-178 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 14.2306 | 14.2303 | -0.0003
GEN-2017-178 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.3471 | 14.3465 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4625 | 28.4632 | 0.0007
GEN-2017-178 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.4153 | 14.4148 | -0.0005
GEN-2017-178 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3468 | 22.3446 | -0.0022
GEN-2017-178 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 25.2271 | 25.2247 | -0.0024
GEN-2017-178 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.8436 | 10.843 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 515383 | ENIDINT4 | 138 | 14.1207 | 14.1208 | 0.0001
GEN-2017-178 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2195 | 18.2176 | -0.0019
GEN-2017-178 | 04 SOUTHEAST | 515412 | DMNCRKT4 | 138 | 14.0997 | 14.0996 | -0.0001
GEN-2017-178 | 04 SOUTHEAST | 515426 | RDRUNNR4 | 138 | 8.7499 | 8.7492 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.6591 | 23.6589 | -0.0002
GEN-2017-178 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.2581 | 14.2578 | -0.0003
GEN-2017-178 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5325 | 12.5308 | -0.0017
GEN-2017-178 | 04 SOUTHEAST | 515456 | CHSTNTT2 | 69 | 11.9124 | 11.9108 | -0.0016
GEN-2017-178 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2776 | 40.2784 | 0.0008
GEN-2017-178 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6107 | 21.6107 | 0
GEN-2017-178 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.1797 | 14.1875 | 0.0078
GEN-2017-178 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 14.1601 | 14.1678 | 0.0077
GEN-2017-178 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.878 | 34.8833 | 0.0053
GEN-2017-178 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.8539 | 12.8527 | -0.0012
GEN-2017-178 | 04 SOUTHEAST | 515544 | RENFROW4 | 138 | 14.3653 | 14.3612 | -0.0041
GEN-2017-178 | 04 SOUTHEAST | 515546 | GRANTCO4 | 138 | 6.5156 | 6.5132 | -0.0024
GEN-2017-178 | 04 SOUTHEAST | 515547 | GRANTCO2 | 69 | 7.5408 | 7.5382 | -0.0026
GEN-2017-178 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.7338 | 14.7334 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 515569 | MDFRDTP4 | 138 | 11.599 | 11.5957 | -0.0033
GEN-2017-178 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.9392 | 14.9364 | -0.0028
GEN-2017-178 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7056 | 8.7044 | -0.0012
GEN-2017-178 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.2476 | 14.2459 | -0.0017
GEN-2017-178 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.5541 | 13.5526 | -0.0015
GEN-2017-178 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.223 | 12.2222 | -0.0008
GEN-2017-178 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.335 | 13.3343 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3395 | 18.3389 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 13.1897 | 13.1865 | -0.0032
GEN-2017-178 | 04 SOUTHEAST | 515641 | PLNSMEN4 | 138 | 15.146 | 15.1462 | 0.0002
GEN-2017-178 | 04 SOUTHEAST | 515646 | GRNTWD 7 | 345 | 11.2714 | 11.2695 | -0.0019
GEN-2017-178 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 12.0861 | 12.0835 | -0.0026
GEN-2017-178 | 04 SOUTHEAST | 515694 | ARMFTWD4 | 138 | 11.545 | 11.5462 | 0.0012
GEN-2017-178 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.3743 | 19.3737 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6714 | 14.6681 | -0.0033
GEN-2017-178 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.9417 | 18.9562 | 0.0145
GEN-2017-178 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.9372 | 18.9517 | 0.0145
GEN-2017-178 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 11.8258 | 11.825 | -0.0008
GEN-2017-178 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.276 | 14.2753 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 515978 | OTOETAP4 | 138 | 16.6945 | 16.6949 | 0.0004
GEN-2017-178 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.3683 | 7.3707 | 0.0024
GEN-2017-178 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.7314 | 17.7518 | 0.0204
GEN-2017-178 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.6685 | 17.6889 | 0.0204
GEN-2017-178 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 11.6881 | 11.6857 | -0.0024
GEN-2017-178 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 15.9947 | 15.9928 | -0.0019
GEN-2017-178 | 04 SOUTHEAST | 520409 | WFEC_RNFRO4 | 138 | 10.6323 | 10.6286 | -0.0037
GEN-2017-178 | 04 SOUTHEAST | 520434 | WAKTASW4 | 138 | 6.2797 | 6.2774 | -0.0023
GEN-2017-178 | 04 SOUTHEAST | 520461 | GARBER 4 | 138 | 4.6698 | 4.6698 | 0
GEN-2017-178 | 04 SOUTHEAST | 520535 | BULFTTP4 | 138 | 9.2829 | 9.2825 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 520882 | DOVERSW4 | 138 | 10.8811 | 10.8807 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.2316 | 8.2308 | -0.0008
GEN-2017-178 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.1078 | 10.1072 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 521100 | WARREN 4 | 138 | 6.5659 | 6.5659 | 0
GEN-2017-178 | 04 SOUTHEAST | 522397 | MEDFORD4 | 138 | 7.6012 | 7.5987 | -0.0025
GEN-2017-178 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 14.9097 | 14.9069 | -0.0028
GEN-2017-178 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 10.7308 | 10.7276 | -0.0032
GEN-2017-178 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 20.0279 | 20.0223 | -0.0056
GEN-2017-178 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 18.5124 | 18.5082 | -0.0042
GEN-2017-178 | 04 SOUTHEAST | 532792 | FR2EAST7 | 345 | 6.1747 | 6.1722 | -0.0025
GEN-2017-178 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.3103 | 23.3041 | -0.0062
GEN-2017-178 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.3699 | 13.3641 | -0.0058
GEN-2017-178 | 04 SOUTHEAST | 532803 | EXPEDITION7 | 345 | 9.899 | 9.8967 | -0.0023
GEN-2017-178 | 04 SOUTHEAST | 532984 | SUMNER 4 | 138 | 11.6963 | 11.6934 | -0.0029
GEN-2017-178 | 04 SOUTHEAST | 533036 | CLEARWT4 | 138 | 13.8612 | 13.8548 | -0.0064
GEN-2017-178 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 28.9685 | 28.9605 | -0.008
GEN-2017-178 | 04 SOUTHEAST | 533047 | GILL 4 | 138 | 21.2395 | 21.2316 | -0.0079
GEN-2017-178 | 04 SOUTHEAST | 533075 | VIOLA 4 | 138 | 23.4497 | 23.4388 | -0.0109
GEN-2017-178 | 04 SOUTHEAST | 539008 | MILAN_GOAB | 138 | 11.6192 | 11.613 | -0.0062
GEN-2017-178 | 04 SOUTHEAST | 539009 | CONWAY | 138 | 11.1253 | 11.1193 | -0.006
GEN-2017-178 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1934 | 27.1936 | 0.0002
GEN-2017-178 | 04 SOUTHEAST | 560053 | G15-052T | 345 | 13.168 | 13.1639 | -0.0041
GEN-2017-178 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5666 | 19.5659 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 32.6001 | 32.598 | -0.0021
GEN-2017-178 | 04 SOUTHEAST | 562476 | G14-001-TAP | 345 | 9.867 | 9.8648 | -0.0022
GEN-2017-178 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 19.3738 | 19.3731 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 8.0074 | 8.0069 | -0.0005
GEN-2017-178 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.3646 | 16.3642 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.1537 | 10.1531 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.7624 | 8.7618 | -0.0006
GEN-2017-178 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 6.8369 | 6.8385 | 0.0016
GEN-2017-178 | 04 SOUTHEAST | 588360 | GEN-2016-153 | 345 | 7.3759 | 7.3726 | -0.0033
GEN-2017-178 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.526 | 10.5253 | -0.0007
GEN-2017-178 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.2923 | 6.2923 | 0
GEN-2017-178 | 04 SOUTHEAST | 760809 | GEN-2017-203 | 345 | 9.1289 | 9.1266 | -0.0023
GEN-2017-178 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.9671 | 22.9668 | -0.0003
GEN-2017-178 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9245 | 11.9832 | 0.0587
GEN-2017-178 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.201 | 8.2581 | 0.0571
GEN-2017-178 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0581 | 7.0577 | -0.0004
GEN-2017-178 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.6643 | 5.6641 | -0.0002
GEN-2017-178 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3154 | 6.3151 | -0.0003
GEN-2017-187 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 22.1291 | 22.127 | -0.0021
GEN-2017-187 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 10.5051 | 10.5095 | 0.0044
GEN-2017-187 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.972 | 21.9248 | -0.0472
GEN-2017-187 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.7079 | 12.7108 | 0.0029
GEN-2017-187 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.4447 | 10.4443 | -0.0004
GEN-2017-187 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.3345 | 11.3399 | 0.0054
GEN-2017-187 | 05 SOUTHWEST | 526198 | SP-UPLAND | 115 | 5.7704 | 5.7686 | -0.0018
GEN-2017-187 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 18.2045 | 18.2089 | 0.0044
GEN-2017-187 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.7528 | 15.7633 | 0.0105
GEN-2017-187 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 17.689 | 17.6997 | 0.0107
GEN-2017-187 | 05 SOUTHWEST | 526416 | SLAUGTER_TP2 | 69 | 3.1886 | 3.2097 | 0.0211
GEN-2017-187 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.9626 | 10.9969 | 0.0343
GEN-2017-187 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 10.9768 | 10.9991 | 0.0223
GEN-2017-187 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.2883 | 10.3247 | 0.0364
GEN-2017-187 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.4641 | 6.4781 | 0.014
GEN-2017-187 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 9.6774 | 9.6946 | 0.0172
GEN-2017-187 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7236 | 10.7323 | 0.0087
GEN-2017-187 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8852 | 10.8926 | 0.0074
GEN-2017-187 | 05 SOUTHWEST | 526483 | SP-WOLFORTH3 | 115 | 8.5439 | 8.5466 | 0.0027
GEN-2017-187 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.2748 | 9.3159 | 0.0411
GEN-2017-187 | 05 SOUTHWEST | 526491 | LG-CLAUENE 3 | 115 | 7.9892 | 8.0537 | 0.0645
GEN-2017-187 | 05 SOUTHWEST | 526499 | LG-MEADOW 2 | 69 | 3.7587 | 3.7856 | 0.0269
GEN-2017-187 | 05 SOUTHWEST | 526506 | LG-DOCWEBR 2 | 69 | 4.9838 | 5.0253 | 0.0415
GEN-2017-187 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2016 | 11.2259 | 0.0243
GEN-2017-187 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 12.7487 | 12.764 | 0.0153
GEN-2017-187 | 05 SOUTHWEST | 526711 | LG-DIXON 2 | 69 | 2.528 | 2.543 | 0.015
GEN-2017-187 | 05 SOUTHWEST | 526735 | TERRY_CNTY 2 | 69 | 6.9817 | 7.0519 | 0.0702
GEN-2017-187 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.5551 | 10.7917 | 0.2366
GEN-2017-187 | 05 SOUTHWEST | 526747 | LG-BROWNFLD2 | 69 | 3.6152 | 3.6404 | 0.0252
GEN-2017-187 | 05 SOUTHWEST | 526754 | BROWNFIELD 2 | 69 | 3.0996 | 3.1196 | 0.02
GEN-2017-187 | 05 SOUTHWEST | 526761 | BROWNFLD_TP2 | 69 | 2.8726 | 2.8905 | 0.0179
GEN-2017-187 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 14.1693 | 14.2238 | 0.0545
GEN-2017-187 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0379 | 6.0903 | 0.0524
GEN-2017-187 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.185 | 10.2287 | 0.0437
GEN-2017-187 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 18.4595 | 18.6189 | 0.1594
GEN-2017-187 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 18.4352 | 18.5224 | 0.0872
GEN-2017-187 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.7045 | 9.7109 | 0.0064
GEN-2017-187 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 8.2121 | 8.2384 | 0.0263
GEN-2017-187 | 05 SOUTHWEST | 526965 | KINNEY 2 | 69 | 2.4456 | 2.4826 | 0.037
GEN-2017-187 | 05 SOUTHWEST | 526971 | TOKIO_TP 2 | 69 | 3.6585 | 3.7346 | 0.0761
GEN-2017-187 | 05 SOUTHWEST | 526979 | LG-JS_SMITH2 | 69 | 2.1235 | 2.1353 | 0.0118
GEN-2017-187 | 05 SOUTHWEST | 526985 | WELLMAN 2 | 69 | 2.8693 | 2.9192 | 0.0499
GEN-2017-187 | 05 SOUTHWEST | 526993 | LG-WELLMAN 2 | 69 | 3.0745 | 3.1311 | 0.0566
GEN-2017-187 | 05 SOUTHWEST | 526999 | UNION_TX 2 | 69 | 2.389 | 2.5104 | 0.1214
GEN-2017-187 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 14.5481 | 14.602 | 0.0539
GEN-2017-187 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 14.2018 | 14.2534 | 0.0516
GEN-2017-187 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.6137 | 13.7017 | 0.088
GEN-2017-187 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 10.9689 | 10.9919 | 0.023
GEN-2017-187 | 05 SOUTHWEST | 527036 | SHELL_C2 3 | 115 | 14.676 | 14.7527 | 0.0767
GEN-2017-187 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.5199 | 13.6067 | 0.0868
GEN-2017-187 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8111 | 10.8676 | 0.0565
GEN-2017-187 | 05 SOUTHWEST | 527051 | ODC_TP 3 | 115 | 13.6297 | 13.7179 | 0.0882
GEN-2017-187 | 05 SOUTHWEST | 527056 | ODC 3 | 115 | 10.195 | 10.2457 | 0.0507
GEN-2017-187 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.4583 | 16.5855 | 0.1272
GEN-2017-187 | 05 SOUTHWEST | 527068 | SHELLC3_TP 3 | 115 | 12.9469 | 12.9956 | 0.0487
GEN-2017-187 | 05 SOUTHWEST | 527080 | EL_PASO 3 | 115 | 16.2076 | 16.3307 | 0.1231
GEN-2017-187 | 05 SOUTHWEST | 527096 | OXY_DC_WST 2 | 69 | 4.5386 | 4.5475 | 0.0089
GEN-2017-187 | 05 SOUTHWEST | 527099 | DC_EAST 2 | 69 | 6.094 | 6.1082 | 0.0142
GEN-2017-187 | 05 SOUTHWEST | 527105 | SAN_ANDS_TP3 | 115 | 17.0462 | 17.1728 | 0.1266
GEN-2017-187 | 05 SOUTHWEST | 527106 | SAN_ANDRES 3 | 115 | 12.0303 | 12.0961 | 0.0658
GEN-2017-187 | 05 SOUTHWEST | 527111 | WASSON 2 | 69 | 5.9528 | 5.9664 | 0.0136
GEN-2017-187 | 05 SOUTHWEST | 527117 | SW_7814 2 | 69 | 3.1748 | 3.1801 | 0.0053
GEN-2017-187 | 05 SOUTHWEST | 527125 | DENVER_CTY 2 | 69 | 8.5286 | 8.5521 | 0.0235
GEN-2017-187 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.0147 | 22.2293 | 0.2146
GEN-2017-187 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.0147 | 22.2293 | 0.2146
GEN-2017-187 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 23.4829 | 23.745 | 0.2621
GEN-2017-187 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 15.7285 | 15.7983 | 0.0698
GEN-2017-187 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 15.7285 | 15.7983 | 0.0698
GEN-2017-187 | 05 SOUTHWEST | 527183 | JAYBEE 2 | 69 | 4.4122 | 4.4205 | 0.0083
GEN-2017-187 | 05 SOUTHWEST | 527189 | LG-SEAGRAVE2 | 69 | 3.7901 | 3.7967 | 0.0066
GEN-2017-187 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.7308 | 7.9972 | 0.2664
GEN-2017-187 | 05 SOUTHWEST | 527201 | SEAGRAVES 2 | 69 | 5.3667 | 5.5218 | 0.1551
GEN-2017-187 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 8.77 | 9.2008 | 0.4308
GEN-2017-187 | 05 SOUTHWEST | 527211 | DIAMONDBACK2 | 69 | 2.7617 | 2.8895 | 0.1278
GEN-2017-187 | 05 SOUTHWEST | 527212 | DIAMONDBACK3 | 115 | 3.2626 | 3.513 | 0.2504
GEN-2017-187 | 05 SOUTHWEST | 527217 | MOSS 2 | 69 | 5.2691 | 5.4194 | 0.1503
GEN-2017-187 | 05 SOUTHWEST | 527223 | LG-MC&SMNL+2 | 69 | 2.624 | 2.6653 | 0.0413
GEN-2017-187 | 05 SOUTHWEST | 527228 | RILEY_TP 2 | 69 | 3.9793 | 3.9809 | 0.0016
GEN-2017-187 | 05 SOUTHWEST | 527229 | OZRK_MAH02 2 | 69 | 2.5901 | 2.7063 | 0.1162
GEN-2017-187 | 05 SOUTHWEST | 527235 | LG-ASHMORE 2 | 69 | 2.1766 | 2.2671 | 0.0905
GEN-2017-187 | 05 SOUTHWEST | 527238 | ROZ 3 | 115 | 10.9134 | 10.9423 | 0.0289
GEN-2017-187 | 05 SOUTHWEST | 527242 | AMERADA 3 | 115 | 11.0603 | 11.09 | 0.0297
GEN-2017-187 | 05 SOUTHWEST | 527247 | CEDARLAKE 2 | 69 | 2.4149 | 2.5197 | 0.1048
GEN-2017-187 | 05 SOUTHWEST | 527250 | OXY_CEDRLKE2 | 69 | 2.4226 | 2.5278 | 0.1052
GEN-2017-187 | 05 SOUTHWEST | 527253 | ADAIR 2 | 69 | 2.6253 | 2.7718 | 0.1465
GEN-2017-187 | 05 SOUTHWEST | 527257 | FLATLAND 3 | 115 | 5.9426 | 6.7212 | 0.7786
GEN-2017-187 | 05 SOUTHWEST | 527261 | SULPHUR 2 | 69 | 3.3671 | 3.6073 | 0.2402
GEN-2017-187 | 05 SOUTHWEST | 527262 | SULPHUR 3 | 115 | 5.8913 | 6.6566 | 0.7653
GEN-2017-187 | 05 SOUTHWEST | 527271 | LG-FOSTER +2 | 69 | 2.7178 | 2.8748 | 0.157
GEN-2017-187 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 13.9639 | 14.0105 | 0.0466
GEN-2017-187 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 7.8875 | 7.9124 | 0.0249
GEN-2017-187 | 05 SOUTHWEST | 527284 | RUSSELL 3 | 115 | 9.1639 | 9.181 | 0.0171
GEN-2017-187 | 05 SOUTHWEST | 527286 | HIGGEAST 3 | 115 | 10.127 | 10.1493 | 0.0223
GEN-2017-187 | 05 SOUTHWEST | 527305 | LG-SAWYERFL2 | 69 | 2.0689 | 2.1529 | 0.084
GEN-2017-187 | 05 SOUTHWEST | 527313 | MIDAMERI_TP2 | 69 | 2.2001 | 2.2032 | 0.0031
GEN-2017-187 | 05 SOUTHWEST | 527321 | GAINES 2 | 69 | 4.1248 | 4.1265 | 0.0017
GEN-2017-187 | 05 SOUTHWEST | 527322 | GAINES 3 | 115 | 9.2955 | 9.3114 | 0.0159
GEN-2017-187 | 05 SOUTHWEST | 527325 | OXY_WSEM_TP3 | 115 | 9.1447 | 9.1597 | 0.015
GEN-2017-187 | 05 SOUTHWEST | 527339 | DOSS 2 | 69 | 4.1246 | 4.1269 | 0.0023
GEN-2017-187 | 05 SOUTHWEST | 527340 | DOSS 3 | 115 | 7.9073 | 7.921 | 0.0137
GEN-2017-187 | 05 SOUTHWEST | 527346 | LEGACY 3 | 115 | 7.6587 | 7.6703 | 0.0116
GEN-2017-187 | 05 SOUTHWEST | 527362 | JOHNSON_DRW3 | 115 | 10.7969 | 10.8098 | 0.0129
GEN-2017-187 | 05 SOUTHWEST | 527363 | HIGG 3 | 115 | 10.3034 | 10.3248 | 0.0214
GEN-2017-187 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.053 | 8.0586 | 0.0056
GEN-2017-187 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6278 | 3.6307 | 0.0029
GEN-2017-187 | 05 SOUTHWEST | 761796 | GEN-2017-187 | 115 | 5.9426 | 6.7212 | 0.7786
GEN-2017-203 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.2622 | 15.2482 | -0.014
GEN-2017-203 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3297 | 22.325 | -0.0047
GEN-2017-203 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.5746 | 11.5768 | 0.0022
GEN-2017-203 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.8839 | 19.9034 | 0.0195
GEN-2017-203 | 04 SOUTHEAST | 514710 | WAUKOMI4 | 138 | 11.0905 | 11.0963 | 0.0058
GEN-2017-203 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 17.0064 | 17.0202 | 0.0138
GEN-2017-203 | 04 SOUTHEAST | 514712 | FAIRMON4 | 138 | 15.29 | 15.3017 | 0.0117
GEN-2017-203 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 9.3387 | 9.3389 | 0.0002
GEN-2017-203 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.3798 | 21.4024 | 0.0226
GEN-2017-203 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.8022 | 20.9135 | 0.1113
GEN-2017-203 | 04 SOUTHEAST | 514719 | CLYDE 2 | 69 | 4.4143 | 4.4225 | 0.0082
GEN-2017-203 | 04 SOUTHEAST | 514731 | SO4TH 4 | 138 | 16.6225 | 16.636 | 0.0135
GEN-2017-203 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.2269 | 8.2308 | 0.0039
GEN-2017-203 | 04 SOUTHEAST | 514736 | 4CORNER2 | 69 | 3.6917 | 3.6966 | 0.0049
GEN-2017-203 | 04 SOUTHEAST | 514739 | MEDFORD2 | 69 | 5.4521 | 5.4618 | 0.0097
GEN-2017-203 | 04 SOUTHEAST | 514740 | NUMAOGE2 | 69 | 4.6248 | 4.6305 | 0.0057
GEN-2017-203 | 04 SOUTHEAST | 514757 | CHIKASI4 | 138 | 9.2672 | 9.2765 | 0.0093
GEN-2017-203 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.5499 | 32.5575 | 0.0076
GEN-2017-203 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3727 | 29.381 | 0.0083
GEN-2017-203 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5333 | 18.5361 | 0.0028
GEN-2017-203 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3119 | 34.3238 | 0.0119
GEN-2017-203 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.8405 | 36.8533 | 0.0128
GEN-2017-203 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2158 | 18.2176 | 0.0018
GEN-2017-203 | 04 SOUTHEAST | 515426 | RDRUNNR4 | 138 | 8.7318 | 8.7492 | 0.0174
GEN-2017-203 | 04 SOUTHEAST | 515427 | RCKFALL4 | 138 | 6.4629 | 6.4716 | 0.0087
GEN-2017-203 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.9983 | 14.1875 | 0.1892
GEN-2017-203 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.9792 | 14.1678 | 0.1886
GEN-2017-203 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8639 | 34.8833 | 0.0194
GEN-2017-203 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.4956 | 12.8527 | 0.3571
GEN-2017-203 | 04 SOUTHEAST | 515544 | RENFROW4 | 138 | 14.2502 | 14.3612 | 0.111
GEN-2017-203 | 04 SOUTHEAST | 515546 | GRANTCO4 | 138 | 6.492 | 6.5132 | 0.0212
GEN-2017-203 | 04 SOUTHEAST | 515547 | GRANTCO2 | 69 | 7.5203 | 7.5382 | 0.0179
GEN-2017-203 | 04 SOUTHEAST | 515569 | MDFRDTP4 | 138 | 11.5327 | 11.5957 | 0.063
GEN-2017-203 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.9391 | 14.9364 | -0.0027
GEN-2017-203 | 04 SOUTHEAST | 515581 | COYOTE 4 | 138 | 8.458 | 8.4694 | 0.0114
GEN-2017-203 | 04 SOUTHEAST | 515646 | GRNTWD 7 | 345 | 10.9994 | 11.2695 | 0.2701
GEN-2017-203 | 04 SOUTHEAST | 515694 | ARMFTWD4 | 138 | 11.544 | 11.5462 | 0.0022
GEN-2017-203 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6703 | 14.6681 | -0.0022
GEN-2017-203 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.9182 | 18.9562 | 0.038
GEN-2017-203 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.9136 | 18.9517 | 0.0381
GEN-2017-203 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 11.8266 | 11.825 | -0.0016
GEN-2017-203 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.3596 | 7.3707 | 0.0111
GEN-2017-203 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.7194 | 17.7518 | 0.0324
GEN-2017-203 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.6567 | 17.6889 | 0.0322
GEN-2017-203 | 04 SOUTHEAST | 520409 | WFEC_RNFRO4 | 138 | 10.5742 | 10.6286 | 0.0544
GEN-2017-203 | 04 SOUTHEAST | 520433 | SANDYCR4 | 138 | 6.1369 | 6.1466 | 0.0097
GEN-2017-203 | 04 SOUTHEAST | 520434 | WAKTASW4 | 138 | 6.2668 | 6.2774 | 0.0106
GEN-2017-203 | 04 SOUTHEAST | 520447 | BLUFCRK4 | 138 | 3.8323 | 3.8344 | 0.0021
GEN-2017-203 | 04 SOUTHEAST | 520452 | WAKTASB4 | 138 | 6.2316 | 6.242 | 0.0104
GEN-2017-203 | 04 SOUTHEAST | 520938 | HAZLTAJ2 | 69 | 5.7552 | 5.7601 | 0.0049
GEN-2017-203 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.2269 | 8.2308 | 0.0039
GEN-2017-203 | 04 SOUTHEAST | 521008 | NASH 2 | 69 | 2.9583 | 2.9609 | 0.0026
GEN-2017-203 | 04 SOUTHEAST | 521085 | WAKITA 2 | 69 | 4.6786 | 4.6838 | 0.0052
GEN-2017-203 | 04 SOUTHEAST | 522397 | MEDFORD4 | 138 | 7.5717 | 7.5987 | 0.027
GEN-2017-203 | 04 SOUTHEAST | 522398 | PONDCRK4 | 138 | 5.1686 | 5.1811 | 0.0125
GEN-2017-203 | 04 SOUTHEAST | 532768 | EMPEC 7 | 345 | 18.4123 | 18.4174 | 0.0051
GEN-2017-203 | 04 SOUTHEAST | 532769 | LANG 7 | 345 | 18.1771 | 18.182 | 0.0049
GEN-2017-203 | 04 SOUTHEAST | 532770 | MORRIS 7 | 345 | 12.9577 | 12.9571 | -0.0006
GEN-2017-203 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 10.7388 | 10.7276 | -0.0112
GEN-2017-203 | 04 SOUTHEAST | 532773 | SUMMIT 7 | 345 | 10.6332 | 10.6253 | -0.0079
GEN-2017-203 | 04 SOUTHEAST | 532774 | SWISVAL7 | 345 | 17.0153 | 17.0087 | -0.0066
GEN-2017-203 | 04 SOUTHEAST | 532776 | READWF 7 | 345 | 15.0299 | 15.0332 | 0.0033
GEN-2017-203 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 20.0173 | 20.0223 | 0.005
GEN-2017-203 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 6.9546 | 6.947 | -0.0076
GEN-2017-203 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 5.8306 | 5.8236 | -0.007
GEN-2017-203 | 04 SOUTHEAST | 532790 | EXPED WF7 | 345 | 6.7598 | 6.7544 | -0.0054
GEN-2017-203 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 18.505 | 18.5082 | 0.0032
GEN-2017-203 | 04 SOUTHEAST | 532792 | FR2EAST7 | 345 | 6.1639 | 6.1722 | 0.0083
GEN-2017-203 | 04 SOUTHEAST | 532794 | ROSEHIL7 | 345 | 18.3325 | 18.3335 | 0.001
GEN-2017-203 | 04 SOUTHEAST | 532795 | FR2WEST7 | 345 | 4.9715 | 4.975 | 0.0035
GEN-2017-203 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.2871 | 23.3041 | 0.017
GEN-2017-203 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 17.8339 | 17.8361 | 0.0022
GEN-2017-203 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.283 | 13.3641 | 0.0811
GEN-2017-203 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 15.7286 | 15.7289 | 0.0003
GEN-2017-203 | 04 SOUTHEAST | 532800 | LATHAMS7 | 345 | 10.0249 | 10.0193 | -0.0056
GEN-2017-203 | 04 SOUTHEAST | 532803 | EXPEDITION7 | 345 | 9.9027 | 9.8967 | -0.006
GEN-2017-203 | 04 SOUTHEAST | 532981 | CRESWLN4 | 138 | 8.6184 | 8.6158 | -0.0026
GEN-2017-203 | 04 SOUTHEAST | 532982 | OXFORD 4 | 138 | 10.359 | 10.3537 | -0.0053
GEN-2017-203 | 04 SOUTHEAST | 532984 | SUMNER 4 | 138 | 11.6988 | 11.6934 | -0.0054
GEN-2017-203 | 04 SOUTHEAST | 532985 | TCROCK 4 | 138 | 5.8533 | 5.8488 | -0.0045
GEN-2017-203 | 04 SOUTHEAST | 532986 | BENTON 4 | 138 | 27.3157 | 27.3068 | -0.0089
GEN-2017-203 | 04 SOUTHEAST | 532988 | BELAIRE4 | 138 | 18.5597 | 18.5482 | -0.0115
GEN-2017-203 | 04 SOUTHEAST | 532990 | MIDIAN 4 | 138 | 10.819 | 10.8097 | -0.0093
GEN-2017-203 | 04 SOUTHEAST | 532992 | TIMBJCT4 | 138 | 6.298 | 6.2932 | -0.0048
GEN-2017-203 | 04 SOUTHEAST | 533015 | BENTLEY4 | 138 | 10.4356 | 10.4228 | -0.0128
GEN-2017-203 | 04 SOUTHEAST | 533024 | 29TH 4 | 138 | 19.1784 | 19.1669 | -0.0115
GEN-2017-203 | 04 SOUTHEAST | 533029 | 59TH ST4 | 138 | 16.8763 | 16.8634 | -0.0129
GEN-2017-203 | 04 SOUTHEAST | 533035 | CHISHLM4 | 138 | 20.7355 | 20.7237 | -0.0118
GEN-2017-203 | 04 SOUTHEAST | 533036 | CLEARWT4 | 138 | 13.8697 | 13.8548 | -0.0149
GEN-2017-203 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 28.9678 | 28.9605 | -0.0073
GEN-2017-203 | 04 SOUTHEAST | 533041 | EVANS S4 | 138 | 28.9087 | 28.9012 | -0.0075
GEN-2017-203 | 04 SOUTHEAST | 533042 | FARBER 4 | 138 | 16.2892 | 16.2776 | -0.0116
GEN-2017-203 | 04 SOUTHEAST | 533044 | GILL E 4 | 138 | 21.1869 | 21.1771 | -0.0098
GEN-2017-203 | 04 SOUTHEAST | 533045 | GILL W 4 | 138 | 21.2472 | 21.2375 | -0.0097
GEN-2017-203 | 04 SOUTHEAST | 533046 | GILL S 4 | 138 | 21.2445 | 21.2349 | -0.0096
GEN-2017-203 | 04 SOUTHEAST | 533047 | GILL 4 | 138 | 21.2413 | 21.2316 | -0.0097
GEN-2017-203 | 04 SOUTHEAST | 533052 | PARKCTY4 | 138 | 19.6559 | 19.6439 | -0.012
GEN-2017-203 | 04 SOUTHEAST | 533053 | LAKERDG4 | 138 | 16.4988 | 16.4842 | -0.0146
GEN-2017-203 | 04 SOUTHEAST | 533054 | MAIZE 4 | 138 | 19.8208 | 19.8075 | -0.0133
GEN-2017-203 | 04 SOUTHEAST | 533062 | ROSEHIL4 | 138 | 30.4908 | 30.4844 | -0.0064
GEN-2017-203 | 04 SOUTHEAST | 533063 | SC10BEL4 | 138 | 11.5708 | 11.5651 | -0.0057
GEN-2017-203 | 04 SOUTHEAST | 533065 | SG12COL4 | 138 | 18.2509 | 18.2361 | -0.0148
GEN-2017-203 | 04 SOUTHEAST | 533071 | WACO S 4 | 138 | 18.5648 | 18.5522 | -0.0126
GEN-2017-203 | 04 SOUTHEAST | 533074 | 45TH ST4 | 138 | 22.0195 | 22.0069 | -0.0126
GEN-2017-203 | 04 SOUTHEAST | 533075 | VIOLA 4 | 138 | 23.3996 | 23.4388 | 0.0392
GEN-2017-203 | 04 SOUTHEAST | 533413 | CIRCLE 3 | 115 | 18.34 | 18.3185 | -0.0215
GEN-2017-203 | 04 SOUTHEAST | 533415 | DAVIS 3 | 115 | 8.108 | 8.0969 | -0.0111
GEN-2017-203 | 04 SOUTHEAST | 533416 | RENO 3 | 115 | 21.9073 | 21.8821 | -0.0252
GEN-2017-203 | 04 SOUTHEAST | 533429 | MOUNDRG3 | 115 | 8.4443 | 8.4339 | -0.0104
GEN-2017-203 | 04 SOUTHEAST | 533438 | WMCPHER3 | 115 | 11.0166 | 11.0051 | -0.0115
GEN-2017-203 | 04 SOUTHEAST | 533558 | TIMBJCT2 | 69 | 8.4288 | 8.4232 | -0.0056
GEN-2017-203 | 04 SOUTHEAST | 533653 | WOLFCRK2 | 69 | 5.9361 | 5.935 | -0.0011
GEN-2017-203 | 04 SOUTHEAST | 533795 | GILL E 2 | 69 | 28.8643 | 28.8387 | -0.0256
GEN-2017-203 | 04 SOUTHEAST | 533796 | GILL W 2 | 69 | 28.8725 | 28.8468 | -0.0257
GEN-2017-203 | 04 SOUTHEAST | 539002 | BLF-CRK4 | 138 | 4.7295 | 4.7195 | -0.01
GEN-2017-203 | 04 SOUTHEAST | 539003 | CLDWELL4 | 138 | 5.6062 | 5.5956 | -0.0106
GEN-2017-203 | 04 SOUTHEAST | 539008 | MILAN_GOAB | 138 | 11.621 | 11.613 | -0.008
GEN-2017-203 | 04 SOUTHEAST | 539009 | CONWAY | 138 | 11.1287 | 11.1193 | -0.0094
GEN-2017-203 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.2466 | 7.2322 | -0.0144
GEN-2017-203 | 04 SOUTHEAST | 539675 | MILANTP4 | 138 | 9.8526 | 9.8417 | -0.0109
GEN-2017-203 | 04 SOUTHEAST | 539676 | MILAN 4 | 138 | 10.3352 | 10.3258 | -0.0094
GEN-2017-203 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 12.276 | 12.2678 | -0.0082
GEN-2017-203 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 16.0083 | 16.0029 | -0.0054
GEN-2017-203 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.3728 | 17.3565 | -0.0163
GEN-2017-203 | 04 SOUTHEAST | 560053 | G15-052T | 345 | 13.1681 | 13.1639 | -0.0042
GEN-2017-203 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5686 | 19.5659 | -0.0027
GEN-2017-203 | 04 SOUTHEAST | 562476 | G14-001-TAP | 345 | 9.8708 | 9.8648 | -0.006
GEN-2017-203 | 04 SOUTHEAST | 578530 | FR3HV | 345 | 4.5666 | 4.5687 | 0.0021
GEN-2017-203 | 04 SOUTHEAST | 583850 | GEN-2014-001 | 345 | 6.5705 | 6.5652 | -0.0053
GEN-2017-203 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.3636 | 16.3642 | 0.0006
GEN-2017-203 | 04 SOUTHEAST | 587880 | GEN-2016-111 | 345 | 5.9704 | 5.9634 | -0.007
GEN-2017-203 | 04 SOUTHEAST | 587884 | G16-111-TAP | 345 | 9.2362 | 9.2265 | -0.0097
GEN-2017-203 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 6.8291 | 6.8385 | 0.0094
GEN-2017-203 | 04 SOUTHEAST | 588360 | GEN-2016-153 | 345 | 7.3577 | 7.3726 | 0.0149
GEN-2017-203 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 16.0083 | 16.0029 | -0.0054
GEN-2017-203 | 04 SOUTHEAST | 589060 | GEN-2017-068 | 138 | 26.4581 | 26.4481 | -0.01
GEN-2017-203 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 19.9089 | 19.9137 | 0.0048
GEN-2017-203 | 04 SOUTHEAST | 760641 | GEN-2017-226 | 138 | 28.9678 | 28.9605 | -0.0073
GEN-2017-203 | 04 SOUTHEAST | 760809 | GEN-2017-203 | 345 | 8.7589 | 9.1266 | 0.3677
GEN-2017-203 | 04 SOUTHEAST | 761838 | GEN-2017-121 | 138 | 8.8542 | 8.8497 | -0.0045
GEN-2017-203 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9471 | 11.9832 | 0.0361
GEN-2017-203 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.2407 | 8.2581 | 0.0174
GEN-2017-203 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0573 | 7.0577 | 0.0004
GEN-2017-230 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.547 | 32.5575 | 0.0105
GEN-2017-230 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 42.0218 | 42.0508 | 0.029
GEN-2017-230 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 14.2025 | 14.2303 | 0.0278
GEN-2017-230 | 04 SOUTHEAST | 515009 | MCELROY4 | 138 | 13.9154 | 13.979 | 0.0636
GEN-2017-230 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.2654 | 14.3465 | 0.0811
GEN-2017-230 | 04 SOUTHEAST | 515019 | HY99TAP2 | 69 | 7.3745 | 7.4137 | 0.0392
GEN-2017-230 | 04 SOUTHEAST | 515021 | OAKGROV2 | 69 | 7.5035 | 7.5408 | 0.0373
GEN-2017-230 | 04 SOUTHEAST | 515032 | CUSHING2 | 69 | 8.3408 | 8.3885 | 0.0477
GEN-2017-230 | 04 SOUTHEAST | 515033 | CUSHING4 | 138 | 7.433 | 7.5017 | 0.0687
GEN-2017-230 | 04 SOUTHEAST | 515034 | BRISTOW2 | 69 | 5.8724 | 5.8808 | 0.0084
GEN-2017-230 | 04 SOUTHEAST | 515035 | BRISTOW4 | 138 | 10.9443 | 10.9867 | 0.0424
GEN-2017-230 | 04 SOUTHEAST | 515039 | PAYNESB4 | 138 | 9.028 | 9.1235 | 0.0955
GEN-2017-230 | 04 SOUTHEAST | 515043 | GRTPLNS4 | 138 | 7.093 | 7.2003 | 0.1073
GEN-2017-230 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 16.8768 | 16.9207 | 0.0439
GEN-2017-230 | 04 SOUTHEAST | 515047 | WARWICK4 | 138 | 10.2133 | 10.3447 | 0.1314
GEN-2017-230 | 04 SOUTHEAST | 515048 | KEYWEST4 | 138 | 5.9757 | 6.0028 | 0.0271
GEN-2017-230 | 04 SOUTHEAST | 515051 | JACKTWN4 | 138 | 9.6921 | 9.7191 | 0.027
GEN-2017-230 | 04 SOUTHEAST | 515181 | UNVRSTY4 | 138 | 13.9275 | 13.9815 | 0.054
GEN-2017-230 | 04 SOUTHEAST | 515242 | BLUEBEL4 | 138 | 17.3039 | 17.3161 | 0.0122
GEN-2017-230 | 04 SOUTHEAST | 515249 | BEGGS 4 | 138 | 5.708 | 5.7135 | 0.0055
GEN-2017-230 | 04 SOUTHEAST | 515366 | WFROSST4 | 138 | 12.2404 | 12.3271 | 0.0867
GEN-2017-230 | 04 SOUTHEAST | 515369 | BELLCOW4 | 138 | 6.6016 | 6.6497 | 0.0481
GEN-2017-230 | 04 SOUTHEAST | 515401 | LINWOOD4 | 138 | 6.9915 | 7.1002 | 0.1087
GEN-2017-230 | 04 SOUTHEAST | 515416 | GRNWOOD2 | 69 | 8.5699 | 8.6193 | 0.0494
GEN-2017-230 | 04 SOUTHEAST | 515417 | GRNWOOD4 | 138 | 8.658 | 8.7528 | 0.0948
GEN-2017-230 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 14.9436 | 15.0175 | 0.0739
GEN-2017-230 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.2298 | 14.2578 | 0.028
GEN-2017-230 | 04 SOUTHEAST | 515453 | LNWOODT4 | 138 | 7.0387 | 7.1487 | 0.11
GEN-2017-230 | 04 SOUTHEAST | 515514 | KNIPE 4 | 138 | 8.2605 | 8.4359 | 0.1754
GEN-2017-230 | 04 SOUTHEAST | 515532 | WOLVRNT4 | 138 | 8.443 | 8.4564 | 0.0134
GEN-2017-230 | 04 SOUTHEAST | 515574 | SPGVLLY4 | 138 | 10.7701 | 10.9009 | 0.1308
GEN-2017-230 | 04 SOUTHEAST | 515675 | TRYON 4 | 138 | 8.7331 | 9.0644 | 0.3313
GEN-2017-230 | 04 SOUTHEAST | 520464 | MEEKER 4 | 138 | 8.8944 | 8.9141 | 0.0197
GEN-2017-230 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 12.5715 | 12.5984 | 0.0269
GEN-2017-230 | 04 SOUTHEAST | 520994 | MEEKRSW4 | 138 | 8.1659 | 8.1795 | 0.0136
GEN-2017-230 | 04 SOUTHEAST | 521107 | RSSVILE4 | 138 | 12.2404 | 12.3271 | 0.0867
GEN-2017-230 | 04 SOUTHEAST | 589090 | GEN-2017-071 | 138 | 8.3955 | 8.4843 | 0.0888
GEN-2017-230 | 04 SOUTHEAST | 760158 | GEN-2017-240 | 138 | 8.1848 | 8.2075 | 0.0227
GEN-2017-230 | 04 SOUTHEAST | 762195 | GEN-2017-230 | 138 | 8.6651 | 8.9967 | 0.3316
GEN-2017-231 | 04 SOUTHEAST | 301307 | 5PARK | 161 | 9.0987 | 9.1018 | 0.0031
GEN-2017-231 | 04 SOUTHEAST | 301344 | 5CDRCRST | 161 | 10.695 | 10.697 | 0.002
GEN-2017-231 | 04 SOUTHEAST | 301550 | 5STIGLER | 161 | 6.6643 | 6.6675 | 0.0032
GEN-2017-231 | 04 SOUTHEAST | 301557 | 5LBRTYTKM | 161 | 8.6315 | 8.6509 | 0.0194
GEN-2017-231 | 04 SOUTHEAST | 337900 | 3OLA AR | 115 | 4.9915 | 5.0028 | 0.0113
GEN-2017-231 | 04 SOUTHEAST | 337901 | 3DANVLE AR | 115 | 6.1825 | 6.205 | 0.0225
GEN-2017-231 | 04 SOUTHEAST | 337902 | 5DANVLE AR! | 161 | 7.1484 | 7.1928 | 0.0444
GEN-2017-231 | 04 SOUTHEAST | 337903 | 5DARDANELLE | 161 | 10.3299 | 10.3577 | 0.0278
GEN-2017-231 | 04 SOUTHEAST | 503902 | FITZHUGH 5 | 161 | 11.0914 | 11.1447 | 0.0533
GEN-2017-231 | 04 SOUTHEAST | 503908 | ELLIS 2 | 69 | 4.0545 | 4.0582 | 0.0037
GEN-2017-231 | 04 SOUTHEAST | 504032 | VBI_N 2 | 69 | 11.068 | 11.0848 | 0.0168
GEN-2017-231 | 04 SOUTHEAST | 504172 | BOONEVIL 2 | 69 | 5.8231 | 5.8605 | 0.0374
GEN-2017-231 | 04 SOUTHEAST | 504181 | HACKETT 5 | 161 | 12.5366 | 12.5771 | 0.0405
GEN-2017-231 | 04 SOUTHEAST | 504185 | FIG_FIVE 2 | 69 | 6.955 | 6.9624 | 0.0074
GEN-2017-231 | 04 SOUTHEAST | 504191 | HWY59 5 | 161 | 15.634 | 15.7103 | 0.0763
GEN-2017-231 | 04 SOUTHEAST | 504192 | GRANDPR5 | 161 | 7.3315 | 7.5285 | 0.197
GEN-2017-231 | 04 SOUTHEAST | 505508 | DARDANE5 | 161 | 11.4377 | 11.4657 | 0.028
GEN-2017-231 | 04 SOUTHEAST | 505514 | CLARKSV5 | 161 | 7.6597 | 7.6994 | 0.0397
GEN-2017-231 | 04 SOUTHEAST | 505516 | OZARK H5 | 161 | 10.8057 | 10.856 | 0.0503
GEN-2017-231 | 04 SOUTHEAST | 505522 | VAN BUR5 | 161 | 18.3832 | 18.4885 | 0.1053
GEN-2017-231 | 04 SOUTHEAST | 505524 | LIBERTY5 | 161 | 8.6522 | 8.6717 | 0.0195
GEN-2017-231 | 04 SOUTHEAST | 505526 | AKINS E5 | 161 | 7.5532 | 7.5652 | 0.012
GEN-2017-231 | 04 SOUTHEAST | 505582 | RS KERR5 | 161 | 8.8512 | 8.8593 | 0.0081
GEN-2017-231 | 04 SOUTHEAST | 507183 | BOONVIL2 | 69 | 5.4276 | 5.4639 | 0.0363
GEN-2017-231 | 04 SOUTHEAST | 507185 | REVESRD5 | 161 | 11.4311 | 11.4699 | 0.0388
GEN-2017-231 | 04 SOUTHEAST | 507186 | HUNTING2 | 69 | 9.1639 | 9.1897 | 0.0258
GEN-2017-231 | 04 SOUTHEAST | 507188 | NHUNTNT2 | 69 | 9.6704 | 9.6984 | 0.028
GEN-2017-231 | 04 SOUTHEAST | 507189 | NHUNTNT5 | 161 | 7.7858 | 7.825 | 0.0392
GEN-2017-231 | 04 SOUTHEAST | 507190 | NMAGZIN5 | 161 | 7.6844 | 7.833 | 0.1486
GEN-2017-231 | 04 SOUTHEAST | 507192 | WBOONVL5 | 161 | 6.3681 | 6.4385 | 0.0704
GEN-2017-231 | 04 SOUTHEAST | 507194 | HUNTREC2 | 69 | 6.2428 | 6.2573 | 0.0145
GEN-2017-231 | 04 SOUTHEAST | 507195 | MAGZREC5 | 161 | 6.8358 | 6.9284 | 0.0926
GEN-2017-231 | 04 SOUTHEAST | 507196 | MIDLREC2 | 69 | 7.5795 | 7.5973 | 0.0178
GEN-2017-231 | 04 SOUTHEAST | 507198 | WBOONVL2 | 69 | 5.9696 | 6.0077 | 0.0381
GEN-2017-231 | 04 SOUTHEAST | 512647 | TAHLQH 2 | 69 | 11.6027 | 11.6054 | 0.0027
GEN-2017-231 | 04 SOUTHEAST | 512655 | TAHLQH 5 | 161 | 10.2465 | 10.2503 | 0.0038
GEN-2017-231 | 04 SOUTHEAST | 513044 | BRIGSKM 5 | 161 | 8.3263 | 8.3291 | 0.0028
GEN-2017-231 | 04 SOUTHEAST | 515254 | SUNSTCN5 | 161 | 7.9612 | 7.9678 | 0.0066
GEN-2017-231 | 04 SOUTHEAST | 515277 | ROLANTP2 | 69 | 5.7059 | 5.7118 | 0.0059
GEN-2017-231 | 04 SOUTHEAST | 515298 | VBAVEC 2 | 69 | 8.9347 | 8.9469 | 0.0122
GEN-2017-231 | 04 SOUTHEAST | 515313 | BRANCH 2 | 69 | 7.747 | 7.8349 | 0.0879
GEN-2017-231 | 04 SOUTHEAST | 515316 | BRANCH 5 | 161 | 8.1167 | 8.4072 | 0.2905
GEN-2017-231 | 04 SOUTHEAST | 515317 | PENDER 2 | 69 | 6.6566 | 6.6953 | 0.0387
GEN-2017-231 | 04 SOUTHEAST | 515319 | LSPADRA5 | 161 | 7.5412 | 7.5883 | 0.0471
GEN-2017-231 | 04 SOUTHEAST | 515322 | COALHIL2 | 69 | 6.0456 | 6.0617 | 0.0161
GEN-2017-231 | 04 SOUTHEAST | 515324 | AVECOZK2 | 69 | 9.2558 | 9.2895 | 0.0337
GEN-2017-231 | 04 SOUTHEAST | 515325 | HELBERG2 | 69 | 9.9749 | 10.0132 | 0.0383
GEN-2017-231 | 04 SOUTHEAST | 515326 | GERBRTP5 | 161 | 16.5696 | 16.6356 | 0.066
GEN-2017-231 | 04 SOUTHEAST | 515327 | HELBERG5 | 161 | 9.5502 | 9.593 | 0.0428
GEN-2017-231 | 04 SOUTHEAST | 515334 | ALMA 5 | 161 | 10.7275 | 10.7695 | 0.042
GEN-2017-231 | 04 SOUTHEAST | 515335 | KLGORE 2 | 69 | 7.0683 | 7.0769 | 0.0086
GEN-2017-231 | 04 SOUTHEAST | 515336 | VBI 2 | 69 | 11.142 | 11.159 | 0.017
GEN-2017-231 | 04 SOUTHEAST | 515337 | RUDY 5 | 161 | 11.2982 | 11.3439 | 0.0457
GEN-2017-231 | 04 SOUTHEAST | 515339 | VBI 5 | 161 | 18.6063 | 18.7148 | 0.1085
GEN-2017-231 | 04 SOUTHEAST | 515340 | OAKGROV5 | 161 | 15.5506 | 15.6165 | 0.0659
GEN-2017-231 | 04 SOUTHEAST | 515341 | WHITESD5 | 161 | 15.4339 | 15.4973 | 0.0634
GEN-2017-231 | 04 SOUTHEAST | 515343 | MASSARD5 | 161 | 17.9207 | 17.9851 | 0.0644
GEN-2017-231 | 04 SOUTHEAST | 515346 | PUDDIN 5 | 161 | 9.1557 | 9.1945 | 0.0388
GEN-2017-231 | 04 SOUTHEAST | 515348 | NALCOTP5 | 161 | 16.4952 | 16.5617 | 0.0665
GEN-2017-231 | 04 SOUTHEAST | 515354 | NOARK 5 | 161 | 8.7457 | 8.7936 | 0.0479
GEN-2017-231 | 04 SOUTHEAST | 515355 | IGO 5 | 161 | 8.096 | 8.1622 | 0.0662
GEN-2017-231 | 04 SOUTHEAST | 515357 | RAZRBAK5 | 161 | 6.6114 | 6.6915 | 0.0801
GEN-2017-231 | 04 SOUTHEAST | 515358 | SHORTMT5 | 161 | 6.5617 | 6.6977 | 0.136
GEN-2017-231 | 04 SOUTHEAST | 515360 | TWNBRDG5 | 161 | 13.3937 | 13.4545 | 0.0608
GEN-2017-231 | 04 SOUTHEAST | 515406 | ADABELL5 | 161 | 16.6904 | 16.768 | 0.0776
GEN-2017-231 | 04 SOUTHEAST | 515440 | SUBIACT5 | 161 | 6.375 | 6.4789 | 0.1039
GEN-2017-231 | 04 SOUTHEAST | 515441 | SUBIACO5 | 161 | 6.3135 | 6.4156 | 0.1021
GEN-2017-231 | 04 SOUTHEAST | 515524 | GRNDPRT5 | 161 | 7.521 | 7.7275 | 0.2065
GEN-2017-231 | 04 SOUTHEAST | 515527 | HWY59TP5 | 161 | 15.8337 | 15.9118 | 0.0781
GEN-2017-231 | 04 SOUTHEAST | 515956 | 7CLANS 5 | 161 | 9.7803 | 9.7838 | 0.0035
GEN-2017-231 | 04 SOUTHEAST | 760221 | GEN-2017-231 | 161 | 7.8687 | 8.1594 | 0.2907
GEN-2017-232 | 04 SOUTHEAST | 505595 | GREASYC4 | 138 | 6.9973 | 6.9989 | 0.0016
GEN-2017-232 | 04 SOUTHEAST | 505596 | EXPLOR 4 | 138 | 5.434 | 5.4362 | 0.0022
GEN-2017-232 | 04 SOUTHEAST | 505598 | ALLEN 4 | 138 | 5.4304 | 5.4344 | 0.004
GEN-2017-232 | 04 SOUTHEAST | 505600 | TUPELO 4 | 138 | 10.9595 | 10.9837 | 0.0242
GEN-2017-232 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 8.5728 | 8.7934 | 0.2206
GEN-2017-232 | 04 SOUTHEAST | 505604 | DENISON4 | 138 | 3.1138 | 3.1497 | 0.0359
GEN-2017-232 | 04 SOUTHEAST | 505650 | GERTY 4 | 138 | 4.0081 | 4.0105 | 0.0024
GEN-2017-232 | 04 SOUTHEAST | 505665 | CENTRATAP4 | 138 | 10.7552 | 10.7784 | 0.0232
GEN-2017-232 | 04 SOUTHEAST | 505666 | CENTRAHOMA4 | 138 | 6.0072 | 6.012 | 0.0048
GEN-2017-232 | 04 SOUTHEAST | 505671 | UNION VLY4 | 138 | 5.4465 | 5.4536 | 0.0071
GEN-2017-232 | 04 SOUTHEAST | 505672 | AHLOSO4 | 138 | 4.8528 | 4.8586 | 0.0058
GEN-2017-232 | 04 SOUTHEAST | 505674 | MONTE VISTA4 | 138 | 3.7449 | 3.7488 | 0.0039
GEN-2017-232 | 04 SOUTHEAST | 510862 | COALGAT4 | 138 | 5.9937 | 6.0006 | 0.0069
GEN-2017-232 | 04 SOUTHEAST | 510863 | ALLENNG4 | 138 | 5.6439 | 5.6515 | 0.0076
GEN-2017-232 | 04 SOUTHEAST | 510880 | COALGTP4 | 138 | 6.226 | 6.2333 | 0.0073
GEN-2017-232 | 04 SOUTHEAST | 510881 | ALLENGT4 | 138 | 10.5983 | 10.621 | 0.0227
GEN-2017-232 | 04 SOUTHEAST | 510884 | HOLDEXP4 | 138 | 5.3056 | 5.3078 | 0.0022
GEN-2017-232 | 04 SOUTHEAST | 510887 | ATOKA--4 | 138 | 6.0399 | 6.0453 | 0.0054
GEN-2017-232 | 04 SOUTHEAST | 510895 | LEHIGH-4 | 138 | 5.8495 | 5.8555 | 0.006
GEN-2017-232 | 04 SOUTHEAST | 510916 | ALLEN--4 | 138 | 5.423 | 5.427 | 0.004
GEN-2017-232 | 04 SOUTHEAST | 510935 | EXPCOLT4 | 138 | 7.6611 | 7.6739 | 0.0128
GEN-2017-232 | 04 SOUTHEAST | 510936 | EXPCOLG4 | 138 | 7.5546 | 7.5671 | 0.0125
GEN-2017-232 | 04 SOUTHEAST | 510949 | WAPANUCKA 4 | 138 | 7.935 | 7.9477 | 0.0127
GEN-2017-232 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.8421 | 15.9196 | 0.0775
GEN-2017-232 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1436 | 11.1642 | 0.0206
GEN-2017-232 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.5055 | 11.6142 | 0.1087
GEN-2017-232 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.2721 | 11.3066 | 0.0345
GEN-2017-232 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 8.3916 | 8.4633 | 0.0717
GEN-2017-232 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 8.3896 | 8.4614 | 0.0718
GEN-2017-232 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.198 | 9.287 | 0.089
GEN-2017-232 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 7.3384 | 7.4605 | 0.1221
GEN-2017-232 | 04 SOUTHEAST | 515152 | BROWNTP4 | 138 | 8.409 | 8.6216 | 0.2126
GEN-2017-232 | 04 SOUTHEAST | 515153 | COLEMNT4 | 138 | 6.1616 | 6.2822 | 0.1206
GEN-2017-232 | 04 SOUTHEAST | 515154 | EXPLRPL4 | 138 | 4.3939 | 4.4594 | 0.0655
GEN-2017-232 | 04 SOUTHEAST | 515155 | BODLE 4 | 138 | 6.3937 | 6.5204 | 0.1267
GEN-2017-232 | 04 SOUTHEAST | 515157 | BROWN 4 | 138 | 8.5277 | 8.75 | 0.2223
GEN-2017-232 | 04 SOUTHEAST | 515159 | COLBRTP4 | 138 | 6.4592 | 6.5883 | 0.1291
GEN-2017-232 | 04 SOUTHEAST | 515176 | BUTRFLD4 | 138 | 6.034 | 6.1475 | 0.1135
GEN-2017-232 | 04 SOUTHEAST | 515191 | LULA 2 | 69 | 5.9255 | 5.9312 | 0.0057
GEN-2017-232 | 04 SOUTHEAST | 515192 | LULA 4 | 138 | 9.3855 | 9.4011 | 0.0156
GEN-2017-232 | 04 SOUTHEAST | 515193 | COLBRT-4 | 138 | 4.9318 | 5.0108 | 0.079
GEN-2017-232 | 04 SOUTHEAST | 515408 | REBAR 4 | 138 | 5.7613 | 5.8654 | 0.1041
GEN-2017-232 | 04 SOUTHEAST | 515699 | EFITSTP4 | 138 | 8.0409 | 8.0506 | 0.0097
GEN-2017-232 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.1375 | 11.1761 | 0.0386
GEN-2017-232 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.0572 | 10.0974 | 0.0402
GEN-2017-232 | 04 SOUTHEAST | 515944 | STRRDTP4 | 138 | 8.4969 | 8.7167 | 0.2198
GEN-2017-232 | 04 SOUTHEAST | 520406 | TUPELO 4 | 138 | 9.9907 | 10.0106 | 0.0199
GEN-2017-232 | 04 SOUTHEAST | 520426 | SEAWAY4 | 138 | 4.0851 | 4.1415 | 0.0564
GEN-2017-232 | 04 SOUTHEAST | 520427 | TXI4 | 138 | 3.1324 | 3.1679 | 0.0355
GEN-2017-232 | 04 SOUTHEAST | 520448 | BOGYDPT4 | 138 | 5.2334 | 5.2383 | 0.0049
GEN-2017-232 | 04 SOUTHEAST | 520463 | SCOLEMN4 | 138 | 4.3758 | 4.4338 | 0.058
GEN-2017-232 | 04 SOUTHEAST | 520465 | REAGAN 4 | 138 | 4.1979 | 4.2201 | 0.0222
GEN-2017-232 | 04 SOUTHEAST | 520483 | DURANT 4 | 138 | 4.5786 | 4.6272 | 0.0486
GEN-2017-232 | 04 SOUTHEAST | 520527 | BOGGYDP4 | 138 | 3.7853 | 3.7883 | 0.003
GEN-2017-232 | 04 SOUTHEAST | 520551 | SALTTP 4 | 138 | 5.2998 | 5.3044 | 0.0046
GEN-2017-232 | 04 SOUTHEAST | 520826 | BENNGTN4 | 138 | 4.6611 | 4.6918 | 0.0307
GEN-2017-232 | 04 SOUTHEAST | 520860 | COLBERT4 | 138 | 4.9156 | 4.9941 | 0.0785
GEN-2017-232 | 04 SOUTHEAST | 520862 | COLGATE4 | 138 | 6.1154 | 6.122 | 0.0066
GEN-2017-232 | 04 SOUTHEAST | 520884 | DURANTP4 | 138 | 5.4687 | 5.5344 | 0.0657
GEN-2017-232 | 04 SOUTHEAST | 520963 | KIERSEY4 | 138 | 5.5515 | 5.6499 | 0.0984
GEN-2017-232 | 04 SOUTHEAST | 520969 | LASALLE4 | 138 | 6.7351 | 6.744 | 0.0089
GEN-2017-232 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 11.4328 | 11.5412 | 0.1084
GEN-2017-232 | 04 SOUTHEAST | 521049 | SCLMNJC4 | 138 | 7.195 | 7.3373 | 0.1423
GEN-2017-232 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 9.1067 | 9.1937 | 0.087
GEN-2017-232 | 04 SOUTHEAST | 521071 | STNWLSW4 | 138 | 10.6564 | 10.6782 | 0.0218
GEN-2017-232 | 04 SOUTHEAST | 521074 | BOGGY4 | 138 | 8.9805 | 8.9965 | 0.016
GEN-2017-232 | 04 SOUTHEAST | 521075 | STNWLTP4 | 138 | 9.1561 | 9.1723 | 0.0162
GEN-2017-232 | 04 SOUTHEAST | 521077 | UNGER 4 | 138 | 4.982 | 5.002 | 0.02
GEN-2017-232 | 04 SOUTHEAST | 521115 | BENNSUB4 | 138 | 4.3918 | 4.4197 | 0.0279
GEN-2017-232 | 04 SOUTHEAST | 587200 | GEN-2016-030 | 138 | 6.1168 | 6.3397 | 0.2229
GEN-2017-233 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.5954 | 20.5916 | -0.0038
GEN-2017-233 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 31.7819 | 31.7758 | -0.0061
GEN-2017-233 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.0422 | 14.0275 | -0.0147
GEN-2017-233 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.2986 | 13.2777 | -0.0209
GEN-2017-233 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 13.801 | 13.7865 | -0.0145
GEN-2017-233 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.0262 | 10.0261 | -0.0001
GEN-2017-233 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.0528 | 9.0513 | -0.0015
GEN-2017-233 | 04 SOUTHEAST | 511424 | T-CONCO4 | 138 | 6.9029 | 6.9019 | -0.001
GEN-2017-233 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5808 | 10.5801 | -0.0007
GEN-2017-233 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.4252 | 18.4204 | -0.0048
GEN-2017-233 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 11.7631 | 11.7591 | -0.004
GEN-2017-233 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 8.0176 | 8.018 | 0.0004
GEN-2017-233 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.1423 | 5.1387 | -0.0036
GEN-2017-233 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.5651 | 16.5612 | -0.0039
GEN-2017-233 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.1321 | 25.1312 | -0.0009
GEN-2017-233 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.9014 | 13.906 | 0.0046
GEN-2017-233 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.5655 | 12.5614 | -0.0041
GEN-2017-233 | 04 SOUTHEAST | 511476 | S.W.S.-2 | 69 | 4.3095 | 4.3096 | 0.0001
GEN-2017-233 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.9178 | 34.9339 | 0.0161
GEN-2017-233 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 11.5649 | 11.564 | -0.0009
GEN-2017-233 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.2599 | 10.258 | -0.0019
GEN-2017-233 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 7.3476 | 7.3446 | -0.003
GEN-2017-233 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 21.9622 | 21.9595 | -0.0027
GEN-2017-233 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4179 | 10.4172 | -0.0007
GEN-2017-233 | 04 SOUTHEAST | 511540 | CAN_GAS4 | 138 | 9.2256 | 9.2248 | -0.0008
GEN-2017-233 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 8.689 | 8.6849 | -0.0041
GEN-2017-233 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.5467 | 10.543 | -0.0037
GEN-2017-233 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 11.5277 | 11.5228 | -0.0049
GEN-2017-233 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.1846 | 10.1828 | -0.0018
GEN-2017-233 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.1279 | 5.1244 | -0.0035
GEN-2017-233 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.4585 | 10.455 | -0.0035
GEN-2017-233 | 04 SOUTHEAST | 511575 | LEONARD4 | 138 | 10.2663 | 10.2655 | -0.0008
GEN-2017-233 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.9438 | 6.9428 | -0.001
GEN-2017-233 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.4053 | 21.4024 | -0.0029
GEN-2017-233 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.9165 | 20.9135 | -0.003
GEN-2017-233 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.3949 | 23.7553 | 0.3604
GEN-2017-233 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 29.3933 | 29.381 | -0.0123
GEN-2017-233 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1727 | 11.1642 | -0.0085
GEN-2017-233 | 04 SOUTHEAST | 514817 | SVCELRN2 | 69 | 6.5638 | 6.5639 | 0.0001
GEN-2017-233 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.5498 | 7.55 | 0.0002
GEN-2017-233 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.2498 | 17.252 | 0.0022
GEN-2017-233 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.7114 | 18.7141 | 0.0027
GEN-2017-233 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 15.807 | 15.808 | 0.001
GEN-2017-233 | 04 SOUTHEAST | 514823 | ROMNOSE4 | 138 | 6.0223 | 6.0219 | -0.0004
GEN-2017-233 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.5366 | 18.5361 | -0.0005
GEN-2017-233 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 27.4321 | 27.4391 | 0.007
GEN-2017-233 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 27.9017 | 27.9091 | 0.0074
GEN-2017-233 | 04 SOUTHEAST | 514849 | LAKESID4 | 138 | 25.3869 | 25.3942 | 0.0073
GEN-2017-233 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 30.519 | 30.5292 | 0.0102
GEN-2017-233 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 34.1251 | 34.1397 | 0.0146
GEN-2017-233 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 37.5803 | 37.6002 | 0.0199
GEN-2017-233 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.7789 | 32.7917 | 0.0128
GEN-2017-233 | 04 SOUTHEAST | 514861 | MUSTANG4 | 138 | 39.9489 | 39.9735 | 0.0246
GEN-2017-233 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 22.6178 | 22.6228 | 0.005
GEN-2017-233 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6084 | 27.6188 | 0.0104
GEN-2017-233 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.3297 | 23.3345 | 0.0048
GEN-2017-233 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.0621 | 28.0702 | 0.0081
GEN-2017-233 | 04 SOUTHEAST | 514876 | SW134TP4 | 138 | 30.0534 | 30.0708 | 0.0174
GEN-2017-233 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.9696 | 45.9997 | 0.0301
GEN-2017-233 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2666 | 34.3238 | 0.0572
GEN-2017-233 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.1209 | 24.1374 | 0.0165
GEN-2017-233 | 04 SOUTHEAST | 514887 | WESTMOR4 | 138 | 28.7155 | 28.7306 | 0.0151
GEN-2017-233 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 30.9176 | 30.9327 | 0.0151
GEN-2017-233 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.5867 | 29.6006 | 0.0139
GEN-2017-233 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.1233 | 20.1299 | 0.0066
GEN-2017-233 | 04 SOUTHEAST | 514896 | MORGAN 4 | 138 | 34.2931 | 34.3115 | 0.0184
GEN-2017-233 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.6748 | 46.7216 | 0.0468
GEN-2017-233 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 36.7134 | 36.8533 | 0.1399
GEN-2017-233 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 36.586 | 36.6149 | 0.0289
GEN-2017-233 | 04 SOUTHEAST | 514904 | WESTHSE4 | 138 | 19.45 | 19.4553 | 0.0053
GEN-2017-233 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 20.8421 | 20.8437 | 0.0016
GEN-2017-233 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.3234 | 42.338 | 0.0146
GEN-2017-233 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.3597 | 27.375 | 0.0153
GEN-2017-233 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.4294 | 26.4422 | 0.0128
GEN-2017-233 | 04 SOUTHEAST | 514928 | SOGATE 4 | 138 | 27.0395 | 27.0537 | 0.0142
GEN-2017-233 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.3966 | 45.4476 | 0.051
GEN-2017-233 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.6379 | 21.6438 | 0.0059
GEN-2017-233 | 04 SOUTHEAST | 514932 | MLENIUM4 | 138 | 20.7671 | 20.773 | 0.0059
GEN-2017-233 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.7033 | 42.7454 | 0.0421
GEN-2017-233 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 25.9591 | 26.0139 | 0.0548
GEN-2017-233 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.6625 | 34.6837 | 0.0212
GEN-2017-233 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 23.9684 | 23.976 | 0.0076
GEN-2017-233 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.045 | 23.0521 | 0.0071
GEN-2017-233 | 04 SOUTHEAST | 514952 | STUBMAN4 | 138 | 25.2422 | 25.2528 | 0.0106
GEN-2017-233 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.9381 | 36.9658 | 0.0277
GEN-2017-233 | 04 SOUTHEAST | 514954 | INDNHIL4 | 138 | 29.0639 | 29.079 | 0.0151
GEN-2017-233 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.7192 | 22.7277 | 0.0085
GEN-2017-233 | 04 SOUTHEAST | 514958 | BOYD 4 | 138 | 20.9373 | 20.9434 | 0.0061
GEN-2017-233 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.2851 | 20.2908 | 0.0057
GEN-2017-233 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 30.6245 | 30.6445 | 0.02
GEN-2017-233 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 15.6353 | 15.6378 | 0.0025
GEN-2017-233 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.2809 | 14.2828 | 0.0019
GEN-2017-233 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.481 | 16.484 | 0.003
GEN-2017-233 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.7735 | 40.7859 | 0.0124
GEN-2017-233 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 28.4371 | 28.4632 | 0.0261
GEN-2017-233 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.3293 | 20.3269 | -0.0024
GEN-2017-233 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.5061 | 10.5045 | -0.0016
GEN-2017-233 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.2707 | 27.272 | 0.0013
GEN-2017-233 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.2611 | 21.2592 | -0.0019
GEN-2017-233 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.1476 | 10.1315 | -0.0161
GEN-2017-233 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3525 | 22.3446 | -0.0079
GEN-2017-233 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 25.2342 | 25.2247 | -0.0095
GEN-2017-233 | 04 SOUTHEAST | 515380 | INDIANH4 | 138 | 28.8684 | 28.8833 | 0.0149
GEN-2017-233 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.2198 | 18.2176 | -0.0022
GEN-2017-233 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 10.1957 | 10.1886 | -0.0071
GEN-2017-233 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.3015 | 23.6589 | 0.3574
GEN-2017-233 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5347 | 12.5308 | -0.0039
GEN-2017-233 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.6757 | 20.6817 | 0.006
GEN-2017-233 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.5224 | 7.5184 | -0.004
GEN-2017-233 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.2651 | 40.2784 | 0.0133
GEN-2017-233 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6066 | 21.6107 | 0.0041
GEN-2017-233 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 22.1411 | 22.1448 | 0.0037
GEN-2017-233 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.1953 | 14.1875 | -0.0078
GEN-2017-233 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.8121 | 34.8833 | 0.0712
GEN-2017-233 | 04 SOUTHEAST | 515506 | OKRCHET2 | 69 | 3.7161 | 3.7157 | -0.0004
GEN-2017-233 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.516 | 13.5135 | -0.0025
GEN-2017-233 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.6105 | 14.7334 | 0.1229
GEN-2017-233 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7076 | 8.7044 | -0.0032
GEN-2017-233 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.2495 | 14.2459 | -0.0036
GEN-2017-233 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.5588 | 13.5526 | -0.0062
GEN-2017-233 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.2165 | 12.2222 | 0.0057
GEN-2017-233 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.3259 | 13.3343 | 0.0084
GEN-2017-233 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.317 | 18.3389 | 0.0219
GEN-2017-233 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.2968 | 19.3737 | 0.0769
GEN-2017-233 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.8912 | 33.9154 | 0.0242
GEN-2017-233 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.6839 | 14.6681 | -0.0158
GEN-2017-233 | 04 SOUTHEAST | 515864 | CMTRYRD4 | 138 | 6.7425 | 6.7416 | -0.0009
GEN-2017-233 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.9538 | 18.9562 | 0.0024
GEN-2017-233 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.9492 | 18.9517 | 0.0025
GEN-2017-233 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.4502 | 10.5052 | 0.055
GEN-2017-233 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.2776 | 14.2753 | -0.0023
GEN-2017-233 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 5.8217 | 5.8212 | -0.0005
GEN-2017-233 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.8607 | 39.8724 | 0.0117
GEN-2017-233 | 04 SOUTHEAST | 515980 | MNCWND57 | 345 | 7.6861 | 7.7119 | 0.0258
GEN-2017-233 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 7.3724 | 7.3707 | -0.0017
GEN-2017-233 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.753 | 17.7518 | -0.0012
GEN-2017-233 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16.0004 | 15.9928 | -0.0076
GEN-2017-233 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 26.2193 | 26.2297 | 0.0104
GEN-2017-233 | 04 SOUTHEAST | 520440 | HARPER2 | 69 | 13.9105 | 13.9112 | 0.0007
GEN-2017-233 | 04 SOUTHEAST | 520473 | CKSHATP4 | 138 | 11.1665 | 11.166 | -0.0005
GEN-2017-233 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 12.8348 | 12.8354 | 0.0006
GEN-2017-233 | 04 SOUTHEAST | 520512 | BC SW 4 | 138 | 6.4543 | 6.4542 | -0.0001
GEN-2017-233 | 04 SOUTHEAST | 520513 | BCV SW 4 | 138 | 5.8846 | 5.8844 | -0.0002
GEN-2017-233 | 04 SOUTHEAST | 520514 | BCVI_HVB | 138 | 7.5575 | 7.5575 | 0
GEN-2017-233 | 04 SOUTHEAST | 520530 | AMBERTP4 | 138 | 8.2844 | 8.2834 | -0.001
GEN-2017-233 | 04 SOUTHEAST | 520547 | SEQOYAH4 | 138 | 20.567 | 20.5734 | 0.0064
GEN-2017-233 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 14.6816 | 14.6824 | 0.0008
GEN-2017-233 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 36.8522 | 36.8738 | 0.0216
GEN-2017-233 | 04 SOUTHEAST | 520827 | BINGERJ4 | 138 | 7.9684 | 7.9683 | -0.0001
GEN-2017-233 | 04 SOUTHEAST | 520838 | CADDO 2 | 69 | 11.4811 | 11.4815 | 0.0004
GEN-2017-233 | 04 SOUTHEAST | 520859 | COGAR 4 | 138 | 9.2041 | 9.2034 | -0.0007
GEN-2017-233 | 04 SOUTHEAST | 520893 | EL RENO4 | 138 | 14.59 | 14.5905 | 0.0005
GEN-2017-233 | 04 SOUTHEAST | 520912 | FLETCH-4 | 138 | 7.228 | 7.2262 | -0.0018
GEN-2017-233 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 29.8778 | 29.8899 | 0.0121
GEN-2017-233 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 18.7647 | 18.769 | 0.0043
GEN-2017-233 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.2445 | 11.2453 | 0.0008
GEN-2017-233 | 04 SOUTHEAST | 521024 | PARADSE4 | 138 | 6.001 | 6.0007 | -0.0003
GEN-2017-233 | 04 SOUTHEAST | 521027 | PINERTP2 | 69 | 4.9226 | 4.9222 | -0.0004
GEN-2017-233 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.1874 | 8.1872 | -0.0002
GEN-2017-233 | 04 SOUTHEAST | 521072 | TUTLETP4 | 138 | 7.345 | 7.3443 | -0.0007
GEN-2017-233 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.2705 | 9.2707 | 0.0002
GEN-2017-233 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.798 | 30.8113 | 0.0133
GEN-2017-233 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 7.5778 | 7.5778 | 0
GEN-2017-233 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 6.3778 | 6.3777 | -0.0001
GEN-2017-233 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.1085 | 27.1936 | 0.0851
GEN-2017-233 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.4694 | 9.4705 | 0.0011
GEN-2017-233 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.5733 | 10.5911 | 0.0178
GEN-2017-233 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.0472 | 9.048 | 0.0008
GEN-2017-233 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 10.9563 | 10.969 | 0.0127
GEN-2017-233 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.8876 | 15.9213 | 0.0337
GEN-2017-233 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.4401 | 11.454 | 0.0139
GEN-2017-233 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.8441 | 11.8442 | 0.0001
GEN-2017-233 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.3688 | 16.3642 | -0.0046
GEN-2017-233 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.1563 | 10.1531 | -0.0032
GEN-2017-233 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.6676 | 3.6648 | -0.0028
GEN-2017-233 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 11.3314 | 11.3287 | -0.0027
GEN-2017-233 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.5291 | 10.5253 | -0.0038
GEN-2017-233 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.2918 | 6.2923 | 0.0005
GEN-2017-233 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.4195 | 11.4188 | -0.0007
GEN-2017-233 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.4195 | 11.4188 | -0.0007
GEN-2017-233 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.5617 | 22.9216 | 0.3599
GEN-2017-233 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.6055 | 22.9668 | 0.3613
GEN-2017-233 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.089 | 12.0893 | 0.0003
GEN-2017-233 | 04 SOUTHEAST | 761481 | GEN-2017-156 | 345 | 2.9683 | 2.9648 | -0.0035
GEN-2017-233 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.5175 | 7.5147 | -0.0028
GEN-2017-233 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.986 | 11.9832 | -0.0028
GEN-2017-233 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0574 | 7.0577 | 0.0003
GEN-2017-233 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.664 | 5.6641 | 0.0001
GEN-2017-233 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3149 | 6.3151 | 0.0002
GEN-2017-233 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 36.2685 | 36.2969 | 0.0284
GEN-2017-239 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 7.3667 | 7.2671 | -0.0996
GEN-2017-239 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 8.8695 | 8.8723 | 0.0028
GEN-2017-239 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 22.1276 | 22.127 | -0.0006
GEN-2017-239 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 26.965 | 27.0017 | 0.0367
GEN-2017-239 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 8.5571 | 8.5657 | 0.0086
GEN-2017-239 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 9.9534 | 9.9669 | 0.0135
GEN-2017-239 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 10.4944 | 10.5095 | 0.0151
GEN-2017-239 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 10.4944 | 10.5095 | 0.0151
GEN-2017-239 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.408 | 5.4075 | -0.0005
GEN-2017-239 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9633 | 21.9248 | -0.0385
GEN-2017-239 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 12.6384 | 12.5696 | -0.0688
GEN-2017-239 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 12.5141 | 12.446 | -0.0681
GEN-2017-239 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 11.0035 | 10.9969 | -0.0066
GEN-2017-239 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 10.9779 | 10.9991 | 0.0212
GEN-2017-239 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 9.6731 | 9.6946 | 0.0215
GEN-2017-239 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 12.7585 | 12.764 | 0.0055
GEN-2017-239 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.7938 | 10.7917 | -0.0021
GEN-2017-239 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 13.7533 | 14.2238 | 0.4705
GEN-2017-239 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0902 | 6.0903 | 0.0001
GEN-2017-239 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.1894 | 10.2287 | 0.0393
GEN-2017-239 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 18.4507 | 18.6189 | 0.1682
GEN-2017-239 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 18.0431 | 18.5224 | 0.4793
GEN-2017-239 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.6511 | 9.7109 | 0.0598
GEN-2017-239 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 8.2174 | 8.2384 | 0.021
GEN-2017-239 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 14.0173 | 14.602 | 0.5847
GEN-2017-239 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 13.899 | 14.4735 | 0.5745
GEN-2017-239 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 13.5889 | 14.2534 | 0.6645
GEN-2017-239 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.631 | 13.7017 | 0.0707
GEN-2017-239 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.1687 | 13.2071 | 0.0384
GEN-2017-239 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 10.9097 | 10.9919 | 0.0822
GEN-2017-239 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2181 | 12.2543 | 0.0362
GEN-2017-239 | 05 SOUTHWEST | 527036 | SHELL_C2 3 | 115 | 14.688 | 14.7527 | 0.0647
GEN-2017-239 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.5368 | 13.6067 | 0.0699
GEN-2017-239 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8241 | 10.8676 | 0.0435
GEN-2017-239 | 05 SOUTHWEST | 527051 | ODC_TP 3 | 115 | 13.6471 | 13.7179 | 0.0708
GEN-2017-239 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.4876 | 16.5855 | 0.0979
GEN-2017-239 | 05 SOUTHWEST | 527080 | EL_PASO 3 | 115 | 16.2369 | 16.3307 | 0.0938
GEN-2017-239 | 05 SOUTHWEST | 527105 | SAN_ANDS_TP3 | 115 | 17.0722 | 17.1728 | 0.1006
GEN-2017-239 | 05 SOUTHWEST | 527125 | DENVER_CTY 2 | 69 | 8.5402 | 8.5521 | 0.0119
GEN-2017-239 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.0655 | 22.2293 | 0.1638
GEN-2017-239 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.0655 | 22.2293 | 0.1638
GEN-2017-239 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 23.5525 | 23.745 | 0.1925
GEN-2017-239 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 15.382 | 15.7983 | 0.4163
GEN-2017-239 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 15.382 | 15.7983 | 0.4163
GEN-2017-239 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9785 | 7.9972 | 0.0187
GEN-2017-239 | 05 SOUTHWEST | 527201 | SEAGRAVES 2 | 69 | 5.5193 | 5.5218 | 0.0025
GEN-2017-239 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.1773 | 9.2008 | 0.0235
GEN-2017-239 | 05 SOUTHWEST | 527238 | ROZ 3 | 115 | 10.8855 | 10.9423 | 0.0568
GEN-2017-239 | 05 SOUTHWEST | 527242 | AMERADA 3 | 115 | 11.0316 | 11.09 | 0.0584
GEN-2017-239 | 05 SOUTHWEST | 527257 | FLATLAND 3 | 115 | 6.716 | 6.7212 | 0.0052
GEN-2017-239 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 13.9166 | 14.0105 | 0.0939
GEN-2017-239 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 7.8393 | 7.9124 | 0.0731
GEN-2017-239 | 05 SOUTHWEST | 527286 | HIGGEAST 3 | 115 | 10.1298 | 10.1493 | 0.0195
GEN-2017-239 | 05 SOUTHWEST | 527322 | GAINES 3 | 115 | 9.283 | 9.3114 | 0.0284
GEN-2017-239 | 05 SOUTHWEST | 527340 | DOSS 3 | 115 | 7.8959 | 7.921 | 0.0251
GEN-2017-239 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 10.3378 | 10.3578 | 0.02
GEN-2017-239 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.3875 | 17.4296 | 0.0421
GEN-2017-239 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 31.4788 | 31.5246 | 0.0458
GEN-2017-239 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.216 | 19.2782 | 0.0622
GEN-2017-239 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 11.6554 | 11.6945 | 0.0391
GEN-2017-239 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.6935 | 8.7109 | 0.0174
GEN-2017-239 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.7038 | 8.7226 | 0.0188
GEN-2017-239 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9956 | 9.0053 | 0.0097
GEN-2017-239 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.074 | 6.0785 | 0.0045
GEN-2017-239 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6307 | 3.6307 | 0
GEN-2017-239 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.1687 | 13.2071 | 0.0384
GEN-2017-239 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 12.2186 | 12.8918 | 0.6732
GEN-2017-239 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 12.2972 | 12.3044 | 0.0072
GEN-2017-239 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 7.5823 | 7.5051 | -0.0772